## Sheet1
PJM 2016 RTEP Proposal Window #3 Addendum Tracking Spreadsheet
Proposal Window: | 2016 RTEP Proposal Window 3A
Window Opening Date: | 2016-11-28
Window Closing Date: | 2016-12-13
Current Spreadsheet Version | V1
Project ID | Upgrade/Greenfield | Proposing Entity | Project Cost ($M) | Target Zone(s) | kV Level(s) | Analysis Type | FG# | Major Components/Project Description
2016_3A-1A | Greenfield | Transource | 44.58 | ATSI | 345/138 | Winter Gen Deliv | 392, 393, 400, 407, 489, 490, 493, 504, 915 | Construct a new double circuit 345 kV line between ATSI's Carlisle Station and a new station, Rocky River West, along the Avon Lake-Juniper 345 kV line. Also, construct a new Sheffield 138kV switching station.
2016_3A-1B | Greenfield | Transource | 50.56 | ATSI | 345/138 | Winter Gen Deliv | 386, 392, 393, 400, 407, 489, 490, 493, 504, 915 | Construct a new double circuit 345 kV line between ATSI's Carlisle Station and a new station, Rocky River West, along the Avon Lake-Juniper 345 kV line. Also, construct a new Sheffield 138kV switching station. Construct a new Middle Ridge 345kV Station connecting the existing Beaver-Davis Besse 345kV and Beaver-Carlisle 345kV lines.
2016_3A-2A | Greenfield | Northeast Transmission Development | 62.8 | ATSI | 345/138 | Winter Gen Deliv | 386, 392, 393, 400, 407, 489, 490, 493, 504, 915 | Construct a double circuit 345 kV line to loop the existing 345 kV Avon Lake to Juniper transmission line into the existing 345 kV Carlisle substation. Construct a single circuit 345 kV line from the existing X1-027A Tap to Beaver transmission line to the existing 345 kV Carlisle substation. Reconfigure the existing Beaver to X1-027A Tap 345 kV transmission line to have an X1-027A Tap to Carlisle 345 kV transmission line. Remove the remaining 345 kV transmission line between the new X1-027A Tap to Carlisle 345 kV line and the existing Beaver substation from service
2016_3A-3A | Upgrade | First Energy | 19.97 | ATSI | 345/138 | Winter Gen Deliv | 386, 915 | Reconductor the Beaver-Black River 138kV line (~ 9.8 Miles) 795 Kcmil ACSR, including the 6wire section (~7.0miles) with 954Kcmil ACSS conductor, upgrade the wavetrap at Black River to 2000A, replace the GCY51 relay at Beaver substation with SEL & modify the existing RTU. New ratings after all components are complete: SN 540MVA / SE 540MVA, WN 540MVA / WE 540MVA
2016_3A-3B | Upgrade | First Energy | 13.46 | ATSI | 345/138 | Winter Gen Deliv | 400, 407, 493, 504 | NOTE: Existing PJM RTEP Project b2559 (ISD 2017) reconductors Black River-Lorain 138kV line to 795 ACSS single circuit tower line. Black River-Lorain Q2 138kV line ugrade. Rebuild/Reconductor approx. 6.5miles single 795ACSS/TW conductor between Black River to Charleston and Charleston to Lorain substaions with bundle 795Kcmil ACSS conductor. Terminal upgrades Upgrade 2000A wavetrap at Black River, Lorain and Charleston substation to 3000A. The new Black River-Charleston and Charleston-Lorain 138kV circuit winter (MVA) rating will be 679WN / 753WE / 459WLD (The new limiting element is a substation conductor at Charleston)
2016_3A-3C | Upgrade | First Energy | 3.2 | ATSI | 345/138 | Winter Gen Deliv | 392, 393, 489, 490 | Reconductor the Avon - Lorain 138kV line segment (~4.5miles) with 795Kcmil ACSS conductor. Upgrade the line drops at Avon. New ratings WN 521MVA / WE 611MVA (Avon - Admiral) and WN 438MVA / WE 459MVA (Admiral - Lorain)