## Setup
Enter Stakeholder Committee Name in cell A2:
PC Special Session: Storage as a Transmission Asset
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Storage as a Transmission Asset

## 1. Interest Identification
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
Interest Identification
Instructions: List interests of all parties on this page.
1a | Maintaining reliability of the Bulk Electric System through compliance with NERC standards.
1b | Maintaining reliability with PJM and TO planning criteria
2 | Evaluate and incorporate, where appropriate, grid enhancing technologies such as energy storage in the PJM RTEP.
3 | Ensure PJM is able to compare traditional transmission technology with non-traditional technology such as energy storage.
4 | Preserve operational flexibility to maintain system reliability, including during PJM emergency procedures
5 | Should cause no harm or loss of load while charging or discharging
6 | Maintain integrity of the existing Interconnection Process
7 | Alignment of Market Efficiency modeling and operational guidelines
8 | Transparency of Market Efficiency modeling assumptions and cost constructability review
9 | Ensure stakeholders understand PJM's process for evaluation of SATA
10 | Determine how lower voltage, distribution storage asset would be processed through the PJM RTEP
11 | Determine how a storage asset from a non-member distribution utility would be handled
12 | Avoid pre-judging the type of storage technology
13 | Ensure the impacts of SATA are considered in the load forecasting and RTEP analysis
14 | Protect PJM's focus on managing competitve energy and capacity markets

## 2. Options Matrix- Design Comp.
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
OPTIONS MATRIX
Solution Options2
# | Category | Design Components1 | Priority | Status Quo | A | B | C | D | E
* |  | Implementation
1 | Reliability | Sensitivity cases to ensure compliance with Planning criteria |  | Study cases include summer peak 50/50, summer peak 90/10, winter peak, and light load. Sensitivity cases are ran ad hoc based on any issues that may arise
2 | Reliability | Forecast mechanism to model daily load curves to within an acceptable margin of error, in relation to 5-year planning studies |  | No current consideration of load curves for reliability studies
3 | Reliability | Generator Interconnection Study criteria - special cases to consider |  | Storage is modeled as discharging for summer and winter studies but is charging during light load study The Queue battery generator under study undergoes a Dynamic Dispatch to determine the worst case loading on any facility. Dynamic Dispatch means that the battery is dispatched in two seperate modes; as injecting power (generator), and as consuming power (load). Each flow gate considers both dispatch modes so that the loading reported on any facility is whichever mode yields the worst case loading.
4 | Reliability | Design for violation and identify its role as a harmer or a helper on other criteria tests |  | Complete do-no-harm testing
5 | Reliability | Outline outage reporting and Performance expectations requirements |  | Assumes transmission facilities maintain 100% capability | [5 empty] | Low
6 | Reliability | Allowable modes of operation |  | None | [5 empty] | Low - Medium
7 | Reliability | Charge and discharge schedules and responsibilities |  | None | [5 empty] | Low - High
8 |  | Operation for non-designed constraints conditions beyond the violation it was originally intended to mitigate
9 |  | Operation during emergencies
8 | Reliability | Benefit measurements of SATA vs. traditional resources in reliability studies (subcomponents listed below) | -------- | -------- | -------- | -------- | -------- | -------- | --------
8a | Reliability | Cost elements |  | Facility costs include initial cost, maintenance costs for the lifespan of the asset based on net present value
8b | Reliability | Ancillary Additional benefits |  | Transmission facilities are in-service and available for any violations but their characterisitcs are limited to the asset type
9 | Reliability | Lifespan and retirement considerations |  | Traditional assets can be retired at it's end-of-life. Moving the asset is a maintenance cost, not a capital cost.
10 | Market Efficiency | Generator Interconnection Study Process - special cases to consider (IARRs) |  | Only the network upgrades associated with storage can be considered for IARR
11 | Market Efficiency | Allowable modes of operation |  | Generating, charging, economic. (Dispatched by SCED to minimize production cost, may become depleted)
12 | Market Efficiency | Charge and discharge schedules and responsibilities |  | Charge and discharge schedules determined by the simulation engine to achive the lowest production cost
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component |  |  | Detailed Description
1 | Reliability | Sensitivity cases to ensure compliance with Planning criteria | Sensitivity cases should model the SATA at its extreme of performance; at maximum discharge, and at maximum charging. This would include consideration for pre- and post-contingency.
2 | Reliability | Forecast mechanism to model daily load curves to within an acceptable margin of error, in relation to 5-year planning studies | Daily load curves at the substation bus level or at a suitably granular voltage level must be developed with a rigorous and transparent process. The process will likely include historical trends, forecast load growth, spot loads, future generaton and transmssion expansion.
3 | Reliability | Generator Interconnection Study criteria - special cases to consider | Similar to design component 1, the Generator Interconnection Study must account for all SATA modes of operation in terms of network reinforcement scope and cost responsibility.
4 | Reliability | Design for violation and identify its role as a harmer or a helper on other criteria tests | Determine if the SATA appropriately mitigates the violation. Adverse impacts will need to be determined so it does no harm to other violations whether charging or discharging.
5 | Reliability | Outline outage reporting and Performance expectations requirements | Proposing entity must ensure the SATA design will continue to meet availability and performance requirements taking into consideration degradation of SATA components over its lifetime
6 | Reliability | Allowable modes of operation | Define permissable operational types for SATA installations, which categorizes how the resource will charge and discharge in order to meet the designed constraint.
7 | Reliability | Charge and discharge schedules and responsibilities | Determine responsibilities for state of charge management and SATA scheduling.
8 | Reliability | Benefit measurements of SATA vs. traditional resources in reliability studies (subcomponents listed below) | ------------------------
8a | Reliability | Cost elements | Define elements to be included in the cost of SATA based on its lifecycle.
8b | Reliability | Additional benefits | Identify benefits beyond its intended application
9 | Reliability | Lifespan and retirement considerations | Determine applicable lifetime for comparison with traditional transmission reinforcements.
10 | Market Efficiency | Generator Interconnection Study Process - special cases to consider (IARRs) | Determine/Define how a SATA is studied in the Generator Interconnection Process
11 | Market Efficiency | Allowable modes of operation | Define permissable operational types for SATA installations, which categorizes how the resource will charge and discharge in order to meet the designed constraint.
12 | Market Efficiency | Charge and discharge schedules and responsibilities | Determine responsibilities for state of charge management and SATA scheduling.

## 2b. Option Details
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description

## 3. Package Matrix
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description
Documentation of specific operating guides for SATA
SATA state of charge for operational use
Outage reporting and output expectations
Operational implementation into day-ahead studies and input into the day-ahead market
Operation for conditions beyond the violation it was originally intended to mitigate
Operation during emergencies

## Revision History
PC Special Session: Storage as a Transmission Asset
Storage as a Transmission Asset
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1 | 2020-06-30 | Initial Matrix pre-populated with PJM interests
2 | 2020-07-07 | Post-meeting feedback and updates
3 | 2020-07-31 | Pre-meeting matrix populated with design components, the design component details, and status quo