## Single Zone Allocation Table
File Posted: 2/9/2015
Revision 1 - Original Version
This document contains all of the new single zone and multiple zone cost allocations that the PJM Board is requested to approve in February 2015
Upgrade ID | Description | Cost Estimate ($M) | Trans Owner | Cost Responsibility | Required IS Date
b1698.7 | Replace Loudoun 230 kV breaker '203052' with 63kA rating | 0.313 | Dominion | Dominion | 2016-06-01
b2362.1 | Install a 230 kV breaker at Squab Hollow 230 kV substation | 0.75 | APS | APS | 2015-06-01
b2542 | Replace the Loudoun 500kV 'H2T502' breaker with a 50kA breaker | 0.79 | Dominion | Dominion | 2019-06-01
b2543 | Replace the Loudoun 500kV 'H2T584' breaker with a 50kA breaker | 0.79 | Dominion | Dominion | 2019-06-01
b2572 | Replace the Peach Bottom 500 kV '#225' breaker with a 63kA breaker | 1.5 | PECO | PECO | 2019-06-01
b2573 | Replace the Warren 115 kV 'B12' breaker with a 40kA breaker | 0.25 | PENELEC | PENELEC | 2016-06-01
b2574 | Replace the Sunbury 230 kV 'MONTOUR NORT' breaker with a 63kA breaker | 0.75 | PPL | PPL | 2019-06-01
b2581 | Open the Corner 138 kV circuit breaker 86 for an overload of the Corner - Washington MP 138 kV line. The tower contingency loss of Belmont - Trissler 138 kV and Belmont - Edgelawn 138 kV should be added to Operational contingency | 0 | AEP | AEP | 2015-06-01
b2583 | Install 500 kV breaker at Ox Substation to remove Ox Tx#1 from H1T561 breaker failure outage. | 1.24 | Dominion | Dominion | 2019-06-01
b2584 | Relocate the Bremo load (transformer #5) to #2028 (Bremo- Charlotsville 230 kV) line and Cartersville distribution station to #2027 (Bremo-Midlothian 230 kV) line | 1.67 | Dominion | Dominion | 2018-11-01
b2585 | Reconductor 7.63 miles of existing line between Cranes and Stafford, upgrade associated line switches at Stafford | 7.12 | Dominion | PEPCO | 2019-06-01
b2586 | Upgrade the V74 34.5 kV transmission line between Allenhurst and Elberon Substations | 14.76 | JCPL | JCPL | 2018-06-01
b2587 | Reconfigure Pierce Brook 345 kV station to a ring bus and install a 125 MVAR shunt reactor at the station | 5.53 | PENELEC | PENELEC | 2018-09-01
b2588 | Install a 36.6 MVAR 115 kV capacitor at North Bangor substation | 0.98 | ME | ME | 2019-06-01
b2589 | Install a 100 MVAR 230 kV shunt reactor at Mercer station | 7.2 | PSEG | PSEG | 2018-09-01
b2590 | Install two 75 MVAR 230 kV capacitors at Sewaren station | 8.4 | PSEG | PSEG | 2019-06-01
b2591 | Construct a new line approximately 2.5 miles from Colfax to Drewry's. Construct a new Drewry's station and install a new circuit breaker at Colfax station. | 7.922 | AEP | AEP | 2019-06-01
b2592 | Rebuild existing East Coshocton – North Coshocton double circuit line which contains Newcomerstown - N. Coshocton 34.5 kV Circuit and Coshocton – North Coshocton 69 kV circuit | 5.09 | AEP | AEP | 2019-06-01
b2593 | Rebuild existing West Bellaire - Glencoe 69 kV line with 138 kV & 69 kV circuits and install 138/69 kV transformer at Glencoe Switch | 30 | AEP | AEP | 2019-06-01
b2594 | Rebuild 1.0 mile of Brantley - Bridge Street 69 kV Line with 1033 ACSR overhead conductor | 1.5 | AEP | AEP | 2019-06-01
b2595.1 | Rebuild 7.82 mile Elkhorn City - Haysi S.S 69 kV line utilizing 1033 ACSR built to 138 kV standards | 31.86 | AEP | AEP | 2019-06-01
b2595.2 | Rebuild 5.18 mile Moss - Haysi SS 69 kVline utlizing 1033 ACSR built to 138 kV standards |  | AEP | AEP | 2019-06-01
b2596 | Move load from the 34.5 kV bus to the 138 kV bus by installing a new 138/12 kV XF at New Carlisle station in Indiana | 2.025 | AEP | AEP | 2019-06-01
b2597 | Rebuild approximately 1 mi. section of Dragoon-Virgil Street 34.5 kV line between Dragoon and Dodge Tap switch and replace Dodge switch MOAB to increase thermal capability of Dragoon-Dodge Tap branch | 2.154 | AEP | AEP | 2019-06-01
b2598 | Rebuild approximately 1 mile section of the Kline-Virgil Street 34.5 kV line between Kline and Virgil Street tap. Replace MOAB switches at Beiger, risers at Kline, switches and bus at Virgil Street. | 1.689 | AEP | AEP | 2019-06-01
b2599 | Rebuild approximately 0.1 miles of 69 kV line between Albion and Albion tap | 0.2 | AEP | AEP | 2019-06-01
b2600 | Rebuild Fremont - Pound line as 138 kV | 14.5 | AEP | AEP | 2019-06-01
b2601 | Fremont Station Improvements | 2.5 | AEP | AEP | 2019-06-01
b2601.1 | Replace MOAB towards Beaver Creek with 138kV breaker |  | AEP | AEP | 2019-06-01
b2601.2 | Replace MOAB towards Clinch River with 138kV breaker |  | AEP | AEP | 2019-06-01
b2601.3 | Replace 138kV Breaker A with new bus-tie breaker |  | AEP | AEP | 2019-06-01
b2601.4 | Re-use Breaker A as highside protection on transformer #1 |  | AEP | AEP | 2019-06-01
b2601.5 | Install two (2) circuit switchers on highside of transformers # 2 and 3 at Fremont Station |  | AEP | AEP | 2019-06-01
b2602.1 | Install 138 kV breaker E2 at North Proctorville | 12.56 | AEP | AEP | 2019-06-01
b2602.2 | Construct 2.5 Miles of 138 kV 1033 ACSR from East Huntington to Darrah 138 kV substations |  | AEP | AEP | 2019-06-01
b2602.3 | Install breaker on new line exit at Darrah towards East Huntington |  | AEP | AEP | 2019-06-01
b2602.4 | Install 138 kV breaker on new line at East Huntington towards Darrah |  | AEP | AEP | 2019-06-01
b2602.5 | Install 138 kV breaker at East Huntington towards North Proctorville |  | AEP | AEP | 2019-06-01
b2603 | Boone Area Improvements | 43.18 | AEP | AEP | 2019-06-01
b2603.1 | Purchase approximately a 200X300 station site near Slaughter Creek 46 kV station (Wilbur Station) |  | AEP | AEP | 2019-06-01
b2603.2 | Install 3 138 kV circuit breakers, Cabin Creek to Hernshaw 138 kV circuit |  | AEP | AEP | 2019-06-01
b2603.3 | Construct 1 mi. of double circuit 138 kV line on Wilbur - Boone 46 kV line with 1590 ACSS 54/19 conductor @ 482 Degree design temp. and 1-159 12/7 ACSR and one 86 Sq.MM. 0.646" OPGW Static wires |  | AEP | AEP | 2019-06-01
b2604 | Bellefonte Transformer Addition | 31.65 | AEP | AEP | 2019-06-01
b2605 | Rebuild and reconductor Kammer - George Washington 69 kV circuit and George Washington - Moundsville Ckt #1, designed for 138kV. Upgrade limiting equipment at remote ends and at tap stations | 26 | AEP | AEP | 2019-06-01
b2606 | Convert Bane - Hammondsville from 23kV to 69kV operation | 9.3 | AEP | AEP | 2019-06-01
b2607 | Pine Gap Relay Limit Increase | 0 | AEP | AEP | 2019-06-01
b2608 | Richlands Relay Upgrade | 0.2 | AEP | AEP | 2019-06-01
b2609 | Therofare - Ivydale Area Build | 53 | AEP | AEP | 2019-06-01
b2610 | Rebuild Pax Branch - Scaraboro as 138 kV | 11.3 | AEP | AEP | 2019-06-01
b2611 | Skin Fork Area Improvements | 25.98 | AEP | AEP | 2019-06-01
b2611.1 | New 138/46 kV station near Skin Fork and other components |  | AEP | AEP | 2019-06-01
b2611.2 | Construct 3.2 miles of 1033 ACSR double circuit from new Station to cut into Sundial-Baileysville 138 kV line |  | AEP | AEP | 2019-06-01
b2612.1 | Relocate All Dam 6 138 kV line and the 138 kV line to AE units 1&2 | 0.93 | APS | APS | 2019-06-01
b2612.2 | Install 138kV, 3000A bus-tie breaker in the open bus-tie position next to the Shaffers corner 138 kV line |  | APS | APS | 2019-06-01
b2612.3 | Install a 6-pole manual switch, foundation, control cable, and all associated facilities |  | APS | APS | 2019-06-01
b2613 | Replace relays at Mazon substation | 0.7 | ComEd | ComEd | 2019-06-01
b2614 | Decouple the double-circuited Spurlock - Maysville Industrial Tap 138-kV & Spurlock - Flemingsburg 138-kV line segments | 0.76 | EKPC | EKPC | 2019-06-01
b2615 | Upgrade the Bullitt County 161/69 kV transformer facility | 1.29 | EKPC | EKPC | 2019-06-01
b2459 | Install +260/-150 MVAR SVC at Lake Shore | 34.7 | ATSI | ATSI | 2015-06-01

## Multi Zone Allocation Table
File Posted: 2/9/2015
Revision 1 - Original Version
This document contains all of the new single zone and multiple zone cost allocations that the PJM Board is requested to approve in February 2015
Upgrade ID | Description | Cost Estimate ($M) | Trans Owner | Cost Responsibility | Required IS Date
b2443.3 | Glebe - Station C PAR | 10 | Dominion | DVP - 22.57%, PEPCO - 77.43% | 2018-06-01
b2582 | Rebuild the Elmont - Cunningham 500 kV line | 106.1 | Dominion | AEC - 0.77%, AEP - 7.66%, APS - 2.94%, ATSI - 3.88%, BGE - 5.29%, ComEd - 6.19%, ConEd - 0.29%, Dayton - 1.01%, DEOK - 1.61%, DL - 0.85%, DVP - 47.03%, DPL - 1.22%, ECP - 0.1%, EKPC - 1.08%, O66 - 0.10%, JCPL - 1.77%, ME - 0.89%, NEPTUNE - 0.21%, PECO - 2.59%, PENELEC - 0.96%, PEPCO - 7.97%, PPL - 2.53%, PSEG - 2.99%, RE - 0.13% | 2018-06-01