## Posted Project Information
PJM 2016/17 ME Long Term Proposal Window Tracking Spreadsheet
Proposal Window: | 2016/17 ME Long term Proposal Window
Window Opening Date: | 2016-11-01
Window Closing Date: | 2017-02-28
Current Spreadsheet Version | V1
Projects described as proposed by submitted entities
Project ID | Proposing Entity | Project Description | Upgrade/ Greenfield | kV level | In-Service Cost ($mil) | In-Service Year | Target Zone | ME Constraint
201617_1-1A | WPPI | Provide a second New Carlisle-Olive 138 kV circuit. | Upgrade | 138 kV | 1 | 2019 | AEP | OLIVE - BOSSERMAN 138 kV
201617_1-2A | PPL | Reconductor the Susquehanna - Harwood 230 kV DCT line and replace a limited number of structures as necessary to accommodate the heavier conductor. | Upgrade | 230 kV | 13.13 | 2021 | PPL | SUSQUEHANNA - HARWOOD 230 kV
201617_1-2B | PPL | Reconductor the Susquehanna - Harwood 230 kV DCT line and replace a limited number of structures as necessary to accommodate the heavier conductor. Update protection settings at Susquehanna, Harwood, and Sugarloaf 230 kV substations to accommodate the new line ratings. | Upgrade | 230 kV | 13.01 | 2021 | PPL | SUSQUEHANNA - HARWOOD 230 kV
201617_1-2C | PPL | Route existing Susquehanna - Wescosville 500 kV line in and out of new Siegfried 500 kV bus station. Install a new 500/230 kV Siegfried transformer. Connect low side of new transformer to Siegfried 230 kV West Bus. | Upgrade | 230/500 kV | 18.32 | 2021 | PPL | SUSQUEHANNA - HARWOOD 230 kV
201617_1-3A | ComEd | Upgrade capacity on 345 kV E. Frankfort - University Park line. | Upgrade | 345 kV | 0.835 | 2021 | ComEd | E. FRANKFORT - UNIVERSITY PARK 345 kV + RPM Benefits
201617_1-3B | ComEd | Upgrade equipment at Pontiac Midpoint station to increase capacity on 345kV Pontiac-Brokaw line. | Upgrade | 345 kV | 5.62 | 2021 | ComEd | PONTIAC - BROKAW 345 kV + RPM Benefits
201617_1-4A | First Energy | Connect existing on-site spare 500-138kV transformer at Belmont Substation as TR4, in parallel with TR3. Relocate the termination of two 138 kV lines to provide 138 kV termination for TR4. | Upgrade | 138/500 kV | 2.79 | 2019 | APS | BELMONT TR 500/138 KV
201617_1-4B | First Energy | Replace relaying and replace wave traps at both terminal ends to raise the circuit rating to the line conductor limit. | Upgrade | 138 kV | 0.48 | 2018 | ATSI | HOYTDALE - MAPLE 138 kV
201617_1-5A | BGE | Increase capacity on existing towers by reconductoring the Conastone to Graceton 2323 & 2324 230kV circuits. | Upgrade | 230 kV | 5.97 | 2020 | BGE | CONASTONE - GRACETON 230 kV
201617_1-5B | BGE | Increase capacity on existing towers by adding additional conductors to the Graceton-Bagley-Raphael Road 230kV circuits. | Upgrade | 230 kV | 14.2 | 2021 | BGE | GRACETON - BAGLEY 230 kV
201617_1-5C | BGE | Increase capacity on existing towers by reconductoring the Conastone to Graceton 230kV, adding additional/bundled conductors to the Graceton-Bagley-Raphael Road 230kV. | Upgrade | 230 kV | 20.3 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-5D | BGE | Increase capacity on existing towers by reconductoring the Conastone to Graceton 230 kV circuits, adding additional conductors to the Graceton-Bagley-Raphael Road 230 kV circuits and removing substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230 kV | 20.4 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-5E | BGE | Increase capacity on existing towers by reconductoring the Conastone to Graceton 230kV circuits, adding additional conductors to the Graceton-Bagley-Raphael Road 230 kV circuits, reconductoring the Raphael Road to Northeast, and removing substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230 kV | 25.4 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-6F | BGE PECO | Expand existing Graceton substation to 500/230 kV by tapping the existing Conastone 500 kV, constructing a 500 kV station to accommodate new line configuration and new 500/230 kV transformer, increase capacity on existing towers by adding/bundle additional conductors to the Graceton-Bagley-Raphael Road 230 kV circuits, reconductoring the Raphael Road to Northeast, removing substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230/500 kV | 49.2 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-6G | BGE PECO | Expand existing Graceton substation to 500/230 kV by tapping the existing Conastone 500 kV located at Graceton substation, constructing a 500 kV station to accommodate new line configuration and new 500/230kV transformer, increase capacity on existing towers by adding/bundle additional conductors to the Graceton-Bagley-Raphael Road 230kV circuits, reconductoring the Raphael Road to Northeast, removing substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230/500 kV | 56 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-6L | BGE PECO | Increase capacity on existing towers by reconductoring the Conastone to Graceton 230 kV circuits, adding/bundle additional conductors to the Graceton-Bagley-Raphael Road 230 kV circuits, reconductoring the Raphael Road to Northeast circuits, removing substation ratings limitation on Windy Edge to Glenarm adding new circuit between Peach Bottom 230 kV and existing Cooper 230 kV with series reactor, reconductoring existing Graceton-Cooper circuit, adding circuit breakers and replacing terminal equipment at Peach Bottom and Cooper. | Upgrade | 115/230 kV | 41.7 | 2021 | BGE PECO | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-6M | BGE PECO | Expand existing Graceton substation to 500/230kV, constructing a 500 kV station to accommodate new line configuration and new 500/230kV transformer, increase capacity on existing towers by adding/bundle additional conductors to the Graceton-Bagley-Raphael Road 230kV circuits, reconductoring the Raphael Road to Northeast circuits, removing substation ratings limitation on Windy Edge to Glenarm circuit adding new circuit between Peach Bottom 230kV and existing Cooper 230kV, reconductoring existing Graceton-Cooper circuit, replacing terminal equipment at Peach Bottom and Cooper. | Upgrade | 115/230/500 kV | 65.49 | 2021 | BGE PECO | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-7H | PECO | Install a new 230 kV transmission line connecting Peach Bottom substation to Cooper substation. Reconductor the Graceton-Cooper 230 kV line. Bundle the existing conductors on the Graceton-Bagley-Raphael Rd. 230 kV lines. Reconductor the Raphael Road to Northeast, remove substation ratings limitation on Windy Edge to Glenarm circuit. | Upgrade | 115/230 kV | 35.6 | 2021 | BGE PECO | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-7I | PECO | Install a new 230 kV transmission line connecting Peach Bottom substation to Cooper substation. Rebuild the 220-93 Graceton-Cooper 230 kV line. Bundle the existing conductors on the Graceton-Bagley-Raphael Road 230 kV lines. Reconductor the Raphael Road to Northeast, remove substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230 kV | 59.8 | 2021 | BGE PECO | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-7J | PECO | Install a new 230 kV transmission line connecting Peach Bottom substation to Graceton substation. Bundle the existing conductors on the Graceton-Bagley-Raphael Road 230 kV lines. Reconductor the Raphael Road to Northeast, remove substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230 kV | 68.1 | 2022 | BGE PECO | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-7K | BGE PECO | Install two new 500-230 kV transformers at Peach Bottom substation. Install a new double circuit 230 kV transmission line connecting Peach Bottom substation to Graceton substation. Bundle the existing conductors on the Graceton-Bagley-Raphael Road 230 kV lines. Reconductor Raphael Road to Northeast, remove substation ratings limitation on Windy Edge to Glenarm. | Upgrade | 115/230/500 kV | 191.4 | 2022 | BGE PECO | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-8A | Dominion | Build one (1) 230 kV shunt capacitor bank at DVP's Belvoir substation. | Upgrade | 230 kV | 3.73 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230 kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8B | Dominion | This is proposed by Dominion Virginia Power to build one (1) 230 kV shunt capacitor bank at DVP's Bull Run substation. | Upgrade | 230 kV | 4.14 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8C | Dominion | This is proposed by Dominion Virginia Power to build one (1) 230 kV shunt capacitor bank at DVP's Cannon Branch substation. | Upgrade | 230 kV | 1.82 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8D | Dominion | Build one (1) 230 kV shunt capacitor bank at DVP's Edwards Ferry substation. | Upgrade | 230 kV | 6.11 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8E | Dominion | Build one (1) 230 kV shunt capacitor bank at DVP's Greenway substation. | Upgrade | 230 kV | 3.79 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8F | Dominion | Build four (4) 230 kV shunt capacitor banks at four (4) DVP's substations. | Upgrade | 230 kV | 15.45 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8G | Dominion | Build three (3) 230 kV shunt capacitor banks at three (3) DVP's substations. | Upgrade | 230 kV | 10.68 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8H | Dominion | Build one (1) 230 kV shunt capacitor bank at DVP's Loudoun substation. | Upgrade | 230 kV | 4.81 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8I | Dominion | Build one (1) 230 kV shunt capacitor bank at DVP's Reston substation. | Upgrade | 230 kV | 5 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8J | Dominion | Build one (1) 500 kV Thyristor Controlled Series Capacitor (TCSC) at DVP's Morrisville substation on the Front Royal - Morrisville (Line 541) transmission line. | Upgrade | 500 kV | 44.11 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8K | Dominion | Reconductor the Pleasant View - Ashburn - Beaumeade 230 kV transmission line, replace limiting equipment along Line 274, and build one (1) 230 kV Thyristor Controlled Series Capacitor at DVP's Pleasant View substation on the Pleasant View - Beaumeade transmission line. | Upgrade | 230 kV | 49.25 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8L | Dominion | Install a new 500/230 kV transformer at the Goose Creek 500kV bus and connect the low side to the 230 kV by looping into the 2180 line. | Upgrade | 230 kV | 31.74 | 2021 | Dominion | I:AP SOUTH, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8M | Dominion | Reconductor Dooms - Crozet - Barracks Rd - Hydraulic Rd - Charlottesville 230kV line (Line 233) and replace limiting equipment along the line. | Upgrade | 230 kV | 32.39 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8N | Dominion | Reconductor Pleasant View - Ashburn - Beaumeade 230 kV line (Line 274) and replace limiting equipment along the line. | Upgrade | 230 kV | 5.18 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8O | Dominion | Reconductor a segment of Charlottesville - Proffit DP 230 kV line (Line 2054) and replace limiting equipment along the line. | Upgrade | 230 kV | 9.12 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8P | Dominion | Reconductor North Anna - Louisa - South Anna 230 kV line (Line 255), reconductor South Anna - Louisa CT 230 kV line (Line 2074), and replace limiting equipment along the lines. | Upgrade | 230 kV | 23.71 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-8Q | Dominion | Build a new 500kV station (Palmyra) by connecting and building a ring bus at the intersection of two (2) 500 kV lines including North Anna - Midlothian 500kV line (Line 576) and Cunningham - Elmont 500 kV line (Line 553) and add a 300MVAR capacitor bank. | Greenfield | 230 kV | 31.9 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-9A | NIPSCO | Reconductor existing NIPSCO line section between AEP Bosserman and Olive substation. | Upgrade | 138 kV | 8 | 2019 | AEP NIPSCO | OLIVE - BOSSERMAN 138 kV
201617_1-9B | NIPSCO | New NIPSCO line section between Thayer and Morrison substations. | Greenfield | 138 kV | 42.5 | 2022 | AML ComEd NIPSCO | PAXTON - GIFFORD 138 kV
201617_1-10A | Nextera | Build a new substation (Spring Hill) connecting an existing 230 kV substation and an existing 500 kV line in the area. | Greenfield | 230 kV | 33.8 | 2021 | PPL | SUSQUEHANNA - HARWOOD 230 kV
201617_1-10B | Nextera | Build a new 345/138 kV substation (Rolling Prairie) connecting the following an existing 345 kV line to two existing 138 kV lines. | Greenfield | 138 kV | 19.2 | 2021 | AEP | BOSSERMAN - OLIVE 138 kV
201617_1-10C | Nextera | Build a new 230 kV line between existing Perryman and Conowingo substations. | Greenfield | 230 kV | 44.4 | 2021 | BGE | GRACETON - BAGLEY 230 kV
201617_1-10D | Nextera | Build a new 230 kV transmission line between two existing 230 kV stations and build a new substation connecting an existing 230 kV substation to an existing 500 kV line. | Greenfield | 230 kV | 93.5 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-10E | Nextera | Build two new 230 kV transmission lines connecting separately three existing 230 kV stations and build a new 500/230 kV substation connecting an existing 230 kV substation to an existing 500 kV line. | Greenfield | 230/500 kV | 105.7 | 2021 | PPL | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-11A | AEP | Claytor 138 kV Corridor Upgrades. | Upgrade | 138 kV | 3.35 | 2019 | AEP | CHRIS - CLAYTOR 138 kV
201617_1-11B | AEP | Accelerate the previously approved baseline project to reconductor the entire Dequine-Eugene 345 kV. | Upgrade | 345 kV | 0 | 2019 | AEP | EUGENE - DEQUIN 345 kV + RPM Benefits
201617_1-11C | AEP | Accelerate the previously approved baseline project to reconductor the entire Dequine - Meadow Lake 345 kV. | Upgrade | 345 kV | 0 | 2019 | AEP | DEQUIN - MEADOW 345 kV + RPM Benefits
201617_1-12D | AEP NIPSCO | Rebuild sections of the 34.5 kV line between New Carlisle and Silver Lake as double circuit 138 kV, operating one circuit as 34.5 kV while the other as 138 kV. Extend the 138 kV circuit to Liquid Carbonics by constructing a green field single circuit line. Rebuild the Michigan City-Trail Creek-Bosserman 138 kV. | Upgrade | 138 kV | 41.86 | 2021 | AEP | OLIVE - BOSSERMAN 138 kV
201617_1-13A | Transource | Construct a new Baldwin Road 500/230 kV station along the Peach Bottom - Rock Springs 500 kV line, just south of the existing Peach Bottom station. Add two 500/230 kV 1200/1500 MVA transformers at Baldwin Road, operated together. | Greenfield | 230/500 kV | 345.9 | 2024 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13B | Transource | Construct a 230 kV line between Conastone 230 Station and a new Dulaney Valley 230/115 Station. | Greenfield | 230 kV | 51.54 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13C | Transource | Construct a 230 kV line between Conastone to a new Long Green 230/115 Station. | Greenfield | 230 kV | 169.27 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13D | Transource | Construct a 230 kV line between Conastone to a new Long Green 230/115 Station and another 230 kV line from the new Long Green Station to Raphael Road 230 Station. | Greenfield | 230 kV | 182.99 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13E | Transource | Construct a 230 kV line between a new Hereford 500/230 Station and a new Dulaney Valley 230/115 Station. | Greenfield | 115/230/500 kV | 149.23 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13F | Transource | Construct a 230 kV line between a new Love Run 500/230 Station and Perryman 230 Station. | Greenfield | 230/500 kV | 371.3 | 2024 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13G | Transource | Upgrade Conastone-Graceton-Bagley-Raphael Road-Northeast 230 kV Circuits. Upgrade Five Forks - Windy Edge 115 kV Circuits. | Upgrade | 115/230 kV | 192.07 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-13H | Transource | Tap the Tanners Creek - Losantville 345 kV line and build a single circuit line to a new 345/138 kV station (Coyote) next to Wiley. | Greenfield | 138/345 kV | 71.88 | 2021 | DEOK | TANNERS CREEK - MIAMI FORT 345 kV
201617_1-14A | ATC | Build a new 230 kV line from Furnace Run - Perryman. The second portion of the proposed project adds a series reactor to each of the Conastone-Graceton 230 kV lines (two total). The third portion of the proposed project will rebuild the 115 kV line from Glen Arm to Windy Edge. | Greenfield | 115/230 kV | 114.8 | 2023 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-15A | ATXI East PPL | A new double circuit 230 kV line from Conastone to a new 230/115 substation (Baldwin). Baldwin will have two 230/115 XFMR. The Sub will break up the Five Forks - Windy Edge 115 kV lines. From Baldwin to Windy Edge the 115 kV lines will need to be rebuilt. Also a new double circuit 230 kV line from Baldwin to Raphael Road will be constructed. | Greenfield | 115/230 kV | 138.5 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-15B | ATXI East PPL | A new double circuit 230 kV line from Peachbottom to Otter Point, a new double circuit line from Raphael Road to a new substation (Baldwin). Baldwin will have two 230/115 XFMR that step down into a breaker and a half 115 kV sub. The sub will break up the Five Forks - Windy Edge 115 kV line. From Baldwin to Windy Edge the 115 kV lines will need to be rebuilt. The double circuit line from Otter Point to Raphael Road and Raphael Road to Northeast will need to have the conductor replaced. | Greenfield | 115/230 kV | 178.3 | 2022 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-16A | PSEG | New 230kV Circuit from Peach Bottom to Otter Point. | Greenfield | 230 kV | 70.5 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-16B | PSEG | New 230kV circuit from Peach Bottom to Raphael Road. | Greenfield | 230 kV | 92.2 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-16C | PSEG | New 230kV circuit from Conastone to Raphael Road. | Greenfield | 230 kV | 87.2 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-16D | PSEG | New 230kV circuit from Conastone to Northeast. | Greenfield | 230 kV | 105.1 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-16E | PSEG | New 230kV circuit from Peach Bottom to Northeast. | Greenfield | 230 kV | 109.3 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-17A | AEP Exelon | Install a new substion at TSS 142 Cottage Grove and additional upgrades at TSS 179 Bloom and TSS 177 Burnham. | Greenfield | 345 kV | 66.9 | 2021 | ComEd | E. FRANKFORT - UNIVERSITY PARK 345 kV + RPM Benefits
201617_1-17B | AEP Exelon | Meadow Lake – Pike Creek 345 kV Double Circuit Greenfield Line and Pike Creek 345kV Station. | Greenfield | 345 kV | 197.97 | 2021 | ComEd | OLIVE - BOSSERMAN 138 kV + RPM Benefits
201617_1-18A | Northeast Transmission Development | Build a double circuit 230 kV line from the existing Graceton substation to a new substation ("Robinson Run") interconnecting the existing Peach Bottom - Delta Power Plant (York) 500 kV line. Upgrade the Graceton - Northeast double circuit 230 kV circuits and the Rock Ridge - Windy Edge 115 kV circuits. Build a 230/115 kV substation ("Pumpkin Run") interconnecting the Raphael Road - Northeast 230 kV circuits and Crane - Windy Edge 115 kV circuits. | Greenfield | 115/230/500 kV | 119.8 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-18B | Northeast Transmission Development | Build a double circuit 230 kV line from the existing Graceton substation to a new substation ("Bookers Run") interconnecting the existing Peach Bottom - Three Mile Island 500 kV line. Upgrade the Graceton - Northeast double circuit 230 kV circuits and the Five Forks - WIndy Edge 115 kV circuits. | Greenfield | 115/230/500 kV | 126.1 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-18C | Northeast Transmission Development | Build a double circuit 230 kV line from the existing Otter Point substation to a new substation ("Robinson Run") interconnecting the existing Peach Bottom - Delta Power Plant (York) 500 kV line. Upgrade the Raphael Road - Northeast double circuit 230 kV circuits. | Greenfield | 230/500 kV | 142.4 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-18D | Northeast Transmission Development | Build a double circuit 230 kV line from the existing Otter Point substation to a new substation ("Slate") interconnecting the existing Peach Bottom - Rock Springs 500 kV line. Upgrade the Raphael Road - Northeast double circuit 230 kV circuits. Build a 230/115 kV substation ("Pumpkin Run") interconnecting the Raphael Road - Northeast 230 kV circuits and Crane - Windy Edge 115 kV circuits. | Greenfield | 115/230/500 kV | 157.9 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-18E | Northeast Transmission Development | Build a double circuit 230 kV line from the existing Otter Point substation to a new substation ("Slate") interconnecting the existing Peach Bottom - Rock Springs 500 kV line. Upgrade the Raphael Road - Northeast double circuit 230 kV circuits and both Rock Ridge - WIndy Edge 115 kV circuits. | Greenfield | 115/230/500 kV | 145.4 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-18F | Northeast Transmission Development | Build a double circuit 230 kV line from the existing Conastone substation to a new substation ("Fitzhugh Run") interconnecting the existing Shawan Road - Summerfield 115 kV transmission lines and Windy Edge - Texas 115 kV transmission lines. | Greenfield | 115/230 kV | 90.5 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV, CONASTONE - PEACH BOTTOM 500 kV
201617_1-18G | Northeast Transmission Development | Build a 500/230 kV substation ("Fells Creek") interconnecting the existing Susquehanna - Wescosville 500 kV line and the existing Siegfried 230 kV substation. | Greenfield | 230/500 kV | 31.2 | 2021 | PJM PPL | SUSQUEHANNA - HARWOOD 230 kV
201617_1-18H | Northeast Transmission Development | Build a single circuit 138 kV line from the existing Grand Point 138 kV substation to a new substation ("Green Ridge") interconnecting the planned Rice - Ringgold 230 kV transmission line. | Greenfield | 138/230 kV | 16.3 | 2021 | Dominion | I:AP SOUTH
201617_1-18I | Northeast Transmission Development | Build a single circuit 138 kV line from the existing Grand Point 138 kV substation to a new substation ("Green Ridge") interconnecting the existing Conemaugh - Hunterstown 500 kV transmission line. | Greenfield | 138/500 kV | 31.4 | 2021 | Dominion | I:AP SOUTH
201617_1-18J | Northeast Transmission Development | Build a single circuit 230 kV line from the existing Hunterstown substation to a new 230 kV switchyard ("Green Valley") interconnecting the Carroll - Mt. Airy 230 kV transmission line. | Greenfield | 230 kV | 40.2 | 2021 |  | I:AP SOUTH, I:CENTRAL, RINGGOLD - OLD FARM 230 kV, GERMANTOWN - STRABAN 115 kV
201617_1-18K | Northeast Transmission Development | Build 600 MVAR Static VAR Compensation ("James Creek") interconnected to Brighton 500 kV Substation. | Greenfield | 500 kV | 39.7 | 2021 |  | I:BC_PEP
201617_1-18L | Northeast Transmission Development | Build 600 MVAR Static VAR Compensation ("Limestone Ridge") interconnected to Juniata 500 kV Substation. | Greenfield | 500 kV | 38.6 | 2021 |  | I:5004/5005, I:CENTRAL
201617_1-18M | Northeast Transmission Development | Build a single circuit 345 kV line from the existing Marysville 345 kV substation to the existing Miami 345 kV substation with a new intermediate substation ("Bull Branch") interconnecting to the existing Urbana 138 kV substation. Build a new 138 kV transmission line interconnecting the existing Crown 138 kV substation to a new 345/138 kV substation ("Spring Run") interconnecting the existing West Milton - Miami Fort 345 kV transmission line. | Greenfield | 138/345 kV | 117.3 | 2021 | AEP | Dayton LDA RPM Benefits
201617_1-18N | Northeast Transmission Development | Build a single circuit 345 kV line from the existing Marysville 345 kV substation to the existing Miami 345 kV substation with a new intermediate substation ("Bull Branch") interconnecting to the existing Urbana 138 kV substation. | Greenfield | 138/345 kV | 97.7 | 2021 | AEP | Dayton LDA RPM Benefits
201617_1-18O | Northeast Transmission Development | Build a double circuit 138 kV line from the existing Glen Lyn 138 kV substation to a new substation ("Smith Branch") interconnecting the existing Kanawha River - Matt Funk 345 kV transmission line. | Greenfield | 138/345 kV | 23.9 | 2021 | Dominion | I:AEP-DOM
201617_1-18P | Northeast Transmission Development | Build a new 138 kV transmission line interconnecting the existing Crown 138 kV substation to a new 345/138 kV substation ("Spring Run") interconnecting the existing West Milton - Miami Fort 345 kV transmission line. | Greenfield | 138/345 kV | 19.7 | 2021 | Dayton | Dayton LDA RPM Benefits
201617_1-18Q | Northeast Transmission Development | Construct a single circuit 230 kV line from the existing Harwood substation to a new switching station ("Trexler Run") interconnecting the Catawissa - Frackville 230 kV transmission line. | Greenfield | 230 kV | 32 | 2021 | PPL | SUSQUEHANNA - HARWOOD 230 kV
201617_1-18R | Northeast Transmission Development | Build a 500 kV switching station ("Turkey Creek") interconnecting the Cunningham to Elmont 500 kV transmission line and the North Anna to Midlothian 500 kV transmission line. | Greenfield | 500 kV | 19.3 | 2021 | Dominion | I:AEP-DOM
201617_1-18S | Northeast Transmission Development | Build a 345/138 kV substation ("Coffee Creek") interconnecting the Green Acres to Olive 345 kV line and the Flint Lake to Luchtman Road 138 kV line. | Greenfield | 138/345 kV | 17.4 | 2021 | AEP | OLIVE - BOSSERMAN 138 kV
201617_1-19A | Dominion Pepco | This is a joint proposal by Dominion Virginia Power and Pepco to upgrade their existing tie-line. Reconductor and double circuit the existing Pleasant View - Dickerson 230kV Line (Line 203). | Upgrade | 230 kV | 39.63 | 2021 | Dominion | I:AP SOUTH, I:AEP-DOM, I:5004/5005, I:CENTRAL, CONASTONE - GRACETON - BAGLEY 230 kV, BOSSERMAN - Olive 138 kV, SUSQUEHANNA - HARWOOD 230 kV, OAKBAY - NORTH RVR 230kV, PEACH BOTTOM - CONASTONE 500 kV
201617_1-20A | ITC | Construct a new 230 kV switchyard (Old Post) cutting-in the Raphael Road - Otter Point 230 kV line. Extend 230 kV from the new 230 kV switchyard to the existing Peach Bottom 230 kV substation. Upgrade the existing Peach Bottom 230 kV substation to accomodate the new 230 kV line. | Greenfield | 230 kV | 73.6 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20B | ITC | Construct a new 230 kV single circuit line between the existing Conastone and existing Raphael Road 230 kV substations. Upgrade the existing Conastone and Raphael Road 230 kV substations to accommodate the new 230 kV line. | Greenfield | 230 kV | 63 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20C | ITC | Construct a new 230 kV single circuit line between the existing Conastone and existing Northeast 230 kV substations. Upgrade the existing Conastone and Northeast 230 kV substations to accommodate the new 230 kV line. | Greenfield | 230 kV | 135.8 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20D | ITC | Construct a new 230 kV switchyard (Old Post) cutting-in the Raphael Road - Otter Point 230 kV line. Extend 230 kV from the new 230 kV switchyard to the existing Conastone 230 kV substation. Upgrade the existing Conastone 230 kV substation to accomodate the new 230 kV line. | Greenfield | 230 kV | 75.9 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20E | ITC | Construct a new 230 kV switchyard (Fallston) cutting-in the Graceton - Bagley 230 kV line. Construct a new 230 kV switchyard (Old Post) cutting-in the Raphael Road - Otter Point 230 kV line. Construct a new 230 kV switchyard (Pyle Rd). Construct 230 kV lines between the existing Peach Bottom 230 kV substation and the new Pyle Rd 230 kV switchyard, the new Fallston 230 kV switchyard and new Pyle Rd 230 kV switchyard, and the new Old Post 230 kV switchyard and the new Pyle Rd 230 kV switchyard. Upgrade the existing Peach Bottom 230 kV substation to accommodate the new 230 kV line. | Greenfield | 230 kV | 132.2 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20F | ITC | Construct a new 230 kV switchyard (Fallston) cutting-in the Graceton - Bagley 230 kV line. Construct a new 230 kV switchyard (Old Post) cutting-in the Raphael Road - Otter Point 230 kV line. Construct a new 230 kV switchyard (Pyle Rd). Construct 230 kV lines between the existing Conastone 230 kV substation and the new Pyle Rd 230 kV switchyard, the new Fallston 230 kV switchyard and new Pyle Rd 230 kV switchyard, and the new Old Post 230 kV switchyard and the new Pyle Rd 230 kV switchyard. Upgrade the existing Conastone 230 kV substation to accommodate the new 230 kV line. | Greenfield | 230 kV | 126 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20G | ITC | Construct a new 230 kV single circuit line between the existing Peach Bottom and existing Northeast 230 kV substations. Upgrade the existing Peach Bottom and Northeast 230 kV substations to accommodate the new 230 kV line. | Greenfield | 230 kV | 151.5 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20H | ITC | Construct a new 230 kV switchyard (Old Post) cutting-in the Raphael Road - Otter Point 230 kV line. Extend 230 kV from the new 230 kV switchyard to the existing Peach Bottom 230 kV substation. Upgrade the existing Peach Bottom 230 kV substation to accomodate the new 230 kV line. Install a transmission battery energy storage system at the Old Post switchyard. | Greenfield | 230 kV | 107.5 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV
201617_1-20I | ITC | Construct a new 230 kV switchyard (Fallston) cutting-in the Graceton - Bagley 230 kV line. Construct a new 230 kV switchyard (Old Post) cutting-in the Raphael Road - Otter Point 230 kV line. Construct a new 230 kV switchyard (Pyle Rd). Construct 230 kV lines between the existing Peach Bottom 230 kV substation and the new Pyle Rd 230 kV switchyard, the new Fallston 230 kV switchyard and new Pyle Rd 230 kV switchyard, and the new Old Post 230 kV switchyard and the new Pyle Rd 230 kV switchyard. Upgrade the existing Peach Bottom 230 kV substation to accommodate the new 230 kV line. Install a transmission battery energy storage system at the Fallston switchyard. | Greenfield | 230 kV | 165.7 | 2021 | BGE | CONASTONE - GRACETON - BAGLEY 230 kV