## Setup
Enter Stakeholder Group Name in cell A2:
DER Ride Through Task Force
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
DER Ride Through

## 1. Interest Identification
DER Ride Through Task Force
DER Ride Through
Interest Identification
Instructions: List interests of all parties on this page.
1 | Hot line worker safety | Distribution
2 | Integration with existing distribution protection | Distribution
3 | Risk of reclosing into an unintended island given uncertainty in anti-islanding algorithms | Distribution
4 | Flexibility to deal with diverse system conditions. | Distribution
5 | Standardization | Developer and manufacturer
6 | Interconnection costs (i.e., transfer trip or upgrade to dead-permissive reclose) | Developer and manufacturer
7 | Reduce nusance trips | Developer and manufacturer
8 | Transmission contingencies do not trigger widespread DER trips | PJM and Transmission
9 | DER contribute (Not hinder) to system stability during black start or similar conditions | PJM and Transmission
10 | Both of these are met if meet or exceed NERC PRC-024 | PJM and Transmission
11 | Limitations of resource | DER Operators
12 | Ease of compliance and demonstration of compliance | Developer
13 | Impact of island detection run on times as a result of Ride-Through | Distribution
14 | Commisioning expections around compliance. Documentation requirements? | Developer
15 | Will primary frequency response impact ride through requirements or anti-island capability? | Distribution
16 | Integration with regards to maintaining predictibility and stability | Distribution
17 | Power flow/dynamic, arc flash, distribution fault study | Evidence based solutions
18 | Coordination with load shedding schemes (Under voltage/frequency) | Distribution
19 | Ability to distinguish Transmission vs Distribution faults | Transmission
20 | Communication protocals between distribution/transmission | Developer/Operator
21 | Control assumptions for DER during design/retrofit phase | Developer/Operator
22 | Voltage profile/dynamics along distribution feeders with respect to ride through | Distribution

## 2. Options Matrix- Design Comp.
DER Ride Through Task Force
DER Ride Through
OPTIONS MATRIX
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E
* | Implementation |  |  | An IEEE 1547-2018 Cat III or CA Rule 21 certified inverter with trip points (UV1, UV2, OV1, OV2, UF1, UF2, OF1, and OF2) adjusted to meet those specified herein, plus adjustment of the momentary cessation threshold to XXX% of nominal voltage (see Design Component 4) as per IEEE 1547-2018 clause 6.4.2.7.3, is type certified to meet theseride through capability requirements and meets the trip requirements. | Utility-developed Source Requirements Document with trip points (UV1, UV2, OV1, OV2, UF1, UF2, OF1, and OF2) adjusted to meet those specified herein, plus adjustment of the momentary cessation threshold to XXX% of nominal voltage (see Design Component 4), and with a corresponding UL1741SA listing, is type certified to meet these ride through capability requirements and meets the trip requirements.
1 | IEEE 1547-2018 Abnormal Conditions Category |  | IEEE 1547-2003 | Cat II | Cat III
2 | UV1 intermediate low voltage trip) |  | clearing time 2 seconds for V ≤ 0.88 p.u. (no ride through) | clearing time 2 seconds at V < 0.88 p.u. (implies 1.84 second ride through as specified in Cat II) | clearing time 10 seconds at V < 0.88 p.u. (ride through between 3 - 5s as specified in Cat II) | clearing time 11 seconds at V < 0.88 p.u. (ride through between 3 - 5s as specified in Cat II) | clearing time 21 seconds at V < 0.88 p.u. (ride through for 10s or 20s as specified in Cat III)
3 | UV2 severe low voltage trip) |  | clearing time 0.16 seconds for V ≤ 0.50 p.u. (no ride through) | clearing time 0.32 seconds at V < 0.45 p.u. (implies 0.16 second ride through in "permissive operation" mode down to 0.30 p.u. as specified in Cat II) | clearing time 1.1 seconds at V < 0.45 p.u. (implies 0.16 second ride through in "permissive operation" mode down to 0.30 p.u. as specified in Cat II) | clearing time 1.5 seconds at V < 0.5 p.u. (implies 0.16 second ride through in "permissive operation" mode down to 0.30 p.u. as specified in Cat II) | clearing time 2 seconds at V < 0.5 p.u. (with 1 second of ride through in "permissive operation" mode down to 0.0 p.u. as specified in Cat III)
4 | Additional requirements |  | NA | "Mandatory operation" mode required in Cat II "permissive operation" regime, and for V < 0.30 p.u., add "ride through in momentary cessation" for 0.160 seconds followed by "momentary cessation" until trip at 0.320 s. | Within Cat II "Permissive Operation" regime, Mandatory Operation mode required for V > 0.50 p.u., and Momentary Cessation mode required for V < 0.50 p.u.
5 | OV1 (intermediate high voltage trip) |  | clearing time 1 second for V ≥ 1.1 p.u. (no ride through) | Use 1547-2018 Cat II default: clearing time 2 seconds for V > 1.1 p.u. (with stepped ride through between 0.20 and 1 seconds, as specified in Cat II) | Use 1547-2018 Cat III default: clearing time 13 seconds for V > 1.1 p.u. (with ride through in momentary cessation for 12 seconds, as specified in Cat III) |  |  |  | Low
6 | OV2 (severe high voltage trip) |  | clearing time 0.160 seconds for V ≥ 1.2 p.u. (no ride through) | Use 1547-2018 Cat II default: clearing time 0.160 seconds for V > 1.2 p.u., with implication of no ride through as specified in Cat II | Use 1547-2018 Cat III default: clearing time 0.160 seconds for V > 1.2 p.u., with implication of no ride through as specified in Cat III |  |  |  | Low - Medium
7 | UF1 (intermediate low frequency trip) |  | clearing time 0.160 seconds for f ≤ 59.3 Hz (no ride through) | Use 1547-2018 default: clearing time 300 seconds at f < 58.5 Hz (with 299 seconds of ride through) |  |  |  |  | Low - High
8 | UF2 (severe low frequency trip) |  | clearing time 0.160 seconds for f ≤ 57 Hz (no ride through) | Use 1547-2018 default: clearing time 0.160 seconds at f < 56.5 Hz (with no ride through below 57 Hz) | clearing time 0.160 seconds at f < 57 Hz (with no ride through below 57 Hz) (ComEd Tariff) |  |  |  | Medium
9 | OF1 (intermediate high frequency trip) |  | NA | Use 1547-2018 default: clearing time 300 seconds for f ≥ 61.2 Hz (ride through for 299 seconds for f ≤ 61.8 Hz as specified in IEEE 1547-2018) |  |  |  |  | Medium - High
10 | OF2 (severe high frequency trip) |  | clearing time 0.160 seconds for f ≥ 60.5 Hz (no ride through) | Use 1547-2018 default: clearing time 0.160 seconds for f ≥ 62 Hz (no ride through) |  |  |  |  | High
11 | Handling of DER that are physically incapable of meeting the recommended requirement |  |  | IEEE 1547-2018 Cat I | IEEE 1547-2018 Cat II but without the addition of momentary cessation etc. | Up to utility discretion | Cat II without M.C. if possible, otherwise Cat I
12
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attibute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
DER Ride Through Task Force
DER Ride Through
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
DER Ride Through Task Force
DER Ride Through
SOLUTION OPTION DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Corresponding cell number from Options Matrix (ex. 1A, 1B, 2A, etc.) | <enter detailed description of this option>

## 3. Package Matrix
DER Ride Through Task Force
DER Ride Through
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1
2
3
4
5
6
7
8
9 | [8 empty] | Low
10 | [8 empty] | Low - Medium
Low - High
Medium
Instructions: | [8 empty] | Medium - High
1. Copy over design component, priority, and status quo columns from options matrix | [8 empty] | High
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
DER Ride Through Task Force
DER Ride Through
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
DER Ride Through Task Force
DER Ride Through
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description

## Revision History
DER Ride Through Task Force
DER Ride Through
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3