## 2016-2017 Parameters
2016-2017 RPM Base Residual Auction Planning Parameters | [5 empty] | 2013-05-29 | 734653-v7
Updated on 5/29/2013 - Added Post-Clearing Credit Rate.
| RTO | Notes:
Installed Reserve Margin (IRM) | 15.6% | 1. Load data: from 2013 Load Report.
Pool-Wide Average EFORd | 5.69% | 2. Adjustments were made in the Zonal Peak Load Forecast of AEP, DEOK, and EKPC to account for EKPC integration.
Forecast Pool Requirement (FPR) | 1.0902 | 3. See "Net CONE" worksheet for Net CONE calculations.
Demand Resource (DR) Factor | 0.955 | Planning Parameters were updated on 4/16/2013 to reflect: (1) FRR Elections for which FRR Obligations were satisfied by the 4/13/2013 deadline; (2) increased CETL for SWMAAC, PEPCO and DPL SOUTH LDAs associated with customer-funded upgrades for which ICTR certifications were made by the 3/29/2013 deadline; and (3) 13 MW decrease in EKPC forecast load due to correction of historical load data used in original EKPC load forecast.
Preliminary Forecast Peak Load | 165412
Short-Term Resource Procurement Target | 2.5%
Pre-Clearing BRA Credit Rate, $/MW | 36193.04 | Limited DR Reliability Targets revised based on FERC approved alternate methodology (Filing 20121130-er13-486-000).
LOCATIONAL DELIVERABILITY AREA (LDA)
| RTO | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland
CETO | NA | 5220 | 6140 | 5840 | 6450 | 2450 | 1580 | 2730 | 5390 | 3800
CETL | NA | 6495 | 8916 | 8786 | 6581 | 2936 | 1901 | 6846 | 7881 | 5245
Reliability Requirement | 180332.2 | 72299 | 39694 | 17316 | 12870 | 6440 | 3160 | 9012 | 16255 | 6164
Total Peak Load of FRR Entities | 13029.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Preliminary FRR Obligation | 14204.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reliability Requirement adjusted for FRR | 166127.5 | 72299 | 39694 | 17316 | 12870 | 6440 | 3160 | 9012 | 16255 | 6164
Short-Term Resource Procurement Target | 4153.2 | 1664.7403 | 907.5669 | 383.9696 | 288.9039 | 140.1184 | 66.467 | 185.3345 | 362.3563 | 124.3459
Net CONE, $/MW-Day (UCAP Price) | 330.53 | 276.9 | 329.94 | 276.9 | 329.94 | 329.94 | 329.94 | 276.9 | 362.64 | 362.64
Variable Resource Requirement Curve:
Point (a) UCAP Price, $/MW-Day | 495.8 | 415.35 | 494.91 | 415.35 | 494.91 | 494.91 | 494.91 | 415.35 | 543.96 | 543.96
Point (b) UCAP Price, $/MW-Day | 330.53 | 276.9 | 329.94 | 276.9 | 329.94 | 329.94 | 329.94 | 276.9 | 362.64 | 362.64
Point (c) UCAP Price, $/MW-Day | 66.11 | 55.38 | 65.99 | 55.38 | 65.99 | 65.99 | 65.99 | 55.38 | 72.53 | 72.53
Point (a) UCAP Level, MW | 157663 | 68758 | 37756.3 | 16482.7 | 12247.1 | 6132.8 | 3011.5 | 8592.8 | 15470.8 | 5879.7
Point (b) UCAP Level, MW | 163411.4 | 71259.7 | 39129.8 | 17081.8 | 12692.4 | 6355.6 | 3120.9 | 8904.6 | 16033.3 | 6093
Point (c) UCAP Level, MW | 169159.7 | 73761.4 | 40503.3 | 17681 | 13137.8 | 6578.4 | 3230.2 | 9216.5 | 16595.7 | 6306.3
Customer-Funded ICTRs Awarded | NA | 159 | NA | 444 | NA | NA | 37 | 191 | NA | NA
Post-Clearing BRA Credit Rate (LMT), $/MW | 7300 | 8696.49 | 8696.49 | 8696.49 | 15987 | 15987 | 8696.49 | 8696.49 | 7300 | 7300
Post-Clearing BRA Credit Rate (ES), $/MW | 7300 | 8696.49 | 8696.49 | 8696.49 | 15987 | 15987 | 8696.49 | 8696.49 | 8338.79 | 8338.79
Post-Clearing BRA Credit Rate (ANL), $/MW | 7300 | 8696.49 | 8696.49 | 8696.49 | 15987 | 15987 | 8696.49 | 8696.49 | 8338.79 | 8338.79
Min Ext Summer Resource Req'ment, MW | 158512.2 | 62179.2 | 28559.2 | 7503.3 | 5483.4 | 3113.3 | 1114.3 | 1712.9 | 7668.1 | 676.8
Min Annual Resource Req'ment, MW | 149469.1 | 58109.3 | 24606.9 | 6183.2 | 4214.2 | 2503.1 | 903.5 | 750 | 6200.8 | 0
FRR Load Requirements:
Min % Internal Resource Req'ment | NA | 98.8% | 84.8% | 55.5% | 54.4% | 62.5% | 47.4% | 29.2% | 57.8% | 18.5%
Min % Ext Summer Resource Req'ment | 95.02% | 86% | 71.95% | 43.33% | 42.61% | 48.34% | 35.26% | 19.01% | 47.17% | 10.98%
Min % Annual Resource Req'ment | 89.12% | 80.37% | 61.99% | 35.71% | 32.74% | 38.87% | 28.59% | 8.323% | 38.15% | 0%
LDA CETO/CETL Data; Zonal Peak Loads, Base Zonal FRR Scaling Factors, and Zonal Short-Term Resource Procurement Target.
* (Asterisk) – LDA has adequate internal resources to meet the reliability criterion.
ATSI, DPL and PS Zonal peak loads and Short-Term Resource Procurement Targets include the corresponding sub-zonal values.
LDA/Zone | CETO | CETL (Changes shown in red) | CETL to CETO Ratio | 2012 Zonal W/N Coincident Peak Loads | Preliminary Zonal Peak Load Forecast | Base Zonal FRR Scaling Factor | Short-Term Resource Procurement Target | FRR Portion of the Preliminary Peak Load Forecast | Preliminary Zonal Peak Load Forecast less FRR load**
RTO | NA | NA | NA | 154501.8 | 165412 | NA | 4153.2 | 13029.4 | 152382.6
AE | 1030 | > 1185 | > 115% | 2600 | 2782 | 1.07 | 75.8236 | 0 | 2782
AEP | 2110 | > 2427 | > 115% | 22663.9 | 24007.6 | 1.0593 | 324.4799 | 12102.3 | 11905.3
APS | 1970 | > 2266 | > 115% | 8210 | 8786 | 1.0702 | 239.4631 | 0 | 8786
ATSI | 5390 | 7881 | 146.2% | 12660 | 13295 | 1.0502 | 362.3563 | 0 | 13295
ATSI-CLEVELAND | 3800 | 5245 | 138% | NA | 4562.3 | NA | 124.3459 | 0 | 4562.3
BGE | 5130 | > 5900 | > 115% | 6870 | 7288 | 1.0608 | 198.635 | 0 | 7288
COMED | 1330 | > 1530 | > 115% | 21650 | 23504 | 1.0856 | 640.6034 | 0 | 23504
DAYTON | 960 | > 1104 | > 115% | 3230 | 3556 | 1.1009 | 96.9191 | 0 | 3556
DEOK | 3800 | > 4370 | > 115% | 5246.5 | 5572.2 | 1.0621 | 127.4938 | 894.4 | 4677.8
DLCO | 1350 | > 1553 | > 115% | 2800 | 2996 | 1.07 | 81.6562 | 0 | 2996
DOM | -70 | * | * | 18570 | 20415 | 1.0994 | 556.4125 | 0 | 20415
DPL | 1000 | > 1150 | > 115% | 3950 | 4212 | 1.0663 | 114.7984 | 0 | 4212
DPL SOUTH | 1580 | 1901 | 120.3% | NA | 2438.7 | NA | 66.467 | 0 | 2438.7
EKPC | 580 | > 667 | > 115% | 2096.4 | 2200.2 | 1.0495 | 59.0754 | 32.7 | 2167.5
JCPL | 3300 | > 3795 | > 115% | 5960 | 6381 | 1.0706 | 173.9147 | 0 | 6381
METED | 1170 | > 1346 | > 115% | 2820 | 3068 | 1.0879 | 83.6186 | 0 | 3068
PECO | 2860 | > 3289 | > 115% | 8320 | 8908 | 1.0707 | 242.7883 | 0 | 8908
PENLC | 1300 | > 1495 | > 115% | 2740 | 3044 | 1.1109 | 82.9645 | 0 | 3044
PEPCO | 2730 | 6846 | 250.8% | 6540 | 6800 | 1.0398 | 185.3345 | 0 | 6800
PL (incl. UGI) | 1360 | > 1564 | > 115% | 7075 | 7581 | 1.0715 | 206.6208 | 0 | 7581
PS | 6450 | 6581 | 102% | 10100 | 10600 | 1.0495 | 288.9039 | 0 | 10600
PS NORTH | 2450 | 2936 | 119.8% | NA | 5141 | NA | 140.1184 | 0 | 5141
RECO | NA | NA | NA | 400 | 416 | 1.04 | 11.3381 | 0 | 416
EMAAC | 6140 | 8916 | 145.2% | NA | 33299 | NA | 907.5669 | 0 | ** Used to allocate Short-Term Resource Procurement Target to Zones.
SWMAAC | 5840 | 8786 | 150.4% | NA | 14088 | NA | 383.9696 | 0
Western MAAC | -3840 | * | * | NA | 13693 | NA | 373.2038 | 0
MAAC | 5220 | 6495 | 124.4% | NA | 61080 | NA | 1664.7403 | 0
Western PJM | 5940 | > 6831 | > 115% | NA | 83917 | NA | 1932.0472 | 13029.4
Limiting conditions at the CETL for modeled LDAs:
LDA | Violation/Limiting Facility
MAAC | Thermal/Sandy Springs-High Ridge 230 kV
EMAAC | Voltage/Loss of Keeney - Rock Springs 500 kV
SWMAAC | Thermal/Graceton - Bagley 230 kV
PS | Thermal/Roseland - Cedar Grove 230 kV F
PSNORTH | Thermal/Cedar Grove F - Clifton K 230 kV line
DPLSOUTH | Thermal/Easton - Trappe Tap 69 kV
PEPCO | Thermal/Conastone - Northwest 230 kV
ATSI | Thermal/Ashtabula 345/138 kV transformer
ATSI-CLEVELAND | Thermal/Ashtabula 345/138 kV transformer

## Net CONE
RPM CONE and E&AS Values for 2016/2017 Base Residual Auction
CONE values are as filed on November 21, 2012, in Docket No. ER12-513-000 and approved by FERC January 31, 2013.
ICAP to UCAP Conversion Factor:
UCAP Price = ICAP Price/(1 - Pool-Wide Average EFORd)
Pool-Wide Average EFORd for 2016/2017 = | 5.69%
CONE Area 1: AE, DPL, JCPL, PECO, PS, RECO
CONE Area 2: BGE, PEPCO
CONE Area 3: AEP, APS, ATSI, ComEd, Dayton, DEOK, Duquesne (DLCo), EKPC
CONE Area 4: MetEd, Penelec, PPL
CONE Area 5: Dominion
MAAC CONE used is the lowest of the three CONE Areas 1, 2, and 4.
| CONE Area 1 | CONE Area 2 | CONE Area 3 | CONE Area 4 | CONE Area 5 | MAAC: Used Area 2 CONE | RTO
Settlement CONE (2015/2016) approved by FERC: Levelized Revenue Requirement, $/MW-Year | 140000 | 130600 | 127500 | 134500 | 114500 | 130600 | 128000
12 Months Handy Whitman Index (July 1, 2012) | 8.9% | 8.9% | 9.4% | 8.9% | 9.1% | 8.9% | 8.9%
Region basis for the Handy Whitman Index | North Atlantic | North Atlantic | North Central | North Atlantic | South Atlantic | North Atlantic | North Atlantic
2016/2017 BRA CONE, escalated by Handy Whitman Index, $/MW-Year | 152460 | 142223.4 | 139485 | 146470.5 | 124919.5 | 142223.4 | 139392
Historic (2010-2012) Net Energy Revenue Offset, $/MW-Year for the Zone in the CONE Area Specified | 36685.9786 | 44707.4732 | 12453.4679 | 32929.4491 | 34129.0462 | 44707.4732 | 23414.7349
Zonal LMP used for Net Energy Offset Calculation | AE Zonal LMP | BGE Zonal LMP | ComEd Zonal LMP | MetEd Zonal LMP | Dominion Zonal LMP | BGE Zonal LMP | PJM Average LMP
Ancillary Services Offset, $/MW-Year per Tariff | 2199 | 2199 | 2199 | 2199 | 2199 | 2199 | 2199
Net CONE, $/MW-Day, ICAP Price | 311.1644 | 261.1423 | 342.0069 | 305.0467 | 242.7163 | 261.1423 | 311.7213
Net CONE, $/MW-Day, UCAP Price | 329.94 | 276.9 | 362.64 | 323.45 | 257.36 | 276.9 | 330.53

## Key Transmission Upgrades
New Key Transmission Upgrades included for 2016/2017 model
Upgrade ID | Description | Transmission Owner
b1251 | Rebuild the existing Bagley - Raphael Rd. 230 kV line to double circuit 230 kV line | BGE
b1589 | Re-configure the Kearny 230 kV substation and loop the P-2216-1 (Essex - NJT Meadows) 230 kV circuit | PSEG
b1591 | Reconductor the underground portion of the Richmond - Waneeta 230 kV, replace terminal equipments, and replace three 230 kV circuit breakers to give an emergency rating of 1195 MVA | PECO
b1592 | Reconductor the Oak Grove – Bowie 230 kV circuit and upgrade terminal equipments at Oak Grove and Bowie 230 kV substations | PEPCO
b1593 | Reconductor the Bowie - Burtonsville 230 kV circuit and upgrade terminal equipments at Bowie and Burtonsville 230 kV substations | PEPCO
b1594 | Reconductor the Oak Grove – Bowie 230 kV ‘23042’ circuit and upgrade terminal equipments at Oak Grove and Bowie 230 kV substations | PEPCO
b1595 | Reconductor the Bowie – Burtonsville 230 kV ‘23042’ circuit and upgrade terminal equipments at Oak Grove and Burtonsville 230 kV substations | PEPCO
b1596 | Reconductor the Dickerson station “H” – Quince Orchard 230 kV ‘23032’ circuit and upgrade terminal equipments at Dickerson station “H” and Quince Orchard 230 kV substations | PEPCO
b1597 | Reconductor the Oak Grove - Aquasco 230 kV ‘23062’ circuit and upgrade terminal equipments at Oak Grove and Aquasco 230 kV substations | PEPCO
b1663 | Install a new 765/138 transformer, 6 new 138 kV breakers at Jackson's Ferry, breaker disconnect switches and associated bus work, 2 new 138 kV breakers at Wythe, breaker disconnect switches and associ | AEP
b1663.2 | Install 2 765 kV circuit breakers, breaker disconnect switches and associated bus work for the new 765 kV breakers, and new relays for the 765 kV breakers at Jackson's Ferry | AEP
b1690 | Build a new third 230 kV line into the Red Bank 230 kV substation | JCPL
b1694 | Rebuild Loudoun - Brambleton 500 kV | Dominion
b1697 | Build a 2nd Clark - Idylwood 230 kV line and install 230 kV gas-hybrid breakers at Clark | Dominion
b1698 | Install a 2nd 500/230 kV transformer at Brambleton | Dominion
b1699 | Reconfigure Line #203 to feed Edwards Ferry sub radial from Pleasant View 230 kV and install new breaker bay at Pleasant View Sub | Dominion
b1701 | Reconductor Fredericksburg - Cranes Corner 230 kV | Dominion
b1787 | Build a second 230 kV circuit from Cox's Corner - Lumberton | PSEG
b1800 | Build a 500 MVAR SVC at Hunterstown 500 kV | ME
b1801 | Build a 250 MVAR SVC at Altoona 230 kV | PENELEC
b1804 | Build a 600 MVAR SVC at Meadow Brook 500 kV | APS
b1805 | Build a 250 MVAR SVC at Mt. Storm 500 kV & change voltage regulation at Mt. Storm to 1.05 pu | Dominion
b1813.8 | Build a new Paupack - North 230 kV line (Approximately 21 miles) | PPL
b1819 | Rebuild the Robinson Park - Sorenson 138 kV line corridor as a 345 kV double circuit line with one side operated at 345 kV and one side at 138 kV | AEP
b1847 | Add 230 MVAR of capacitors at TSS 141 Pleasant Valley | ComEd
b1864.1 | Add two additional 345/138 kV transformers at Kammer | AEP
b1864.2 | Add second West Bellaire - Brues 138 kV circuit | AEP
b1905.1 | Surry to Skiffes Creek 500 kV Line (7 miles overhead) | Dominion
b1905.2 | Surry 500 kV Station Work | Dominion
b1905.3 | Skiffes Creek 500-230 kV Tx and Switching Station | Dominion
b1905.4 | New Skiffes Creek - Whealton 230 kV line | Dominion
b1906.5 | Install a third 500/230 kV TX at Yadkin | Dominion
b1907 | Install a 3rd 500/230 kV TX at Clover | Dominion
b1908 | Rebuild Lexington – Dooms 500 kV | Dominion
b1909 | Uprate Bremo – Midlothian 230 kV to its maximum operating temperature | Dominion
b1910 | Build a Suffolk – Yadkin 230 kV line (14 miles) and install 4 breakers | Dominion
b1911 | Add a second Valley 500/230 kV TX | Dominion
b1912 | Install a 500 MVAR SVC at Landstown 230 kV | Dominion
b1913.1 | Convert Eastlake unit 1 to synchronous condensers | ATSI
b1913.2 | Convert Eastlake unit 2 to synchronous condensers | ATSI
b1913.3 | Convert Eastlake unit 3 to synchronous condensers | ATSI
b1914 | Convert Lakeshore 18 to a synchronous condenser | ATSI
b1924 | Build a new Mansfield - Northfield ("Glen Willow") 345 kV line | ATSI
b1936 | Build new Allen Jct - Midway - Lemonye 345 kV line (48 miles of open tower position) | ATSI
b1948 | Establish a new 765/345 interconnection at Sporn. Install a 765/345 kV transformer at Mountaineer and build ¾ mile of 345 kV to Sporn | AEP
b1959 | Build a new West Fremont-Groton-Hayes 138kV line | ATSI
b1972 | Replace disconnect switch on the South Canton 765/345 kV transformer | AEP
b1977 | Build new Toronto 345/138 kV substation by looping in the Sammis – Wylie Ridge 345 kV line and tie in four 138 kV lines | ATSI
b1983 | Add 150 MVAR SVC and a 100 MVAR capacitor at New Castle | ATSI
b2003 | Construct a Whippany to Montville 230 kV line (6.4 miles) | JCPL
b2017 | Reconductor or rebuild Sporn - Waterford - Muskingum River 345 kV line | AEP
b2019 | Establish Burger 345/138 kV station | AEP
b2127 | Install two 300 MVAR SVC's on the 138 kV red and blue buses at Prospect Heights substation | ComEd
Key Transmission Upgrades included for 2015/2016 model but not included for 2016/2017 model
b0497 | Install a second Conastone - Graceton 230 kV circuit and replace Conastone 230 kV breaker 2323/2302 | BGE
b1016 | Rebuild Graceton - Bagley 230 kV as double circuit line using 1590 ACSR. Terminate new line at Graceton with a new circuit breaker. | BGE
b1383 | Install 2nd 500/138 kV transformer at 502 Junction | APS

## Min Res Req'ments
2016/2017 Minimum Resource Requirements
Forecast Pool Requirement | 1.0902
Demand Resource Factor | 0.955
Quantities are in Unforced Capacity Megawatts | PJM Region | MAAC | EMAAC | SWMAAC | PS | PS NORTH | DPL SOUTH | PEPCO | ATSI | ATSI-Cleveland
Reliability Requirement adjusted for FRR | 166127.5 | 72299 | 39694 | 17316 | 12870 | 6440 | 3160 | 9012 | 16255 | 6164
CETL | NA | 6495 | 8916 | 8786 | 6581 | 2936 | 1901 | 6846 | 7881 | 5245
Preliminary Peak Load Forecast | 165412 | 61080 | 33299 | 14088 | 10600 | 5141 | 2438.7 | 6800 | 13295 | 4562.3
FRR Peak Load | 13029.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Load Forecast adjusted for FRR | 152382.6 | 61080 | 33299 | 14088 | 10600 | 5141 | 2438.7 | 6800 | 13295 | 4562.3
Limited Demand Resource Reliability Target
Percent of Preliminary Forecast Peak Load * | 4.8% | 5.7% | 6.4% | 7% | 7.3% | 7.3% | 5.7% | 6.4% | 5.1% | 5.1%
Unforced Capacity, MW | 7615.2851 | 3624.7949 | 2218.8131 | 1026.7316 | 805.6349 | 390.7329 | 144.7247 | 453.1046 | 705.9404 | 242.2499
Extended Summer Demand Resource Reliability Target
Percent of Preliminary Forecast Peak Load | 10.5% | 12.1% | 17.8% | 16% | 18.8% | 18.7% | 14% | 20% | 15.7% | 26.1%
Unforced Capacity, MW | 16658.4361 | 7694.74 | 6171.0738 | 2346.8151 | 2074.7858 | 1000.9186 | 355.4643 | 1415.9518 | 2173.1892 | 1239.7494
Minimum Resource Requirements for RPM, MW
Minimum Extended Summer Resource Requirement | 158512.2 | 62179.2 | 28559.2 | 7503.3 | 5483.4 | 3113.3 | 1114.3 | 1712.9 | 7668.1 | 676.8
Minimum Annual Resource Requirement | 149469.1 | 58109.3 | 24606.9 | 6183.2 | 4214.2 | 2503.1 | 903.5 | 750 | 6200.8 | 0
Minimum Resource Requirements for FRR (% Obligation)
Minimum Extended Summer Resource Requirement | 95.02% | 86% | 71.95% | 43.33% | 42.61% | 48.34% | 35.26% | 19.01% | 47.17% | 10.98%
Minimum Annual Resource Requirement | 89.12% | 80.37% | 61.99% | 35.71% | 32.74% | 38.87% | 28.59% | 8.323% | 38.15% | 0%
* Limited Demand Resource Reliability Targets revised based on FERC approved alternate methodology (Filing 20121130-er13-486-000).