## 1. Interest Identification
PC - Enhanced Inverter
Interest Identification
Instructions: List interests of all parties on this page.
1 | Avoid a planning and operational issue within the eastern interconnection
2 | Proactively explore any issue effecting grid reliability
3 | Review existing standards and ensure they are relevant to emerging technologies as well
4 | Improve coordination/eliminate conflicts between interconnection standards for transmission-connected and distributed energy resources
5 | Leverage available grid-support capabilities of inverters to the extent possible
6 | Seek cost-effective solutions to reliability issues.
7 | Develop standards for PJM that have broad applicability in other regions and nationally.
8 | Extend applicability of standards to generation and storage connected at the distribution level
9 | Detailed specifications to maintain flexibility for TO voltage
10 | Develop recommenedation for over-frequency curtailment requirement
11 | Clearly define applicability as it relates to size, technology and interconnection process (transmisssion, distribution)
12 | Explore market based mechanisms to achieve the optimum result | PJM to research
13 | Explore other technology solution(s) than can provide grid services | PJM to research
14
15

## 2. Options Matrix- Design Comp.
PC - Enhanced Inverter
OPTIONS MATRIX
Strive for simplicity
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D
1 | Active Power Control - upon request (curtailments) - Attachement O- Schedule H of PJM Tariff; PJM Manual 14D Manual 12, Attachment B - Already a requirement for PJM inverter based jurisdictional generators |  | All PJM connected FERC jurisdictional inverter based generators* must have the capability to receive and respond to curtailment instructions from dispatch. Pool-scheduled or self-scheduled resources must be operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | No change
2 | Active Power Control - automatic (e.g. for frequency control) - Attachement O- Schedule H of PJM Tariff; PJM Manual 14D | Medium | No specific requirements for active power control for Inverter based technologies. | PJM connected FERC jurisdictional inverter based generators* must have the capability to : 1) Have an automated reduction in active power in response to high system frequency with droop characteristics 2) Have an automated increase in active power in response to low system frequency with droop characteristics when the resource has been curtailed by PJM either for economic or reliability reasons has additional power available for generation at the time of the request
3 | Reactive Power Support / Power Factor Control - OATT at Part VI, Section 4.7 in Att. O, App. 2, of the Tariff for Reactive Power Requirements for new and existing facilities. | High | For wind and other asynchronous generator: 0.95 leading to 0.95 lagging if identified during the system impact study. For new synchronous generation:0.95 leading to 0.9 lagging | PJM connected FERC jurisdictional inverter based generators* must have the capability to autonomously provide dynamic reactive support within a range of 0.95 leading to 0.95 lagging at inverter terminals unless system impact study or TO establishes a need for more conservative limits | PJM connected FERC jurisdictional inverter based generators* must have the capability to respond to a centrally dispatched signal to provide dynamic reactive support within a range of 0.95 leading to 0.95 lagging at inverter terminals unless system impact study or TO establishes a need for more conservative limits
4 | Voltage Ride-Through - Schedule H of the PJM Tariff and Attachment G of Manual 14 B | High | Current regulations for LVRT come from FERC Order 661A and are documented in Manual 14B. LVRT requires wind turbine generators to stay connected to the grid for a number of conditions identified by FERC(for upto 9 cycles). This is specific for Wind Turbines and not applicable to other technologies. | Expand existing Voltage ride through requirements for wind generators to all PJM connected FERC jurisdictional inverter based generators* and adhere to NERC PRC-024 standard irrespective of generator size |  |  |  | Low
5 | Frequency Ride-Through - PJM Tariff, Schedule H and Section 7.1.1, Manual 14 D | High | Inverter operation is mostly governed by IEEE 1547. IEEE 1547 drives inverter design more than any specific system requirements. | PJM connected FERC jurisdictional inverter based generators* must adhere to NERC PRC-024 standard irrespective of generator size |  |  |  | Low - Medium
6 | Communication capabilities |  | Require all generation in the PJM interconnection queue greater than 20 MW to have capability to support two way communication. Pool-scheduled or self-scheduled wind resources must only be eligible to receive LOC credits if they were operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | No change |  |  |  | High
7 | Ramp rate control | Medium | Currently there are no PJM requirements. | PJM connected FERC jurisdictional inverter based generators* must have the capability to limit ramp rates |  |  |  | Medium
* Definition: PJM connected FERC jurisdictional inverter based generators are defined as asynchronous generation in the PJM footprint that either have a WMPA or an ISA

## 2a. Component Details
PC - Enhanced Inverter
COMPONENT DETAILS
Design Component |  | Detailed Description
1 | Active Power Control - upon request (curtailments) | Ability to limit active power output due to congestion/reliability in response to central control
2 | Active Power Control - automatic (e.g. for frequency control, or to limit ramp rates) | Ability to automatically control active power for reliability purposes
3 | Reactive Power Support / Power Factor Control - Central | Ability to absorb or generate reactive power under central control
4 | Reactive Power Support / Power Factor Control - Autonomous | Ability to absorb or generate reactive power under autonomous control
5 | Voltage Ride-Through | Ability to remain connected to the system during transient voltages
6 | Frequency Ride-Through | Ability to remain connected to the system during transient frequency
7 | Communication capabilities | Ability to have reliable and secure communication in additional to already required communication standards for participants in PJM markets
8 | Ramp rate control | Ability to limit ramp rate in either direction
*Definition
All requirements referred to in the matrix are applicable only to "PJM inverter based Jurisdictional Generators". PJM inverter based Jurisdictional generators are defined as inverter based generators that have either a WMPA or an ISA with PJM
Add

## 2b. Solution Details
PC - Enhanced Inverter
SOLUTION DETAILS
Package Solutions2
| A | B | C | D | E
1
2
3
4
5

## 3. Package Matrix
PC - Enhanced Inverter
PACKAGE/ PROPOSAL MATRIX
Packages
# | Design Components | Priority | Status Quo | A | B | C | D | E
1 | Active Power Control - upon request (curtailments) - Attachement O- Schedule H of PJM Tariff; PJM Manual 14D Manual 12, Attachment B - Already a requirement for PJM inverter based jurisdictional generators |  | All PJM connected FERC jurisdictional inverter based generators* must have the capability to receive and respond to curtailment instructions from dispatch. Pool-scheduled or self-scheduled resources must be operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | No change
2 | Active Power Control - automatic (e.g. for frequency control) - Attachement O- Schedule H of PJM Tariff; PJM Manual 14D | Medium | No specific requirements for active power control for Inverter based technologies. | PJM connected FERC jurisdictional inverter based generators* must have the capability to : 1) Have an automated reduction in active power in response to high system frequency with droop characteristics 2) Have an automated increase in active power in response to low system frequency with droop characteristics when the resource has been curtailed by PJM either for economic or reliability reasons has additional power available for generation at the time of the request.
3 | Reactive Power Support / Power Factor Control - OATT at Part VI, Section 4.7 in Att. O, App. 2, of the Tariff for Reactive Power Requirements for new and existing facilities. | High | For wind and other asynchronous generator: 0.95 leading to 0.95 lagging if identified during the system impact study. For new synchronous generation:0.95 leading to 0.9 lagging | PJM connected FERC jurisdictional inverter based generators* must have the capability to autonomously provide dynamic reactive support within a range of 0.95 leading to 0.95 lagging at inverter terminals unless system impact study or TO establishes a need for more conservative limits
4 | Voltage Ride-Through - Schedule H of the PJM Tariff and Attachment G of Manual 14 B | High | Current regulations for LVRT come from FERC Order 661A and are documented in Manual 14B. LVRT requires wind turbine generators to stay connected to the grid for a number of conditions identified by FERC(for upto 9 cycles). This is specific for Wind Turbines and not applicable to other technologies. | Expand existing Voltage ride through requirements for wind generators to all PJM connected FERC jurisdictional inverter based generators* and adhere to NERC PRC-024 standard irrespective of generator size
5 | Frequency Ride-Through - PJM Tariff, Schedule H and Section 7.1.1, Manual 14 D | High | Current requirements documented in Manual 14D | PJM connected FERC jurisdictional inverter based generators* must adhere to NERC PRC-024 standard irrespective of generator size
6 | Communication capabilities |  | Require all generation in the PJM interconnection queue greater than 20 MW to have capability to support two way communication. Pool-scheduled or self-scheduled wind resources must only be eligible to receive LOC credits if they were operated according to Tariff, Operating Agreement, and PJM Manual requirements, specifically, supervisory control and data acquisition (“SCADA”) capability to transmit data and receive instructions from PJM to protect system reliability | No change
7 | Ramp rate control | Medium | Currently there are no PJM requirements. | PJM connected FERC jurisdictional inverter based generators* must have the capability to limit ramp rates
8 | Implementation Timeframe |  |  | Effective date will apply to new queue requests |  |  |  |  | Low - High
Medium
Medium - High
High
* Definition: PJM connected FERC jurisdictional inverter based generators are defined as asynchronous generation in the PJM footprint that either have a WMPA or an ISA

## Parking Lot
PC - Enhanced Inverter
Interest Identification
Instructions: Use this space to document any items not specific to another topic area.
consideration for additional solutions other than inverters (ie - demand response)
inverter technolgies - what to pursue? - internal research