## Version History
PJM 2015 RTEP Proposal Window #2 Tracking Spreadsheet
Proposal Window: | 2015 RTEP Proposal Window 2
Window Opening Date: | 2015-08-05
Window Closing Date: | 2015-09-04
Current Spreadsheet Version | V1
V1: Original Posting for 10/8/2015 TEAC

## Tracking By Proposal
PJM 2015 RTEP Proposal Window #2 Tracking Spreadsheet
Proposal Window: | 2015 RTEP Proposal Window 2
Window Opening Date: | 2015-08-05
Window Closing Date: | 2015-09-04
Current Spreadsheet Version | V1
Project ID | Upgrade/Greenfield | Proposing Entity | Final Project Cost ($M) | Target Zone(s) | kV Level(s) | Analysis Type | FG# | Major Components/Project Description
2015_2-1A | Upgrade | First Energy | 4.065 | JCPL | 230; 34.5 | N-1 Thermal | JC-1, JC-2 | Replace the existing 125 MVA 230-34.5 kV #1 Transformer at Oceanview with a 168 MVA Transformer.
2015_2-1B | Upgrade | First Energy | 2.432 | JCPL | 115; 34.5 | N-1 Thermal | JC-3, JC-4 | Replace the existing 90 MVA 115-34.5 kV #1 Transformer at Deep Run with a 125 MVA Transformer.
2015_2-2A | Greenfield | Northeast Transmission Development | 7.4 | AEP | 138 | TO Thermal; TO Voltage | AEP-T1, AEP-T2, AEP-T3, AEP-T4, AEP-T6; AEP-V1, AEP-V2, AEP-V3 | Build a 138 kV switching station ("Grassy Creek") interconnecting the Summerfield-Switzer 138 kV line, the Ball Hollow-Natrium 138 kV line and the Tap to Somerton 138 kV line
2015_2-2B | Greenfield | Northeast Transmission Development | 6.2 | AEP | 138 | TO Thermal | AEP-T5, AEP-T6 | Build a double circuit 138 kV line from the Nottingham-Holloway 138 kV line to the Glencoe 138 kV substation
2015_2-2C | Greenfield | Northeast Transmission Development | 4 | AEP | 138 | TO Thermal | AEP-T5, AEP-T6 | Build a 138 kV line from the Nottingham-Holloway 138 kV line to the Glencoe 138 kV substation
2015_2-2D | Greenfield | Northeast Transmission Development | 18.4 | AEP | 138; 34.5 | TO Thermal; TO Voltage | AEP-T4, AEP-T10, AEP-T11; AEP-V2, AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Build a double circuit 138 kV line from the Nottingham-Reedsburg 138 kV line to a new 138/34.5 kV substation ("Smyrna 138 kV") and interconnecting to the Smyrna 34.5 kV substation
2015_2-2E | Greenfield | Northeast Transmission Development | 12.6 | AEP | 138; 34.5 | TO Thermal; TO Voltage | AEP-T4, AEP-T10, AEP-T11; AEP-V2, AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Build a 138 kV line from the Nottingham-Reedsburg 138 kV line to a new 138/34.5 kV substation ("Smyrna 138 kV") and interconnecting to the Smyrna 34.5 kV substation
2015_2-2F | Greenfield | Northeast Transmission Development | 19.8 | AEP | 138; 34.5 | TO Thermal; TO Voltage | AEP-T4, AEP-T10, AEP-T11; AEP-V2, AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Build a new 138 kV line from the Nottingham 138 kV switching station to a new 138/34.5 kV substation ("Smyrna 138 kV") and interconnecting to the Smyrna 34.5 kV substation
2015_2-2G | Greenfield | Northeast Transmission Development | 6 | AEP | 138 | TO Thermal | AEP-T5, AEP-T6 | Build a 138 kV switching station ("Oak Ridge") interconnecting the West Bellaire-Glencoe 138 kV line and the Nottingham-Holloway 138 kV line
2015_2-2H | Greenfield | Northeast Transmission Development | 6 | AEP | 138 | TO Thermal | AEP-T9 | Build a 138 kV switching station ("Rattle Creek") interconnecting the Hansonville-Meadowview 138 kV line and the Clinch River-Abingdon 138 kV line
2015_2-2I | Greenfield | Northeast Transmission Development | 29.7 | AEP | 138; 34.5 | TO Thermal; TO Voltage | AEP-T1, AEP-T2, AEP-T3, AEP-T4, AEP-T5, AEP-T6, AEP-T10, AEP-T11; AEP-V1, AEP-V2, AEP-V3, AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Build a 138 kV switching station ("Grassy Creek") interconnecting the Summerfield-Switzer 138 kV line, the Ball Hollow-Natrium 138 kV line and the Tap to Somerton 138 kV line. Build a 138 kV switching station ("Oak Ridge") interconnecting the West Bellaire-Glencoe 138 kV line and the Nottingham-Holloway 138 kV line. Build a double circuit 138 kV line from the Nottingham-Reedsburg 138 kV line to a new 138/34.5 kV substation ("Smyrna 138 kV") and interconnecting to the Smyrna 34.5 kV substation.
2015_2-3A | Greenfield | AEP | 25.19 | AEP | 69 | N-1 Thermal | AEP-T9 | South Abingdon station, install a 138/69kV step down transformer, one 138kV circuit breaker, one 138kV circuit switcher and one 69kV circuit breaker. Extend a new 8 miles 69kV line from the proposed South Abingdon station to the Arrowhead station. Arrowhead station, Install three 69kV circuit breakers.
2015_2-3B | Upgrade | AEP | 6.014 | AEP | 69 | N-1 Thermal | AEP-T5, AEP-T6 | Rebuild/upgrade line between Glencoe and Willow Grove Switch.
2015_2-3C | Greenfield | AEP | 24.32 | AEP | 138 | N-0 Thermal; N-0 Voltage | AEP-T10, AEP-T11; AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Install a new 138 kV line from Nottingham station to Smyrna station 138 kV, approximately 11 miles. Install 138 kV circuit breakers at Nottingham station and at Smyrna station. Install a 34.5 kV Vail Sw circuit breaker.
2015_2-3D | Greenfield | AEP | 21.9 | AEP | 138 | N-0 Thermal; N-0 Voltage | AEP-T10, AEP-T11; AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Install a new 69 kV line from Flushing station to Smyrna station, approximately 11.5 miles. Install circuit breakers at Flushing, Smyrna and Vail Sw station.
2015_2-3E | Greenfield | AEP | 22.57 | AEP | 138 | N-0 Thermal; N-0 Voltage | AEP-T10, AEP-T11; AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Install a new 34.5 kV line (to be built at 69 kV) from Flushing station to Smyrna station, approximately 11.5 miles. Install 69 kV circuit breakers (to be operated at 34.5 kV) at Smyrna station and at Flushing station. Install a 34.5 kV Vail Sw circuit breaker. Install a 69/34.5 kV 30 MVA transformer at Flushing station.
2015_2-3F | Greenfield | AEP | 14.355 | AEP | 138 | N-0 Thermal; N-0 Voltage | AEP-T10, AEP-T11; AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Build approximatley 11.5 miles of 34.5 kV line with 556.5 ACSR 26/7 Dove wood poles from Flushing station to Smyrna station.
2015_2-3G | Greenfield | AEP | 21.9 | AEP | 138 | N-0 Thermal; N-0 Voltage | AEP-T10, AEP-T11; AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Install a new 34.5 kV line from Slater station to Smyrna station, approximately 10.1 miles. Install circuit breakers at Slater, Smyrna, Nottingham and Vail Sw station.
2015_2-3H | Greenfield | AEP | 14.335 | AEP | 138 | N-0 Thermal; N-0 Voltage | AEP-T10, AEP-T11; AEP-V6, AEP-V7, AEP-V8, AEP-V9 | Install a new 34.5 kV line from Slater station to Smyrna station, approximately 10.1 miles. Install circuit breakers at Slater, Smyrna, Nottingham and Vail Sw station.
2015_2-3I | Greenfield | AEP | 25.7 | AEP | 138 | N-1 Thermal, N-1 Voltage Magnitude | AEP-T1, AEP-T2, AEP-T3, AEP-T4; AEP-V1, AEP-V2, AEP-V3 | Construct Herlan Station (Breaker and a half) and Herlan-Blue Racer 138kV circuit.
2015_2-3J | Greenfield | AEP | 17.8 | AEP | 138 | N-1 Thermal, N-1 Voltage Magnitude | AEP-T1, AEP-T2, AEP-T3, AEP-T4; AEP-V1, AEP-V2, AEP-V3 | Construct Herlan Station (ring Bus)and Herlan-Blue Racer 138kV circuit.
2015_2-4A | Upgrade | EKPC | 0.4 | EKPC | 69 | N-1 Voltage Magnitude | EKPC-V1 | Install a 25.511 MVAR, 69 KV capacitor bank at Sewellton Junction substation.
2015_2-4B | Upgrade | EKPC | 0.075 | EKPC | 69 | N-1 Thermal | EKPC-T1 | Upgrade 69kV bus at Summershade associated with the 161/69kV Auto Transformer. Uprate CT to 190 MVA.