## CT
Combustion Turbine Heat Rate & Cost Curves
Heat Rate Curves
Output | Heat Input | Heat Rate | Incrementals
(MW) | (MBtu/hr) | (Btu/kWh) | (Btu/kWh)
0 | 578.23 |  |  | No Load
70 | 879.02 | 12557.4286 | 4297 | Min
90 | 1054.57 | 11717.4444 | 8777.5 | Base
100 | 1157.28 | 11572.8 | 10271 | Peak
Conditions at 59F
a= | 578.23 | (No Load Fuel) |  |  |  | Fuel Cost | 4 | $/mmBtu
b= | 0.8122 |  |  |  |  | VOM | 75 | $/EOH
c= | 0.0498 |  |  |  |  | PF | 1.02 |  |  | 1st
[6 empty] | Average |  |  |  | Derivative |  |  | No Load = | 1363.3
Gas |  |  | Maintenance |  | Operating | Incremental | No Load = | 2359.1784 | $/hr | Incremental | Incremental | Incremental | Incremental | Operating
Net Gen | Heat Input | Heat Rate | Factor | Total Cost | Rate | Heat Rate |  | Incremental Cost |  | Heat Rate | Fuel Cost | Maint Cost | Cost | Rate
MW | MMBtu/Hr | Btu/Kwh |  | $/MWH | $/Hr | Btu/Kwh |  | $/MWH |  | Btu/Kwh | $/Hr | $/Hr | $/MWH
0
0 | 578.23 | [11 empty] | 32.83
70 | 879.104 | 12558.6286 | 1 | 52.3106 | 3661.7443 | 4298.2 | 4298.2 | 18.6081 | 18.6081 | 7784.2 | 2223.1675 | 75 | 32.831 | 3661.4675
90 | 1054.708 | 11718.9778 | 1 | 48.6468 | 4378.2086 | 8780.2 | 8780.2 | 35.8232 | 35.8232 | 9776.2 | 3589.8206 | 0 | 39.8869 | 4953.1206
100 | 1157.45 | 11574.5 | 4 | 50.224 | 5022.396 | 10274.2 | 10274.2 | 64.4187 | 64.4187 | 10772.2 | 4395.0576 | 225 | 66.4506 | 8008.3576