## Setup
Enter Stakeholder Committee Name in cell A2:
DER and Inverter-based Resources
Enter issue title (use title from Issue Tracking if applicable) in cell A5:
Solar-Battery Hybrid Resources

## 1. Interest Identification
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
Interest Identification
Instructions: List interests of all parties on this page.
1 | Ensure that solar-battery hybrid resources in the PJM interconnection queue have a clear understanding of the rules and requirements that apply to this resource type for the purposes of participation in PJM energy and ancillary services markets.
2 | Consideration of unique operational aspects of solar-battery hybrid resources.
3 | Operational visibility of each resource type, in real time, within a hybrid resource.
4 | Ensure that hybrid participation models can fully accommodate dc-coupled configurations, including metering requirements and ability to charge battery directly from co-located solar without scheduling or settlement implications.
Ensure the ability of dc-coupled hybrids to make use of co-located resources for charging the storage resource without incurring undue costs, such as for transmission or schedule deviations
7 | Ensure that well defined parameters and clear market rules are provided for all different potential configurations and that the parameters are coordinated between operations, markets and planning.
8 | Ensure that there are clear PJM Planning rules regarding changing project configurations once the study process has started.
9 | Ensure that PJM planning and operations are in agreement with how potential hybrid configurations will impact a resource's ability to charge or not charge from the grid.
10 | Ensure that metering provided to PJM Settlements is also sufficient for purposes of creating Renewable Energy Credits.
11
12
13
14
15
16
17
18
19
20

## 2. Options Matrix- Design Comp.
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
OPTIONS MATRIX
Updated: May 19, 2021
Solution Options2
# | Design Components1 | Priority | Status Quo | A | B | C | D | E | F
* | Implementation
Markets Items
1 | Definitions, including classification of hybrids relative to existing resource types (e.g., Intermittent Resource, Energy Storage Resource, etc). |  | “Combination Resource” shall mean a Generation Capacity Resource that has a component that has the characteristics of a Limited Duration Resource combined with (i) a component that has the characteristics of an Unlimited Resource or (ii) a component that has the characteristics of a Variable Resource. *Proposed as part of the Effective Load Carrying Capability draft RAA language "Energy Storage Resource" shall mean a resource capable of receiving electric energy from the grid and storing it for later injection to the grid that participates in the PJM Energy, Capacity and/or Ancillary Services markets as a Market Participant." | Mixed Technology Facility Resource - a resource facility composed of more than one generation and/or energy storage resource component behind the same point of interconnection. Hybrid Resource - a resource composed of one generation component and one energy storage resource component behind the same point of interconnection operating in the capacity, energy, and/or ancillary services market(s) as a single unit. Co-located Resource - a resource composed of at least one generation and one energy storage resource behind the same point of interconnection operating in the capacity, energy, and/or ancillary services market(s) as more than one unit. a component of a Mixed Technology Facility that operates in the capacity, energy, and/or ancillary services market(s) as a separate resource from the other components of such facility. "Open-Loop Hybrid Resource: A Hybrid Resource that can charge from the grid. An Open-Loop Hybrid Resource consisting of a solar component and a storage component is an Energy Storage Resource". Add to definition of Energy Storage Resource: "An Open-Loop Hybrid Resource consisting of a solar component and a storage component is an Energy Storage Resource." Standalone Energy Storage Resource - "an Energy Storage Resource that is not a Hybrid Resource." | Standalone Energy Storage Resource - "an Energy Storage Resource that is not a Hybrid Resource." Include in the defintion of Open-Loop Solar-Battery Hybrid - … "An Open-Loop Solar-Battery Hybrid is a type of Energy Storage Resource". Also add the inclusion to the definition of Energy Storage Resource. This would give open-loop hybrids the ability to opt-in to the Energy Storage Resource Participation Model, whcih includes the ability to schedule charging energy and inherit the accounting features of charging energy associated with Order 841. | Mixed Technology Resource - a resource composed of more than one generation and/or energy storage resource behind the same point of interconnection. Hybrid Resource - a resource composed of at least one generation and one energy storage resource behind the same point of interconnection operating in the capacity, energy, and/or ancillary services market(s) as a single unit. Co-located Resource - a resource composed of at least one generation and one energy storage resource behind the same point of interconnection operating in the capacity, energy, and/or ancillary services market(s) as more than one unit. Open-Loop Solar-Battery Hybrid - a Hybrid Resource with a solar component and a battery component that can charge the battery component from the grid. Closed-Loop Solar-Battery Hybrid - a Hybrid Resource with a solar component and a battery component that cannot charge the battery component from the grid. Tariff: have new term for Open-Loop Hybrids broadly: "A Hybrid Resource that can charge from the grid". Tariff term for ESR would have an inclusion specifically for hybrids that have a solar component and can charge from the grid.
2 | Generation/storage thresholds to be considered "hybrid resource" |  | N/A | Yes…TBD | No threshold, solar-battery mixed-technology resources may elect "hybrid" status with any ratio of generation to storage | Other terms in Manuals.
3 | Modeling Energy/Ancillary Services |  |  | For closed-loop hybrids: new model similar to the ESR Participation Model, except it has "solar only mode", does not have the non-energy ancillary services modes, and does not have any charging/negative power functionality use existing conventional market model for offers/clearing/dispatch of energy and ancillary services | For open-loop hybrids: include them as a type of Energy Storage Resource, which would give them the ability to opt-in to the Energy Storage Resource Participation Model, which includes the ability to schedule charging energy and inherit the accounting features of charging energy associated with Order 841. They would use a new model similar to the ESR Participation Model, except it has "solar only mode" and does not have the non-energy ancillary services modes. | Mixed Technology Facilities whose components are physically incapable of operating independently are modeled and participate in Capacity and Energy markets as a single Hybrid Resource Conditions that make a mixed-technology resource physically incapable of operating independently include: the sum of the nameplate power rating of the components is greater than 115% of the Maximum Facility Output; closed-loop hybrids.
4 | Market Operations of negative MW |  | Solar: N/A ESR: Only storage resources registered and using the ESR model can schedule negative MW. | See design component 3 solution B
5 | Regulation |  | All resources can participate in Regulation if they meet performance requirements. For co-located resources: battery component can participate in Regulation if submeter telemetry is provided. | All resources can participate in Regulation if they meet performance requirements. For co-located resources, battery resource can participate in Regulation if submeter telemetry is provided. For hybrid resources, two ways to provide regulation service are available: (1) Battery output is used to balance out intermittent renewable output, where resource response is measured at the point of interconnection meter. (2) Battery output is not used to balance out intermittent renewable output, and resource response is instead measured independently for the battery component level using submeter output/telemetry. | Status quo, except non-energy regulation only mode of ESR Participation Model is not available
6 | Reserves |  | Solar: Not included in reserve calculations; Can opt-in to providing spinning reserves. ESR: can offer Tier II SR by default, excluded from Tier I SR by default. DASR: solar and storage excluded by default. Reserve Pricing Reform filing: six reserves are defined: day-ahead and real-time equivalents of 10-minute online, 30-minute online, and 10-minute offline reserves. ESR are by default eligible to offer all reserves they are physically capable of providing. ESR must offer reserves consistent with rules for all other resource types. | Solar-battery hybrids excluded from Tier I SR, Tier II SR, and DASR by default, but can opt in with PJM review/approval (same as status quo for solar and storage). | Solar battery hybrid in which the battery has at least one hour of storage are included in Tier I SR, Tier II SR, and DASR by default. | Solar-battery hybrids can offer Tier II SR by default, excluded from Tier I SR estimates and DASR by default. Can opt in to Tier I SR estimates and DASR with an opt-in process informing PJM of the desire to participate, whereupon PJM will estimate Tier 1 SR and assign DASR in the same manner as other resources scheduling energy (same as status quo for Order 841 ESR Model Participants). Solar-battery hybrids treated the same as Reserve Pricing Reform approach to ESR.
7 | Capacity Market must offer |  | Intermittent Resources, Capacity Storage Resources, Demand Resources, Energy Efficiency Resources are not required to submit a Capacity Performance sell offer segment. | Hybrids consisting solely of currently-exempt resource types are also exempt
7a | Energy Market must offer for Capacity Resources |  | Intermittent Resources and Energy Storage Resources may off quantities that vary from their cleared UCAP quantity | Solar-battery Hybrid Resources may offer quantities that vary from their cleared UCAP quantity
8 | Billing and settlements for charging energy of open-loop hybrids |  | Status quo for Energy Storage Resource Model Participants is that charging energy takes transmission service under certain circumstances (consistent with Order 841), and therefore pays additional non-LMP charges sometimes. See Manual 27 Section 8 and Manual 28 Section 22.
9 | Number of resources for MOPR purposes |  | Hybrid Resources are considered one resource and would be modeled as one resource for MOPR. See OATT Attachment DD 5.14.
9a | Resource Classification Process |  | ELCC proposal limits changes in class to once per five years. | For mixed-technology Capacity Resources: Energy Market modeling must match Capacity Market modeling for the same Delivery Year (it follows that resources that can choose co-located vs. hybrid modeling must retain the choice for 5 years). Capacity Resources switch modeling for a given Delivery Year via ELCC data submission process prior to BRA or first auction a Planned Resource participates in. Energy-only mixed-technology resources that have a choice of hybrid vs. co-located modeling can change classifications once per year with notice to PJM by no later than May 30 for the upcoming January 1 to December 31 participation months. Once a status is chosen, it remains until an another request is received. For an Energy-only mixed-technology resource within the new resource queue process, the modeling choice must be made to no later than 6 months in advance of their initial start in the energy markets.
9b | Uplift eligibility |  | ESR Model Participant is eligible for Reactive Services uplift and discussion of mutually acceptable lost opportunity cost compensation; Solar is not eligible for those things. | Hybrid uplift eligibility same as ESR Model Participant.
9c | Market Settlement to Multiple Members |  | In certain circumstances, a single resource may be eligible to split market settlements among multiple Members | Hybrids that are otherwise eligible to split market settlements among multiple Members cannot split market settlements by component, only by share of the overall hybrid.
Operations Items
10 | Telemetry & Metering *Accuracy is at a system level |  | M-14D, Section 4.2.3 If an Energy Storage Resource is collocated with another Generating Facility such as a wind or solar unit, then the resources must choose to participate in markets as single, integrated resources or as two separate resources. When separate, separate telemetry and billing metering is required for each component. If a solar park is collocated with an energy storage facility such as a battery, then separate metering is required for each component in order to preserve solar forecast accuracy. Proposed ELCC construct: Combined Resources must provide the directly-measured MWh output of the Variable Resource component. For SREC measurement: Co-located resources use the monthly net of injections minus withdrawals from the solar component settlement data. Hybrid resources use the monthly net of injections minus withdrawals from the hybrid settlement data (i.e., the Point Of Interconnection meter readings). To the extent state or jurisdictional rules allow Certificates to be created for generation that is not delivered to the transmission grid, PJM EIS has procedures in place to do so, as described in the GATS Operating Rules. See Tab 2b, Option Details, for further explanation. | Include hybrids in existing requirement for ESR to telemeter state of charge. Telemetered values from submetering required for a generation component of a Hybrid Resource. This submetering measures just the generation component output (and is not affected by the storage component output/charging). This submetering is required for ELCC purposes and for maintaing the solar and wind forecasts--it is not used in MWh settlements or in determining zonal load. Telemetered submeter values for the generation component may be inferred as the difference between the POI telemetry and the battery component telemetry (corrected for losses to the POI). For submeter data for hybrids, real-time accuracy requirement is 5% and ex-post accuracy requirement is 1%. Measurements need to be corrected to the equivalent values at the Point of Interconnection while maintaining the accuracy requirement. Correction needs to account for any losses in power conversion from DC to AC, for transformer losses, and for conductor losses. Solar-battery hybrids must meet all meteorological telemetry requirements of solar resources. Hybrid Resources must have telemetry at the POI for MW and MVAR, and must have revenue metering at the POI for MWh, consistent with any other generation resource. There must be at least one measurement point for each Co-Located Resource at a Mixed Technology Facilty. A Mixed Technology Facility must have a measurement point at the Point of Interconnection; the sum of the measurement values for each interval for each Co-Located Resource at a Mixed Technology Facility must equal the gross value measured at the POI of the Mixed Technolgoy Facility for each such interval. Any measurement point at a Mixed Technology Facility that is not at the POI must be corrected for losses and impedance to the POI. Each such measurement point must have revenue-grade energy settlement metering and real-time MW and MVAR telemetry. The foregoing provisions apply to revenue grade energy settlement values, to real-time MW values, and to real-time MVAR values. | Telemetered values from submetering required for a generation component of any Hybrid Resource (not just solar-battery hybrids). This submetering measures just the generation component output (and is not affected by the storage component output/charging). This submetering is required for ELCC purposes and for maintaing the solar and wind forecasts--it is not used in MWh settlements or in determining zonal load. Telemetered submeter values for the generation component may be inferred as the difference between the POI telemetry and the battery component telemetry (corrected for losses to the POI). | For submeter data for hybrids, real-time accuracy requirement is 5% and ex-post accuracy requirement is 1%. Measurements need to be corrected to the equivalent values at the Point of Interconnection while maintaining the accuracy requirement. Correction needs to account for any losses in power conversion from DC to AC, for transformer losses, and for conductor losses. Hybrid Resources must have telemetry at the POI for MW and MVAR, and must have revenue metering at the POI for MWh, consistent with any other generation resource. There must be at least one measurement point for each Co-Located Resource at a Mixed Technology Facilty. A Mixed Technology Facility must have a measurement point at the Point of Interconnection; the sum of the measurement values for each interval for each Co-Located Resource at a Mixed Technology Facility must equal the gross value measured at the POI of the Mixed Technolgoy Facility for each such interval. Any measurement point at a Mixed Technology Facility that is not at the POI must be corrected for losses and impedance to the POI. Each such measurement point must have revenue-grade energy settlement metering and real-time MW and MVAR telemetry. The foregoing provisions apply to revenue grade energy settlement values, to real-time MW values, and to real-time MVAR values. | All metering is solely at the point of interconnection. | Only real-time sub-meter data is required. The real-time accuracy requirement is 5%. Measurements need to be corrected to the equivalent values at the Point of Interconnection while maintaining the accuracy requirement. Correction needs to account for any losses in power conversion from DC to AC, for transformer losses, and for conductor losses. | add to Status Quo: Hybrid resources use the monthly net of injections minus withdrawals from the hybrid settlement data (i.e., the Point Of Interconnection meter readings) is the default SREC measurement. However, to the extent state or jurisdictional rules differ in the measurement of SRECs, PJM will amend the default approach to account for such differences. | Low - High
11 | Measurement of Hybrid Components *Accuracy is at a system level |  | Direct solar output measurement hardware on the DC bus for DC-coupled hybrids. | Measurements of DC values need to be corrected to the equivalent values at the Point of Interconnection to the following accuracies: for use in ex-post applications--within 1% accuracy; for use in real-time applications--within 5% accuracy. Correction needs to account for losses in power conversion from DC to AC, transformers, and conductors. The corrected value plus any measurement error must stay within the stated accuracy bounds of 1% and 5%. | Measurements of DC values need to be corrected to the equivalent values at the Point of Interconnection to the following accuracies: for use in real-time applications--within 5% accuracy. Correction needs to account for losses in power conversion from DC to AC, transformers, and conductors. The corrected value plus any measurement error must stay within the stated accuracy bounds of 5%. |  |  |  |  | Medium
12 | Data Requirements for Forecasting |  | Solar (M-14D, Section 12.2): Static requirements (12.2.1) Real-time output (12.2.2) - 3MW or greater. "If a solar park is collocated with an energy storage facility such as a battery, then separate metering is required for each component in order to preserve solar forecast accuracy." Real-time meteorological data (12.2.3) | [6 empty] | Medium - High
13 | Operating requirements |  | An intermittent resource’s Economic Minimum shall not exceed the level of its CIR... An intermittent resource’s Emergency Minimum should be set to 0... Intermittent resource curtailment should be achieved within 15 minutes or consistent with the resources ramp rate bid. PJM should be notified if curtailment is expected to exceed 15 minutes. | A solar-battery hybrid's Economic Minimum shall not exceed the level of its CIR... A solar-battery hybrid's Emergency Minimum should be set to 0... The output of a solar-battery hybrid should achieve its dispatch point within 10 5 minutes or consistent with the resource's ramp rate bid. PJM should be notified if the response time is expected to exceed 10 5 minutes. The operator of a solar-battery hybrid that is dispatchable must indicate to PJM the hours for which the plant is operating in “solar-only” mode, during which time the battery is *not* providing power for the purpose of maintaining hybrid output consistent with PJM dispatch. Dispatchable solar-battery hybrids must follow dispatch in both "solar-only" mode and "hybrid mode". | The operator of a solar-battery hybrid that is dispatchable must indicate to PJM the hours for which the plant is operating in “solar-only” mode, during which time the battery is *not* providing power for the purpose of maintaining hybrid output consistent with PJM dispatch. Dispatchable solar-battery hybrids must follow dispatch in both "solar-only" mode and "hybrid mode".
14 | Outage Reporting |  | Solar: Due to the impact of planned/unplanned solar resource outages on solar power forecast accuracy, solar resources shall report any outage of one megawatt or more with duration of one hour or longer. ESR: For Energy Storage Resources: an eDART ticket is required when the ESR is unavailable or derated. Charging or lack of charge does not require an eDART ticket. | For solar-battery hybrid Generating Facilities, eDART and GADS outages shall be reported separately for the solar component and storage component whenever unavailable or derated. No eDART or GADS ticket is required for lack of solar irradiance, charging, nor lack of charge. | [5 empty] | High
15 | Reactive Capability: testing |  | Solar: variable MW output Inverter-based Storage: MAX MW (full lead and lag) ZERO MW output (max lead and lag) MIN MW output (i.e., max charging) (max lead and lag) | Test points/circumstances: DC-COUPLED SOLAR-BATTERY HYBRIDS Max MW Output = fully discharging Min MW Output = fully charging AC-COUPLED SOLAR-BATTERY HYBRIDS Max MW Output = fully discharging Min MW Output = fully charging Max inverter operating point = solar at full output and battery at full charging *Additional test points may be required if these do not capture the most restrictive capability scenarios.
16 | Reactive Capability: D-curves |  | All resources: The “Unit Minimum and Maximum Net MVAR Limits” must indicate the realistic, usable capability that is sustainable during continuous long-term unit operation. ESR: For inverter-based Energy Storage Resources, the reactive capability should be based on Inverter MVA Capability Curve. | DC-coupled: matches ESR. AC-coupled: (see proposal on slide 9 here: https://www.pjm.com/-/media/committees-groups/subcommittees/dirs/2020/20201207/20201207-item-11-reactive-capability-of-hybrid-resources.ashx )
Cost Development Subcommittee items--new Issue Charge required for changes to status quo
17 | Cost Offers |  | Cost Offers of $0 are acceptable, other cost offer methods must follow rules in Manual 15
Instructions:
*Implementation should consider timing for both PJM and stakeholders (added as standard component based on Stakeholder feedback- 2015)
1Design Components - each is an "attribute" or "component" of any proposed solution. Consensus of the group should be sought on selection of a set of solution criteria.
2Solution Options - each is a solution alternative elicited from the stakeholder group that meet one of the specific solution criteria.
To complete the matrix:
1. Elicit from the stakeholder group a set of components (attributes) desired for any proposed solution. Enter a short label for each in the Design Components column.
2. If needed, enter a more detailed description of each criteria on the "Design Component Details" tab (2a).
3. Using informal feedback from the participants, rate each component's priority in the final solution as "high/medium/low"
4. Elicit from the stakeholder group potential solution alternative(s) for each component. Enter a short label for each in the Solution Options columns.
5. If needed, enter a more detailed description of each potential solution option on the "Option Details" tab 2b.
6. Once the matrix is filled out, the group will attempt to select a single solution alternative (column) for each component (row) to form a solution "package", to be documented in tab 3, "Packages Matrix".
Example: cells 1B, 2C, 3A, 4B, 5D could make up a solution package.

## 2a. Design Component Details
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
COMPONENT DETAILS
Instructions: Complete this form as needed. Design components should be populated from the Options Matrix.
Design Component | Detailed Description
1 | <enter detailed description of this component>
2 | <enter detailed description of this component>
3 | <enter detailed description of this component>
4 | <enter detailed description of this component>
5 | <enter detailed description of this component>

## 2b. Option Details
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
SOLUTION OPTION DETAILS
Updated: May 14, 2021
Instructions: Complete this form as needed, including more detailed / expansive descriptions of options than the Options Matrix allows.
Cell # | Detailed Description
Design component #10, Status Quo | Pertaining to the "SREC Measurement" status quo: A Certificate is created in the Generation Attribute Tracking System (GATS) for each MWh of PJM Generation as reported to the PJM Market Settlement System. The original data source for reporting must be from a revenue-quality meter measuring the Energy delivered into the transmission grid at the Point of Interconnection. To the extent state or jurisdictional rules allow Certificates to be created for generation that is not delivered to the transmission grid (e.g., for Wholesale Generation Also Serving On-Site Loads), PJM EIS has procedures in place to do so, as described in the GATS Operating Rules. https://www.pjm-eis.com/-/media/pjm-eis/documents/gats-operating-rules.ashx?la=en.

## 3. Package Matrix
DER and Inverter-based Resources Subcommittee
Solar-Battery Hybrids Resources
PACKAGE/ PROPOSAL MATRIX
Updated: June 23, 2021
Packages
# | Design Components | Priority | Status Quo | A (PJM) | B (Same as Package A, except for DC #6) | C | D | E
| Markets Items |  |  |  | PACKAGE REMOVED BY SPONSOR
1 | Definitions, including classification of hybrids relative to existing resource types (e.g., Intermittent Resource, Energy Storage Resource, etc). |  | “Combination Resource” shall mean a Generation Capacity Resource that has a component that has the characteristics of a Limited Duration Resource combined with (i) a component that has the characteristics of an Unlimited Resource or (ii) a component that has the characteristics of a Variable Resource. *Proposed as part of the Effective Load Carrying Capability draft RAA language "Energy Storage Resource" shall mean a resource capable of receiving electric energy from the grid and storing it for later injection to the grid that participates in the PJM Energy, Capacity and/or Ancillary Services markets as a Market Participant." | Mixed Technology Facility Resource - a resource facility composed of more than one generation and/or energy storage resource component behind the same point of interconnection. Hybrid Resource - a resource composed of one generation component and one energy storage resource component behind the same point of interconnection operating in the capacity, energy, and/or ancillary services market(s) as a single unit. Co-located Resource - a resource composed of at least one generation and one energy storage resource behind the same point of interconnection operating in the capacity, energy, and/or ancillary services market(s) as more than one unit. a component of a Mixed Technology Facility that operates in the capacity, energy, and/or ancillary services market(s) as a separate resource from the other components of such facility. "Open-Loop Hybrid Resource: A Hybrid Resource that can charge from the grid. An Open-Loop Hybrid Resource consisting of a solar component and a storage component is an Energy Storage Resource". Add to definition of Energy Storage Resource: "An Open-Loop Hybrid Resource consisting of a solar component and a storage component is an Energy Storage Resource." Standalone Energy Storage Resource - "an Energy Storage Resource that is not a Hybrid Resource." | Same as Package A
2 | Generation/storage thresholds to be considered "hybrid resource" |  | N/A | No threshold--solar-battery mixed-technology resources may elect "hybrid" status with any ratio of generation to storage | Same as Package A
3 | Modeling Energy/Ancillary Services |  | Note: ESR may opt in or out of the ESR Participation Model once per year. | For closed-loop hybrids: new model similar to the ESR Participation Model, except it has "solar only mode", does not have the non-energy ancillary services modes, and does not have any charging/negative power functionality use existing conventional market model for offers/clearing/dispatch of energy and ancillary services For open-loop hybrids: include them as a type of Energy Storage Resource, which would give them the ability to opt-in to the Energy Storage Resource Participation Model, which includes the ability to schedule charging energy and inherit the accounting features of charging energy associated with Order 841. They would use a new model similar to the ESR Participation Model, except it has "solar only mode" and does not have the non-energy ancillary services modes. Mixed Technology Facilities whose components are physically incapable of operating independently are modeled and participate in Capacity and Energy markets as a single Hybrid Resource Conditions that make a mixed-technology resource physically incapable of operating independently include: the sum of the nameplate power rating of the components is greater than 115% of the Maximum Facility Output; closed-loop hybrids. | Same as Package A
4 | Market Operations of negative MW |  | Solar: N/A ESR: Only storage resources registered and using the ESR model can schedule negative MW. | See Design Component 3 | See Design Component 3
5 | Regulation |  | All resources can participate in Regulation if they meet performance requirements. For co-located resources: battery component can participate in Regulation if submeter telemetry is provided. | Status quo, except non-energy regulation only mode of ESR Participation Model is not available | Status quo
6 | Reserves |  | Solar: Not included in reserve calculations; Can opt-in to providing spinning reserves. ESR: can offer Tier II SR by default, excluded from Tier I SR by default. DASR: solar and storage excluded by default. Reserve Pricing Reform filing: six reserves are defined: day-ahead and real-time equivalents of 10-minute online, 30-minute online, and 10-minute offline reserves. ESR are by default eligible to offer all reserves they are physically capable of providing. ESR must offer reserves consistent with rules for all other resource types. | Solar-battery hybrids can offer Tier II SR by default, excluded from Tier I SR estimates and DASR by default. Can opt in to Tier I SR estimates and DASR with an opt-in process informing PJM of the desire to participate, whereupon PJM will estimate Tier 1 SR and assign DASR in the same manner as other resources scheduling energy (same as status quo for Order 841 ESR Model Participants). Solar-battery hybrids treated the same as Reserve Pricing Reform approach to ESR. | Solar battery hybrid in which the battery has at least four hours of storage are included in Tier I SR, Tier II SR, and DASR by default.
7 | Capacity Market must offer |  | Intermittent Resources, Capacity Storage Resources, Demand Resources, Energy Efficiency Resources are not required to submit a Capacity Performance sell offer segment. | Hybrids consisting solely of currently-exempt resource types are also exempt | Same as Package A
7a | Energy Market must offer for Capacity Resources |  | Intermittent Resources and Energy Storage Resources may off quantities that vary from their cleared UCAP quantity | Solar-battery Hybrid Resources may offer quantities that vary from their cleared UCAP quantity
8 | Billing and settlements for charging energy of open-loop hybrids |  | Status quo for Energy Storage Resource Model Participants is that charging energy takes transmission service under certain circumstances (consistent with Order 841), and therefore pays additional non-LMP charges sometimes. See Manual 27 Section 8 and Manual 28 Section 22. | Status quo | Status quo
9 | Number of resources for MOPR purposes |  | Number of resources for MOPR purposes matches intended offer for the capacity market | Status quo
9a | Resource Classification Process |  | ELCC proposal limits changes in class to once per five years. | For mixed-technology Capacity Resources: Energy Market modeling must match Capacity Market modeling for the same Delivery Year (it follows that resources that can choose co-located vs. hybrid modeling must retain the choice for 5 years). Capacity Resources switch modeling for a given Delivery Year via ELCC data submission process prior to BRA or first auction a Planned Resource participates in. Energy-only mixed-technology resources that have a choice of hybrid vs. co-located modeling can change classifications once per year with notice to PJM by no later than May 30 for the upcoming January 1 to December 31 participation months. Once a status is chosen, it remains until an another request is received. For an Energy-only mixed-technology resource within the new resource queue process, the modeling choice must be made to no later than 3 6 months in advance of their initial start in the energy markets. | Same as Package A
9b | Uplift eligibility |  | ESR Model Participant is eligible for Reactive Services uplift and discussion of mutually acceptable lost opportunity cost compensation; Solar is not eligible for those things. | Hybrid uplift eligibility same as ESR Model Participant.
9c | Market Settlement to Multiple Members |  | In certain circumstances, a single resource may be eligible to split market settlements among multiple Members | Hybrids that are otherwise eligible to split market settlements among multiple Members cannot split market settlements by component, only by share of the overall hybrid.
Operations items
10 | Telemetry & Metering *Accuracy is at a system level |  | M-14D, Section 4.2.3 If an Energy Storage Resource is collocated with another Generating Facility such as a wind or solar unit, then the resources must choose to participate in markets as single, integrated resources or as two separate resources. When separate, separate telemetry and billing metering is required for each component. If a solar park is collocated with an energy storage facility such as a battery, then separate metering is required for each component in order to preserve solar forecast accuracy. Proposed ELCC construct: Combined Resources must provide the directly-measured MWh output of the Variable Resource component. For SREC measurement: Co-located resources use the monthly net of injections minus withdrawals from the solar component settlement data. Hybrid resources use the monthly net of injections minus withdrawals from the hybrid settlement data (i.e., the Point Of Interconnection meter readings). To the extent state or jurisdictional rules allow Certificates to be created for generation that is not delivered to the transmission grid, PJM EIS has procedures in place to do so, as described in the GATS Operating Rules. See Tab 2b, Option Details, for further explanation. | Include hybrids in existing requirement for ESR to telemeter state of charge. Telemetered values from submetering required for a generation component of any Hybrid Resource (not just solar-battery Hybrid Resources). This submetering measures just the generation component output (and is not affected by the storage component output/charging). This submetering is required for ELCC purposes and for maintaing the solar and wind forecasts--it is not used in MWh settlements or in determining zonal load. Telemetered submeter values for the generation component may be inferred as the difference between the POI telemetry and the battery component telemetry (corrected for losses to the POI). For submeter data for hybrids, real-time accuracy requirement is 5% and ex-post accuracy requirement is 1%. Measurements need to be corrected to the equivalent values at the Point of Interconnection while maintaining the accuracy requirement. Correction needs to account for any losses in power conversion from DC to AC, for transformer losses, and for conductor losses. Solar-battery hybrids must meet all meteorological telemetry requirements of solar resources. Hybrid Resources must have telemetry at the POI for MW and MVAR, and must have revenue metering at the POI for MWh, consistent with any other generation resource. There must be at least one measurement point for each Co-Located Resource at a Mixed Technology Facilty. A Mixed Technology Facility must have a measurement point at the Point of Interconnection; the sum of the measurement values for each interval for each Co-Located Resource at a Mixed Technology Facility must equal the gross value measured at the POI of the Mixed Technolgoy Facility for each such interval. Any measurement point at a Mixed Technology Facility that is not at the POI must be corrected for losses and impedance to the POI. Each such measurement point must have revenue-grade energy settlement metering and real-time MW and MVAR telemetry. The foregoing provisions apply to revenue grade energy settlement values, to real-time MW values, and to real-time MVAR values. | Same as Package A
11 | Measurement of Hybrid Components *Accuracy is at a system level |  | Direct solar output measurement hardware on the DC bus for DC-coupled hybrids. | Measurements of DC values need to be corrected to the equivalent values at the Point of Interconnection to the following accuracies: for use in ex-post applications--within 1% accuracy; for use in real-time applications--within 5% accuracy. Correction needs to account for losses in power conversion from DC to AC, transformers, and conductors. The corrected value plus any measurement error must stay within the stated accuracy bounds of 1% and 5%. | Same as Package A
12 | Data Requirements for Forecasting |  | Solar (M-14D, Section 12.2): Static requirements (12.2.1) Real-time output (12.2.2) - 3MW or greater. "If a solar park is collocated with an energy storage facility such as a battery, then separate metering is required for each component in order to preserve solar forecast accuracy." Real-time meteorological data (12.2.3) | Status quo | Status quo
13 | Operating requirements |  | An intermittent resource’s Economic Minimum shall not exceed the level of its CIR... An intermittent resource’s Emergency Minimum should be set to 0... Intermittent resource curtailment should be achieved within 15 minutes or consistent with the resources ramp rate bid. PJM should be notified if curtailment is expected to exceed 15 minutes. | A solar-battery hybrid's Economic Minimum shall not exceed the level of its CIR... A solar-battery hybrid's Emergency Minimum should be set to 0... The output of a solar-battery hybrid should achieve its dispatch point within 10 5 minutes or consistent with the resource's ramp rate bid. PJM should be notified if the response time is expected to exceed 10 5 minutes. The operator of a solar-battery hybrid that is dispatchable must indicate to PJM the hours for which the plant is operating in “solar-only” mode, during which time the battery is *not* providing power for the purpose of maintaining hybrid output consistent with PJM dispatch. Dispatchable solar-battery hybrids must follow dispatch in both "solar-only" mode and "hybrid mode". | Same as Package A
14 | Outage Reporting |  | Solar: Due to the impact of planned/unplanned solar resource outages on solar power forecast accuracy, solar resources shall report any outage of one megawatt or more with duration of one hour or longer. ESR: For Energy Storage Resources: an eDART ticket is required when the ESR is unavailable or derated. Charging or lack of charge does not require an eDART ticket. | For solar-battery hybrid Generating Facilities, eDART and GADS outages shall be reported separately for the solar component and storage component whenever unavailable or derated. No eDART or GADS ticket is required for lack of solar irradiance, charging, nor lack of charge. | Same as Package A
15 | Reactive Capability: testing |  | Solar: variable MW output Inverter-based Storage: MAX MW (full lead and lag) ZERO MW output (max lead and lag) MIN MW output (i.e., max charging) (max lead and lag) | Test points/circumstances: DC-COUPLED SOLAR-BATTERY HYBRIDS Max MW Output = fully discharging Min MW Output = fully charging AC-COUPLED SOLAR-BATTERY HYBRIDS Max MW Output = fully discharging Min MW Output = fully charging Max inverter operating point = solar at full output and battery at full charging *Additional test points may be required if these do not capture the most restrictive capability scenarios. | Same as Package A |  |  |  | Low
16 | Reactive Capability: D-curves |  | All resources: The “Unit Minimum and Maximum Net MVAR Limits” must indicate the realistic, usable capability that is sustainable during continuous long-term unit operation. ESR: For inverter-based Energy Storage Resources, the reactive capability should be based on Inverter MVA Capability Curve. | DC-coupled: matches ESR. AC-coupled: (see proposal on slide 9 here: https://www.pjm.com/-/media/committees-groups/subcommittees/dirs/2020/20201207/20201207-item-11-reactive-capability-of-hybrid-resources.ashx ) | Same as Package A |  |  |  | Low - Medium
| Cost Development Subcommittee items--new Issue Charge required for changes to status quo | [7 empty] | Low - High
17 | Cost Offers |  | Cost Offers of $0 are acceptable, other cost offer methods must follow rules in Manual 15 | Status quo | Status quo
Medium
High
Instructions:
1. Copy over design component, priority, and status quo columns from options matrix
2. Complete individual packages in columns by selecting individual component options from the options matrix.

## 3a. Package Details
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
PACKAGE / PROPOSAL DETAILS
Instructions: Complete this form as needed, including more detailed / expansive descriptions of package components than the Package Matrix allows.
Package Solutions2
| A | B | C | D | E
1 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
2 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
3 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
4 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>
5 | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component> | <enter detailed description of this component>

## Parking Lot
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
PARKING LOT
Instructions: Use this space to document any items not specific to another topic area.
Description
how to make the wind forecast still achieve its function if you are considering a participation as an ESR only

## Revision History
DER and Inverter-based Resources
Solar-Battery Hybrid Resources
Revision History
Current Spreadsheet Version:
Instructions: Document all version changes to this matrix for easy identification of changes.
Version | Posting Date | Description of changes
1
2
3