## Sheet1
Appendix A: Detailed Comparison of Requirements
Low voltage ride-through capabilities
Subject | CAISO 2010 Filing | CASIO Rules After FERC Ruling | IESO | PJM
Requirement | · The Facility shall remain online for the voltage disturbance caused by any fault on the transmission grid, or within the Generating Facility between the Point of Interconnection and the high voltage terminals of the Asynchronous Generating Facility’s step up transformer, having a duration equal to the lesser of the normal three-phase fault clearing time (4-9 cycles) or one-hundred fifty (150) milliseconds, plus any subsequent post-fault voltage recovery to the final steady-state post-fault voltage. Clearing time shall be based on the maximum normal clearing time associated with any three-phase fault location that reduces the voltage at the Asynchronous Generating Facility’s Point of Interconnection to 0.2 per-unit of nominal voltage or less, independent of any fault current contribution from the synchronous Generating Facility. | · Wind generating plants are required to remain in-service during three-phase faults with normal clearing (which is a time period of approximately 4 – 9 cycles) and single line to ground faults with delayed clearing, and subsequent post-fault voltage recovery to prefault voltage unless clearing the fault effectively disconnects the generator from the system. The clearing time requirement for a three-phase fault will be specific to the wind generating plant substation location, as determined by and documented by the Participating TO. The maximum clearing time the wind generating plant shall be required to withstand for a three-phase fault shall be 9 cycles after which, if the fault remains following the location-specific normal clearing time for three-phase faults, the wind generating plant may disconnect from the CAISO Controlled Grid. A wind generating plant shall remain interconnected during such a fault on the CAISO Controlled Grid for a voltage level as low as zero volts, as measured at the high voltage side of the wind GSU. | · Ride through routine switching events and design criteria contingencies assuming standard fault detection, auxiliary relaying, communication, and rated breaker interrupting times unless disconnected by configuration. | All wind generation projects must satisfy the Low Voltage Ride-Through (LVRT) requirement specified in FERC Order 661A. The LVRT criteria tests the ability to the wind farm generator to maintain operation and interconnection with the system during events that cause extremely low voltage transients as measured at the high side of the transformer that steps up the Wind Farm’s voltage to the transmission system (high side of the wind farm GSU.) Peak load conditions are the most stressful for maintaining system voltage so this analysis will be conducted on a peak load power flow model
|  |  | · Typical interrupting times range from 90ms to 141ms for a three phase fault and 150ms to 250ms for a single line to ground fault with delayed breaker clearing. | Wind generation facilities are required to remain in-service during three-phase faults with normal clearing (which is a time period of approximately 4 – 9 cycles) and single line to ground faults with delayed clearing, and subsequent post-fault voltage recovery to prefault voltage unless clearing the fault effectively disconnects the generator from the system. The clearing time requirement for a three-phase fault will be specific to the wind generation facility substation location, as determined by and documented by the transmission provider. The maximum clearing time the wind generation facility shall be required to withstand for a three-phase fault shall be 9 cycles after which, if the fault remains following the location-specific normal clearing time for three-phase faults, the wind generation facility may disconnect from the transmission system. A wind generation facility shall remain interconnected during such a fault on the transmission system for a voltage level as low as zero volts, as measured at the high voltage side of the wind GSU. This requirement does not apply to faults that would occur between the wind generator terminals and the high side of the GSU. Wind generation facilities may be tripped after the fault period if this action is intended as part of a special protection system.
| · Facility shall remain online for any voltage disturbance caused by a single-phase fault on the transmission grid, or within the Asynchronous Generating Facility between the Point of Interconnection and the high voltage terminals of the Generating Facility’s step up transformer, with delayed clearing, plus any subsequent post-fault voltage recovery to the final steady-state post-fault voltage. Clearing time shall be based on the maximum backup clearing time associated with a single point of failure (protection or breaker failure) for any single-phase fault location that reduces any phase-to-ground or phase-to-phase voltage at the Asynchronous Generating Facility’s Point of Interconnection to 0.2 per-unit of nominal voltage or less, independent of any fault current contribution from the Asynchronous Generating Facility. |  | · LVRT capability is demonstrated by comparing simulations of the voltage trajectory for design criteria contingencies against type tests submitted by the proponent during the market entry phase. If type tests are not available then testing must be conducted during the commissioning phase to prove the generator LVRT capabilities meet the market rule criteria and the unit(s) do not trip on out of zone faults.
Definition of Remaining Online | · Remaining on-line shall be defined as continuous connection between the Point of Interconnection and the Asynchronous Generating Facility’s units, without any mechanical isolation. Asynchronous Generating Facilities may cease to inject current into the transmission grid during a fault. | · No definition stated | · No statement explicitly stating definition | Not defined beyond FERC Order requirements
Methods to Achieve LVRT | · Wind generating plants may meet the LVRT requirements of this standard by the performance of the generators or by installing additional equipment (e.g., Static VAr Compensator, etc.) within the wind generating plant or by a combination of generator performance and additional equipment. | · Wind generating plants may meet the LVRT requirements of this standard by the performance of the generators or by installing additional equipment (e.g., Static VAr Compensator, etc.) within the wind generating plant or by a combination of generator performance and additional equipment. | · Generating Facilities may meet the requirements of this section through the performance of the generating units or by installing additional equipment within the generating facility, or by a combination of generating unit performance and additional equipment. | Wind generation facilities may meet the LVRT requirements of this standard by the performance of the generators or by installing additional equipment (e.g., Static VAr Compensator) within the wind generation facility or by a combination of generator performance and additional equipment.
Pre Contingency Conditions | · The provisions of this section apply only if the voltage at the Point of Interconnection has remained within the range of 0.9 and 1.10 per-unit of nominal voltage for the preceding two seconds, excluding any sub-cycle transient deviations. | · No such requirement | · A generating facility must be able to operate over the entire range of pre-contingency voltages specified in the Market Rules and the Ontario Resource and Transmission Assessment Criteria, and must be able to follow voltage dispatch instruction from the IESO. | No requirement
Voltage Regulation
Subject | CAISO 2010 Filing | CASIO Rules After FERC Ruling | IESO | PJM
Mode of Control | · Reactive power capability shall be controlled by an automatic system having both voltage regulation and a net power factor regulation operating modes. | · The Interconnection Customer to maintain a voltage schedule by operating the Electric Generating Unit to produce or absorb reactive power within the design limitations of the Electric Generating Unit. | · Regulate voltage automatically as specified by the IESO. | PJM manuals require that facilities follow voltage and freqency schedules.
| · The default mode of operation will be voltage regulation. |  | · Operation in any other mode of regulation (e.g. power factor or reactive power control) shall be subject to IESO approval.
Point of Voltage Control | · Point of Interconnection | · Does not specify | · Any point whose impedance (based on rated apparent power and rated voltage) is not more than 13% from the highest voltage terminal.
| or | · Relevant NERC requirement |  | Point of Interconnection
| · The CAISO, in coordination with the Participating TO, may permit the Interconnection Customer to regulate the voltage at a point on the Asynchronous Generating Facility’s side of the Point of Interconnection. | o Each Transmission Operator shall specify a voltage or Reactive Power schedule at the interconnection between the generator facility and the Transmission Owner's facilities to be maintained by each generator.
Tolerance | For Voltage Control Mode | · Does not specify | · ±0.5% of any set point within ±5% of rated voltage at a point whose impedance (based on rated apparent power and rated voltage) is not more than 13% from the highest voltage terminal.
| · ± 0.02 per unit of the nominal voltage schedule (set point) assigned by the Participating TO or CAISO, within the constraints of the reactive power capacity of the Asynchronous Generation Facility. | · Relevant NERC requirement which does not make a specific tolerance, rather states it will be on a case by case basis.
| · Deviations outside of this voltage band, except as caused by insufficient reactive capacity to maintain the voltage schedule tolerances, shall not exceed five (5) minutes duration per incident. | o Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule (within applicable Facility Ratings) as directed by the Transmission Operator. |  | The POI voltage tolerance must be maintained within the maximum and minimum voltage limits as described in PJM Manual M03.
| For Power Factor Mode | o The voltage schedule is a target voltage to be maintained within a tolerance band during a specified period.
· The power factor mode will regulate the net power factor measured at the Point of Interconnection. If the Asynchronous Generating Facility uses discrete reactive banks to provide reactive capability, the tolerances of the power factor regulation shall be consistent with the reactive banks’ sizes meeting the voltage regulation tolerances specified in the preceding paragraph.
Voltage Limits | · Voltage at the Point of Interconnection shall not exceed 1.05 per unit, or fall below 0.95 per unit. | · Does not specify, only specifies design limitations of generating unit. | · The voltage at the point of interconnection shall not exceed the voltage ranges specified in the Market Rules and the Ontario Resource and Transmission Assessment Criteria, and any other more restrictive voltage limits that apply for reliability reasons to part of the grid. | The POI voltage must be maintained within the maximum and minimum voltage limits as described in PJM Manual M03.
Unavailability of Voltage Control | · The Interconnection Customer shall not disable voltage regulation controls, without the specific permission of CAISO, while the Asynchronous Generating Facility is in operation at a power level greater than twenty (20) percent of the Asynchronous Generating Facility’s maximum Generating Facility Capacity. | · If the Large Generating Facility’s speed governors and voltage regulators are improperly tuned or malfunctioning, the CAISO shall have the right to order the reduction in output or disconnection of the Large Generating Facility if the reliability of the CAISO Controlled Grid would be adversely affected. | · Automatic voltage regulators shall be in service and in automatic mode unless the registered facility that is a generation facility is specifically directed by the IESO to operate the AVRs in manual mode.
Outage must be submitted to PJM to determine if continued operation can be allowed
Power factor design and reactive power capabilities
Subject | CAISO 2010 Filing | CASIO Rules After FERC Ruling | IESO | PJM
Reactive Power Requirements | · An Asynchronous Generating Facility shall be designed to have sufficient reactive power sourcing capability to achieve a net power factor of 0.95 lagging or less at the Point of Interconnection, at the Generating Facility’s maximum Generating Facility Capacity. | · A wind generating plant shall operate within a power factor within the range of 0.95 leading to 0.95 lagging, measured at the Point of Interconnection in order to maintain a specified voltage schedule, if the Interconnection System Impact Study shows that such a requirement is necessary to ensure safety or reliability. | · Inject or withdraw reactive power continuously (i.e. dynamically) at a connection point up to 33% of its rated active power at all levels of active power output except where a lesser continually available capability is permitted by the IESO. | For all new wind-powered and other non-synchronous generation facilities, if determined in the system impact study to be required for the safety or reliability of the Transmission System, the Generation Interconnection Customer shall design its Customer Facility with the ability to maintain a composite power delivery at continuous rated power output at a power factor of at least 0.95 leading to 0.95 lagging. For all wind-powered and other non-synchronous generation facilities, the power factor requirement shall be measured at the Point of Interconnection. Any different reactive power design criteria that Transmission Provider determines to be appropriate for a wind powered or other non-synchronous generation facility shall be stated in the Interconnection Service Agreement.
| · An Asynchronous Generating Facility shall be designed to have net reactive power sourcing and absorption capability sufficient to achieve or exceed the net reactive power range in Figure 1 of Appendix H as a function of the Point of Interconnection voltage, without exceeding the ratings of any equipment in the generating facility. |  | · The major difference is the IESO requires 33% reactive power at all active power levels while the CAISO proposal only requires 33% reactive power relative to actual power output. | Wind-powered generation facilities and other non-synchronous generation facilities, if determined in the System Impact Study to be required for the safety or reliability of the Transmission System, shall be designed with the ability to maintain a composite power delivery at continuous rated power output at a power factor for all incremental MW of capacity or energy output, of at least 1.0 (unity) to 0.95 lagging. All increases to wind powered and non-synchronous generation facilities interconnected to the Transmission System shall be measured at the Point of Interconnection.
Using Shunt Devices to Achieve Reactive Power Requirements | · Allows the use of switchable shunt devices to achieve target | · Allows the use of switchable shunt devices to achieve target | · Allows the use of switchable shunt devices to achieve target | Reactive Power Requirements can be met by using, for example, power electronic devices designed to supply this level of reactive capability (taking into account any limitations due to voltage level, real power output, etc.) or fixed and switched capacitors if agreed to by the Transmission Provider, or a combination of the two. The Interconnection Customer shall not disable power factor equipment while the wind generation facility is in operation.
| And/Or | And/Or | And/Or
| · Allows the use of dynamic devices (Eg. SVC) to achieve the target | · Allows the use of dynamic devices (Eg. SVC) to achieve the target | · Allows the use of dynamic devices (Eg. SVC) to achieve the target
Dynamic Requirements | · Asynchronous Generating Facilities shall also provide dynamic voltage support if the Interconnection Study requires dynamic voltage support for system safety or reliability. | · Wind plants shall also be able to provide sufficient dynamic voltage support in lieu of the power system stabilizer and automatic voltage regulation at the generator excitation system if the Interconnection System Impact Study shows this to be required for system safety or reliability. | · At any output, achieve 0.9 lagging and 0.95 leading based on the real power rating at the generating unit terminal; | Wind generation facilities shall also be able to provide sufficient dynamic voltage support in lieu of the power system stabilizer and automatic voltage regulation at the generator excitation system if the System Impact Study shows this to be required for system safety or reliability.
Maximum allowable voltage change when varying reactive power output | · Asynchronous Generating Facilities shall vary the reactive power output between the full sourcing and full absorption capabilities such that any step change in the reactive power output does not cause a step change in voltage at the Point of Interconnection greater than 0.02 per unit of the nominal voltage. | · No such limitation. | · No such limitation for maximum voltage change when changing the reactive power output only when this involves shunt elements, there is a limit of 4% voltage change on the connected bus. | No requirement
· The maximum voltage change requirement shall apply when the CAISO Controlled Grid is fully intact (no line or transformer outages), or during outage conditions which do not decrease the three-phase short circuit capacity at the Point of Interconnection to less than ninety (90) percent of the three-phase short-circuit capacity that would be present without the transmission network outage.
Operating at greater than twenty percent of active power | · Net reactive power range at least as great as specified in Figure 1 of Appendix H at the Point of Interconnection, based on the actual real power output level delivered to the Point of Interconnection. | · Does not apply, one rule for all active power levels | · Does not apply, one rule for all active power levels.
|  | · A wind generating plant shall operate within a power factor within the range of 0.95 leading to 0.95 lagging, measured at the Point of Interconnection in order to maintain a specified voltage schedule, if the Interconnection System Impact Study shows that such a requirement is necessary to ensure safety or reliability. | · Inject or withdraw reactive power continuously (i.e. dynamically) at a connection point up to 33% of its rated active power at all levels of active power output except where a lesser continually available capability is permitted by the IESO. | Wind farms are given either a voltage schedule or a power factor schedule which they are expected to follow based on their capabilities.
Operating at less than twenty percent of active power | · Net reactive power shall remain within the range between –6.6% and +6.6% of the Asynchronous Generating Facility’s real power rating. | · Does not apply, one rule for all active power levels. | · Does not apply, one rule for all active power levels.
|  | · A wind generating plant shall operate within a power factor within the range of 0.95 leading to 0.95 lagging, measured at the Point of Interconnection in order to maintain a specified voltage schedule, if the Interconnection System Impact Study shows that such a requirement is necessary to ensure safety or reliability. | · Inject or withdraw reactive power continuously (i.e. dynamically) at a connection point up to 33% of its rated active power at all levels of active power output except where a lesser continually available capability is permitted by the IESO. | Wind farms are given either a voltage schedule or a power factor schedule which they are expected to follow based on their capabilities.
Curtailment of active power if reactive power is not available | · Power output may be curtailed at the direction of CAISO to a value where the net power factor range is met, if the reactive power capability of an Asynchronous Generating Facility is partially or totally unavailable, and if continued operation causes deviation of the voltage at the Point of Interconnection outside +/- 0.02 per unit of scheduled voltage level. | · If the Large Generating Facility’s speed governors and voltage regulators are improperly tuned or malfunctioning, the CAISO shall have the right to order the reduction in output or disconnection of the Large Generating Facility if the reliability of the CAISO Controlled Grid would be adversely affected. | · The IESO may direct a registered facility that is a generation facility providing reactive support service and voltage control service to operate in an under- or over-excited state for a certain period of time in order to maintain prescribed voltages on the IESO-controlled grid. Such direction may require such registered facility to operate in the condense mode or to reduce real power output in order to increase its ability to provide reactive power. | Facilities required to meet voltage and frequency schedules. If unable to meet these then the facility may be curtailed
Maintaining Voltage Limits | · If the Point of Interconnection voltage exceeds 1.05 per unit, the Asynchronous Generating Facility shall provide reactive power absorption to the extent possible without violating the ratings of any of the Asynchronous Generating Facility’s equipment. | · No such requirement | · The IESO may direct a registered facility that is a generation facility providing reactive support service and voltage control service to operate in an under- or over-excited state for a certain period of time in order to maintain prescribed voltages on the IESO-controlled grid. Such direction may require such registered facility to operate in the condense mode or to reduce real power output in order to increase its ability to provide reactive power. | The POI voltage must be maintained within the maximum and minimum voltage limits as described in PJM Manual M03.
· If the Point of Interconnection voltage is less than 0.95 per unit, the Asynchronous Generating Facility shall provide reactive power injection to the extent possible without violating the ratings of any of the Asynchronous Generating Facility’s equipment.
Generator power management
Subject | CAISO 2010 Filing | CASIO Rules After FERC Ruling | IESO | PJM
Active Power Limit | · As of January 1, 2012, Asynchronous Generating Facilities must have the capability to limit active power output in response to a CAISO Dispatch Instruction or Operating Order. This capability shall extend from the Minimum Operating Limit to the Maximum Operating Limit of the Asynchronous Generating Facility in increments of five (5) MW or less. Changes to the power management set point shall not cause a change in voltage at the Point of interconnection exceeding 0.02 per unit of the nominal voltage. | · CAISO may dispatch down a generator for reliability or safety. | · If a controlled reduction of generation is required for reliability reasons, the generating facility’s output change must be completed promptly. | PJM may request wind generator to reduce output if causing transmission constraint
|  | · No requirement in terms of step size or voltage change. | · If an immediate response is required, or if a requested controlled reduction cannot be completed by the specified time, the IESO will request that the generation units be immediately removed from service.
· As of 09/2013 Wind Farms are participating in centralized forecasting and cannot bid lower than the floor prices. If the MCP reaches the floor price the wind farm can be dispatched off.
Limitation of Upward Active Power Ramp Rates | · Asynchronous Generating Facilities must have the installed capability to limit power change ramp rates automatically, except for downward ramps resulting from decrease of the available energy resource for Eligible Intermittent Resources. The power ramp control shall be capable of limiting rates of power change to a value of five (5) percent, (10) percent, or twenty (20) percent of the Asynchronous Generating Facility’s maximum Generating Facility Capacity per minute. The Asynchronous Generating Facility may implement this ramping limit by using stepped increments if the individual step size is five (5) MW or less. | · No such Requirement | · No such requirement | No requirement
Automatic Reduction of Plant Output due to High Frequency | · Asynchronous Generating Facilities must have the installed capability to automatically reduce plant power output in response to an over-frequency condition. This frequency response control shall, when enabled at the direction of CAISO, continuously monitor the system frequency and automatically reduce the real power output of the Asynchronous Generating Facility with a droop equal to a one-hundred (100) percent decrease in plant output for a five (5) percent rise in frequency (five (5) percent droop) above an intentional dead band of 0.036 Hz. | · No such requirement | · Regulate speed with an average droop based on maximum active power adjustable between 3% and 7% and set at 4% unless otherwise specified by the IESO. Regulation dead band shall not be wider than ± 0.06%.
|  |  | Speed shall be controlled in a stable fashion in both interconnected and island operation. A sustained 10% change of rated active power after 10 s in response to a constant rate of change of speed of 0.1%/s during interconnected operation shall be achievable. | Generators are expected to be able to remain on-line for a lmited duration at 62Hz.