## Sheet1
Region | Upgrade ID | Description | Transmisison Owner | Required In Service Date | Revised Required In Service Date | Status | TEAC Cost | TEAC Date | Latest TEAC Date | Database Notes | Board Date | Initial Issue Assessment | Final Assessment
PJM MA | b3130.11 | Replace four Atlantic 34.5 kV breakers (BK1A, BK1B, BK3A and BK3B) with 63kA rated breakers and associated equipment | JCPL | 2023-09-30 |  | PL | 3.5 | 2022-05-16 |  |  |  | Scope/Cost Change | Scope/Cost Change
PJM MA | b3130.12 | Replace Six Werner 34.5 kV breakers (E31A_Prelim, E31B_Prelim, V48 future, W101, M39 and U99) with 40 kA rated breakers and associated equipment.. | JCPL | 2024-06-01 |  | PL | 4.2 | 2022-05-16 |  |  |  | Scope/Cost Change | Scope/Cost Change
PJM WEST | b3350.1 | Replace overdutied 69kV breakers C, G, I, Z, AB and JJ in place. The new 69kV breakers to be rated at 3000 A 40kA breakers. | AEP | 2023-06-01 |  | PL | 2 | 2022-01-21 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM WEST | b3350.2 | Upgrade remote end relaying at Point Pleasant, Coalton and South Point 69KV substations | AEP | 2023-06-01 |  | PL | 0 | 2022-01-21 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM WEST | b3354 | Replace circuit breakers '42' and '43' at Bexley station with 3000A, 40 kA 69 kV breakers (operated at 40 kV), slab, control cables, jumpers, | AEP | 2023-06-01 |  | PL | 1 | 2022-01-21 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM WEST | b3355 | Replace circuit breakers 'A' and 'B' at South Side Lima station with 1200A, 25 kA 34.5 kV breakers , slab, control cables, jumpers, | AEP | 2023-06-01 |  | PL | 0.75 | 2022-01-21 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM WEST | b3356 | Replace circuit breaker 'H' at West End Fostoria station with 3000A, 40 kA 69 kV breaker , slab, control cables, jumpers, | AEP | 2023-06-01 |  | PL | 0.5 | 2022-01-21 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM WEST | b3357 | Replace circuit breakers 'C', 'E', and 'L' at Natrium station with 3000A, 40 kA 69 kV breakers, slab, control cables, jumpers, | AEP | 2023-06-01 |  | PL | 1.5 | 2022-01-21 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM MA | b3688 | Replace the 4/0 SDCU stranded bus with 954 ACSR and a 600 A disconnect switch with a 1200 A disconnect switch on the 6716 line terminal inside Todd substation (on the Preston – Todd 69 kV circuit). | DPL | 2026-06-01 |  | PL | 0.75 | 2021-12-20 |  |  |  | New Upgrade | New Upgrade
PJM MA | b3703 | Construct a third 69kV supply line from Penns Neck substation to the West Windsor substation. | PSEG | 2023-01-01 |  | PL | 1.05 | 2022-01-20 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM MA | b3704 | Replace Lawrence Switching Station 230-69kV transformer 220-4 and its associated circuit switchers with a new larger capacity transformer with Load Tap Changer (LTC) and new dead tank circuit breaker. Install a new 230kV gas insulated breaker, associated disconnects, overhead bus, and other necessary equipment to complete the bay within the Lawrence 230kV Switchyard | PSEG | 2026-06-01 |  | PL | 13.36 | 2022-02-08 |  | 2021_3-524 |  | New Upgrade | New Upgrade
PJM MA | b3705 | Replace existing 230/138kV Athenia 220-1 transformer. | PSEG | 2026-06-01 |  | PL | 13.04 | 2022-02-08 |  | 2021_3-770 |  | New Upgrade | New Upgrade
PJM MA | b3706 | Replace Fair Lawn 230-138kV transformer 220-1 with an existing O&M system spare at Burlington | PSEG | 2026-06-01 |  | PL | 4.454 | 2022-02-08 |  | 2021_3-510 |  | New Upgrade | New Upgrade
Not Specified | b3708 | Shawville - Install a new 230/115 kV transformer and associated facilities. Replace the Plant's 2B 115-17.2 kV transformer with a larger 230/17.2 kV transformer | PENELEC | 2026-06-01 |  | PL | 8.775 | 2022-03-08 |  | 2021_1-100 |  | New Upgrade | New Upgrade
PJM WEST | b3709 | Rebuild the Summer Shade-West Columbia 69 kV 0.19 miles of 266 conductor double circuit to 556 conductor. | EKPC | 2025-12-01 |  | PL | 0.191 | 2022-03-18 |  |  |  | New Upgrade | New Upgrade
PJM WEST | b3711 | Install 345 kV bus tie 5-20 circuit breaker in the ring at Dresden station in series with existing bus tie 5-6. | ComEd | 2026-12-01 |  | PL | 4.26 | 2022-04-12 |  | 2021_2-408 |  | New Upgrade | New Upgrade
PJM WEST | b3712 | Install a 28 MVAR cap bank at Liberty Junction 69 kV. | EKPC | 2022-12-01 |  | PL | 0.542 | 2022-04-22 |  | Immediate Need (TO Criteria Violation) |  | New Upgrade | New Upgrade
PJM MA | b3715.1 | At the existing PPL Williams Grove Substation, install a new 300 MVA 230/115 kV transformer | PPL | 2026-06-01 |  | PL | 6.297 | 2022-05-10 |  | 2021_1-99 |  | New Upgrade | New Upgrade
PJM MA | b3715.2 | Construct a new ~3.4 mile 115 kV single circuit transmission line from Williams Grove to Allen Substation | PPL | 2026-06-01 |  | PL | 5.113 | 2022-05-10 |  | 2021_1-99 |  | New Upgrade | New Upgrade
PJM MA | b3715.3 | Expand the Existing Allen 115 kV substation to four breaker ring bus | ME | 2026-06-01 |  | PL | 6.411 | 2022-05-10 |  | 2021_1-99 |  | New Upgrade | New Upgrade
PJM MA | b3674 | Replace Five Atlantic 34.5 kV breakers (J36, BK1A, BK1B, BK3A and BK3B) with 63kA rated breakers and associated equipment | JCPL | 2026-06-01 |  | PL | 3.5 | 2021-11-18 |  |  | 2022-02-16 | Cancelled in Database | Cancelled
PJM MA | b3675 | Replace Six Werner 34.5 kV breakers (E31A_Prelim, E31B_Prelim, V48 future, W101, M39 and U99) with 40 kA rated breakers and associated equipment.. | JCPL | 2026-06-01 |  | PL | 4.2 | 2021-11-18 |  |  | 2022-02-16 | Cancelled in Database | Cancelled
PJM MA | b3676 | Replace One Freneau 34.5 kV breaker (BK6) with 63 kA rated breakers and associated equipment | JCPL | 2026-06-01 |  | PL | 0.7 | 2021-11-18 |  |  | 2022-02-16 | Cancelled in Database | Cancelled