## Appendix
Region | UpgradeId | Description | Transmission Owner | Immediate Need | Project Submittal Number | Drivers | Required In-Service Date | Revised In-Service Date | Status | Initial TEAC Cost ($M) | Latest TEAC Cost ($M) | Board Approval Date | Issue Category
PJM SOUTH | b3800.210 | Build a new 230kV line from Mars - Prentice Drive on 500/230kV double circuit structures to achieve a summer rating of 1573 MVA. Install 230kV equipment at Mars and Prentice Drive. Remove 230 kV line No. 2095 Mars-Shellhorn and 230 kV line No. 2292 Mars-Sojourner in the existing transmission corridor between Sojourner and Mars substations so that they can be rerouted to the south side of Mars substation, adding approximately 2 miles of new conductor. This is to allow for termination of the line No.2413 and 5003 Golden-Mars 230 and 500 kV circuits into Mars substation. Cut 230 kV line No. 2095 Mars-Shellhorn into Sojourner substation, creating 230 kV line No. 2427 (Mars-Sojourner) and 230 kV line No. 2095 (Sojourner-Shellhorn). Upgrade 4 230 kV breakers at Sojourner substation from 63 kA to 80 kA. | Dominion |  | 2022-W3-692 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 57.95 | 150.8 | 12/11/2023 | Scope/Cost Change
PJM SOUTH | b3800.211 | Build a new 230kV line from Prentice Drive - Golden on 500/230kV double circuit structures to achieve a summer rating of 1573 MVA. Install 230kV equipment at Golden and Prentice. | Dominion |  | 2022-W3-692 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 56.93 | 52.78 | 12/11/2023 | Scope/Cost Change
PJM MA | b4076.9 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL10, 2024-P5DYN-DPL02 | DPL |  |  | Baseline Load Growth Deliverability & Reliability^Stability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.8 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL09 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.7 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL08 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.6 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL07 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.5 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL05 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.4 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL04 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.3 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL03 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.2 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5-DPL02 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.10 | 2024W1 P5: Install open circuit monitoring. Addresses FG # 2024-P5DYN-DPL01 | DPL |  |  | Baseline Load Growth Deliverability & Reliability^Stability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4076.1 | 2024W1 P5: Install open circuit monitoring . Addresses FG # 2024-P5-DPL01 | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.8 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC08 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.7 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC07 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.6 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC06 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.5 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC05 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.4 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC04 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.3 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC03 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.2 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC02 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4075.1 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-AEC01 | ACE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.015 | 0.015 |  | New Upgrade
PJM MA | b4074.9 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO09 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.8 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO08 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.05 | 0.05 |  | New Upgrade
PJM MA | b4074.7 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO07 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.6 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO06 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.5 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO05 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.4 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO04 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.3 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO03 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.2 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO02 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.19 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5DYN-PECO01 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.18 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO18 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.17 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO17 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.05 | 0.05 |  | New Upgrade
PJM MA | b4074.16 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO16 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.15 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO15 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.14 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO14 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.13 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO13 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.12 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO12 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.11 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO11 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.10 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO10 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM MA | b4074.1 | 2024W1 P5: Replace existing battery charger; install Auxiliary Alarm Relay Board; install Shunt enclosure; and connect alarm points to SCADA to monitor and report low voltage and open circuit conditions on the station DC supply to the Control Center.: Addressing FG # 2024-P5-PECO01 | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.025 | 0.025 |  | New Upgrade
PJM WEST | b4073.6 | 2024W1 P5: Install battery monitoring: Addressing FG # 2024-P5-COMED14 | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.1 | 0.1 |  | New Upgrade
PJM WEST | b4073.5 | 2024W1 P5: Install battery monitoring: Addressing FG # 2024-P5-COMED29 | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.1 | 0.1 |  | New Upgrade
PJM WEST | b4073.4 | 2024W1 P5: Install battery monitoring: Addressing FG # 2024-P5-COMED31 | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.1 | 0.1 |  | New Upgrade
PJM WEST | b4073.3 | 2024W1 P5: Install battery monitoring: Addressing FG # 2024-P5-COMED28 | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.05 | 0.05 |  | New Upgrade
PJM WEST | b4073.2 | 2024W1 P5: Install battery monitoring: Addressing FG # 2024-P5-COMED30 | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.1 | 0.1 |  | New Upgrade
PJM WEST | b4073.1 | 2024W1 P5: Install battery monitoring: Addressing FG # 2024-P5-COMED01 | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.25 | 0.25 |  | New Upgrade
PJM MA | b4072.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-ME02 | ME |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM MA | b4071.1 | 2024W1 P5: Separate DC supply to backup relaying and the second trip coils, modify relay wiring: Addressing FG # 2024-P5DYN-PN03 | PENELEC |  |  | Stability | 6/1/2029 |  | PL | 0.6624 | 0.6624 |  | New Upgrade
PJM MA | b4070.1 | 2024W1 P5: Modify relay wiring: Addressing FG # 2024-P5DYN-ME01 | ME |  |  | Stability | 6/1/2029 |  | PL | 0.3312 | 0.3312 |  | New Upgrade
PJM MA | b4067.1 | 2024W1 P5: Install battery monitoring, DC panel, and modify relay wiring: Addressing FG # 2024-P5DYN-JCPL01 | JCPL |  |  | Stability | 6/1/2029 |  | PL | 0.8073 | 0.8073 |  | New Upgrade
PJM MA | b4066.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-PN05 | PENELEC |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 2.5785 | 2.5785 |  | New Upgrade
PJM MA | b4065.2 | 2024W1 P5: Install 1 relay panel at a confidential substation connected to the substation associated with b4065.1. Addresses FG # 2024-P5-PN04. | PENELEC |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0 | 0 |  | New Upgrade
PJM MA | b4065.1 | 2024W1 P5: Install battery monitoring system & replace 2 115kV line protection schemes. Addresses FG # 2024-P5-PN04. | PENELEC |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 2.9007 | 2.9007 |  | New Upgrade
PJM WEST | b4064.1 | 2024W1 P5: Install battery monitoring, relay panels, and modify relay wiring: Addressing FG # 2024-P5-APS23 | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 1.9368 | 1.9368 |  | New Upgrade
PJM WEST | b4063.1 | 2024W1 P5: Install battery monitoring, DC panel(s), replace bus differential scheme, and modify relay wiring: Addressing FG # 2024-P5-APS22 | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 1.2893 | 1.2893 |  | New Upgrade
PJM WEST | b4062.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-APS08 | APS |  |  | Stability | 6/1/2029 |  | PL | 0.6417 | 0.6417 |  | New Upgrade
PJM WEST | b4061.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-APS05 | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM WEST | b4060.1 | 2024W1 P5: Install open battery monitoring, install relay panel, modify relay wiring: Addressing FG # 2024-P5-APS01 | APS |  |  | Stability | 6/1/2029 |  | PL | 1.1385 | 1.1385 |  | New Upgrade
PJM MA | b4059.1 | 2024W1 P5: Install open battery monitoring, install relay panel, modify relay wiring: Addressing FG # 2024-P5-ME05 | ME |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.6882 | 0.6882 |  | New Upgrade
PJM MA | b4058.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-ME04 | ME |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.5106 | 0.5106 |  | New Upgrade
PJM WEST | b4057.1 | 2024W1 P5: Install relay panel and modify relay wiring: Addressing FG # 2024-P5-APS06 | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.3552 | 0.3552 |  | New Upgrade
PJM MA | b4056.1 | 2024W1 P5: Move backup relaying DC supply to separate battery & modify relay wiring Addresses FG # 2024-P5DYN-PN02. | PENELEC |  |  | Stability | 6/1/2029 |  | PL | 0.481 | 0.481 |  | New Upgrade
PJM MA | b4055.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-PN04 | PENELEC |  |  | Stability | 6/1/2029 |  | PL | 0.40404 | 0.40404 |  | New Upgrade
PJM MA | b4054.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-ME03 | ME |  |  | Stability | 6/1/2029 |  | PL | 0.333 | 0.333 |  | New Upgrade
PJM WEST | b4051.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-ATSI09 | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.45386 | 0.45386 |  | New Upgrade
PJM WEST | b4050.1 | 2024W1 P5: Modify relay wiring: Addressing FG # 2024-P5-ATSI05 | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.66417 | 0.66417 |  | New Upgrade
PJM MA | b4049.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-JCPL02 | JCPL |  |  | Stability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM MA | b4048.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-ME02 | ME |  |  | Stability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM MA | b4047.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-JCPL03 | JCPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.6417 | 0.6417 |  | New Upgrade
PJM MA | b4046.1 | 2024W1 P5: Install battery monitoring, DC panel, and modify relay wiring: Addressing FG # 2024-P5DYN-JCPL04 | JCPL |  |  | Stability | 6/1/2029 |  | PL | 0.8073 | 0.8073 |  | New Upgrade
PJM MA | b4045.1 | 2024W1 P5: Install relay panel and modify relay wiring: Addressing FG # 2024-P5-JCPL01 | JCPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.6624 | 0.6624 |  | New Upgrade
PJM MA | b4044.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-ME04 | ME |  |  | Stability | 6/1/2029 |  | PL | 0.6417 | 0.6417 |  | New Upgrade
PJM MA | b4043.1 | 2024W1 P5: Modify relay wiring: Addressing FG # 2024-P5-JCPL06 | JCPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.6624 | 0.6624 |  | New Upgrade
PJM MA | b4042.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-JCPL03 | JCPL |  |  | Stability | 6/1/2029 |  | PL | 0.481 | 0.481 |  | New Upgrade
PJM WEST | b4041.1 | 2024W1 P5: Install battery monitoring, DC panel, line panel, and modify relay wiring: Addressing FG # 2024-P5-ATSI15 | ATSI |  |  | Stability | 6/1/2029 |  | PL | 1.2276 | 1.2276 |  | New Upgrade
PJM WEST | b4040.1 | 2024W1 P5: Install battery monitoring, DC panel, and modify relay wiring: Addressing FG # 2024-P5-APS03 | APS |  |  | Stability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM WEST | b4039.4 | 2024W1 P5: Replace 1 relay panel at a confidential substation connected to the substation associated with b4039.1. Addresses FG # 2024-P5-APS24. | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0 | 0 |  | New Upgrade
PJM WEST | b4039.3 | 2024W1 P5: Replace 1 relay panel at a confidential substation connected to the substation associated with b4039.1. Addresses FG # 2024-P5-APS24. | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0 | 0 |  | New Upgrade
PJM WEST | b4039.2 | 2024W1 P5: Replace 1 relay panel at a confidential substation connected to the substation associated with b4039.1. Addresses FG # 2024-P5-APS24. | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0 | 0 |  | New Upgrade
PJM WEST | b4039.1 | 2024W1 P5: Replace 3 relay panels & modify relay wiring. Addresses FG # 2024-P5-APS24. | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 4.2165 | 4.2165 |  | New Upgrade
PJM WEST | b4038.1 | 2024W1 P5: Modify relay wiring: Addressing FG # 2024-P5-APS02 | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.6624 | 0.6624 |  | New Upgrade
PJM WEST | b4037.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5-APS25 | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.60302 | 0.60302 |  | New Upgrade
PJM MA | b4010.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-PN05 | PENELEC |  |  | Stability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM MA | b4009.1 | 2024W1 P5: Modify relay wiring: Addressing FG # 2024-P5-PN03 | PENELEC |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.3312 | 0.3312 |  | New Upgrade
PJM MA | b4008.1 | 2024W1 P5: Install open battery monitoring & modify relay wiring: Addressing FG # 2024-P5DYN-PN01 | PENELEC |  |  | Stability | 6/1/2029 |  | PL | 0.9729 | 0.9729 |  | New Upgrade
PJM MA | b4007.7 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-BGE13 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.02 | 0.02 |  | New Upgrade
PJM MA | b4007.6 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-BGE04 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.08 | 0.08 |  | New Upgrade
PJM MA | b4007.5 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-BGE05 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.02 | 0.02 |  | New Upgrade
PJM MA | b4007.4 | 2024W1 P5: Install trip coil monitors: Addressing FG # 2024-P5-BGE14 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.1 | 0.1 |  | New Upgrade
PJM MA | b4007.3 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-BGE11 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.04 | 0.04 |  | New Upgrade
PJM MA | b4007.2 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-BGE07 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.06 | 0.06 |  | New Upgrade
PJM SOUTH | b3938.6 | 2024W1 DVP P5 Solution #45 - Replace & upgrade relay & associated equipment at DVP substation, addressing FG #2024-P5-DVP03 | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.2 | 0.2 |  | New Upgrade
PJM SOUTH | b3938.3 | 2024W1 DVP P5 Solution #42 - Replace & upgrade relay & associated equipment at DVP substation, addressing FG #2024-P5-DVP14 | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.18441 | 0.18441 |  | New Upgrade
PJM SOUTH | b3938.2 | 2024W1 DVP P5 Solution #41 - Replace & upgrade relay & associated equipment at DVP substation, addressing FG #2024-P5-DVP23 | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.10669 | 0.10669 |  | New Upgrade
PJM SOUTH | b3938.1 | 2024W1 DVP P5 Solution #40 - Replace & upgrade relay & associated equipment at DVP substation, addressing FG #2024-P5-DVP16 | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.18972 | 0.18972 |  | New Upgrade
PJM WEST | b4035.2 | Replace Smith Mountain 138 kV Switches CS1, CS2 and C1S2 with 3000 A switches and replace switch jumpers with 2-1272 AAC | AEP |  | 2025-ME1-733 | Congestion Relief - Economic | 1/1/2029 |  | PL | 0.37439 |  |  | New Upgrade
PJM WEST | b4035.1 | Reconductor one span of the Smith Mountain-Museville 138 kV line with 2-556 ACSR conductor | AEP |  | 2025-ME1-733 | Congestion Relief - Economic | 1/1/2029 |  | PL | 1.4317 |  |  | New Upgrade
PJM SOUTH | b4034.4 | This project at Lanexa Substation requires a relay reset only on Line 2016 relays. | Dominion |  | 2025-ME1-525 | Congestion Relief - Economic | 1/1/2029 |  | PL | 0.020108 |  |  | New Upgrade
PJM SOUTH | b4034.3 | This project at Harmony Village Substation requires a relay reset only on Line 2016 relays. | Dominion |  | 2025-ME1-525 | Congestion Relief - Economic | 1/1/2029 |  | PL | 0.020108 |  |  | New Upgrade
PJM SOUTH | b4034.2 | This project involves installing a new 230/115kV TX1 transformer using a 115kV breaker and associated switches, as well as a new 230kV line from Lanexa & Harmony Village with a 230kV Breaker and associated switches. | Dominion |  | 2025-ME1-525 | Congestion Relief - Economic | 1/1/2029 |  | PL | 17.3306 |  |  | New Upgrade
PJM SOUTH | b4034.1 | The existing line 2016 in the corridor will be cut into the Goalders Creek 3-breaker ring bus station such that the remaining section of line going to Harmony Village will be renumbered to 2XX1. | Dominion |  | 2025-ME1-525 | Congestion Relief - Economic | 1/1/2029 |  | PL | 4.484 |  |  | New Upgrade
PJM MA | b4007.1 | 2024W1 P5: Install open circuit battery monitoring: Addressing FG # 2024-P5-BGE03 | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.02 | 0.02 |  | New Upgrade
PJM MA | b4020.3 | Wreck and Rebuild OH circuit including transfer of any underbuilt circuits below the 69kV Install composite poles instead of wood poles. Install shield wire. Install fiber and all necessary fiber accessories. Install high-capacity conductor from Gloucester to Nicholson. Minimum Ratings: Summer Normal -1100 amps (131MVA). Replace UG cable with high capacity conductor and sweeps as required. | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 9.45 |  |  | New Upgrade
PJM MA | b4020.2 | Replace existing OH wire with high capacity conductor at Nicholson 230kV. Replace LP10K relays with new primary SEL-311L and backup SEL-411L relays | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.15 |  |  | New Upgrade
PJM MA | b4020.1 | Replace/update pole riser, pot head riser, associated sweeps and cable as required to accept high-capacity conductor at Gloucester 230kV . Replace LP41K relays with new primary SEL-311L and backup SEL-411L relays Replace duct banks as required. | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 1.2 |  |  | New Upgrade
PJM WEST | b3985.4 | Johnson Substation - Replace 451-B-163 breaker with a 63 kA, 3000 A circuit breaker. | ATSI |  |  | Short Circuit | 6/1/2030 |  | PL | 0.95669 |  |  | New Upgrade
PJM WEST | b3985.3 | Hoytdale Substation - Replace 83-B-14, 83-B-18, 83-B-22 breakers with 63 kA, 3000 A circuit breakers. This will not affect the Hoytdale - New Castle line ratings, which are currently rated at 435/500 SN/SE for circuit Z104 and 329/413 SN/SE for circuit Z110. | ATSI |  |  | Short Circuit | 6/1/2030 |  | PL | 2.8701 |  |  | New Upgrade
PJM WEST | b3985.2 | Eastlake Substation - Replace the following breakers with 80 kA, 3000 A circuit breakers. This will not affect the existing line ratings at the station. 46-B-18 46-B-21 46-B-24 46-B-35 46-B-36 46-B-32 46-B-33 46-B-27 46-B(795) 46-B-45 46-B-54 46-B-97 | ATSI |  |  | Short Circuit | 6/1/2030 |  | PL | 11.4803 |  |  | New Upgrade
PJM WEST | b3984.1 | Replace 69 kV Circuit Breakers - 501-B-24 - 501-B-272 - 501-B-274 | ATSI |  |  | Short Circuit | 6/1/2030 |  | PL | 1.53 |  |  | New Upgrade
PJM WEST | b3983.2 | Belmont Substation - Replace B-8 138 kV circuit breaker with a 63 kA, 3000 A breaker. This will not affect the line ratings of the Belmont - Trissler 138kV 604 line which is currently rated at 176/229 SN/SE or the Belmont - Edgelawn 138kV line which is currently rated at 292/314 SN/SE. | APS |  |  | Short Circuit | 6/1/2030 |  | PL | 0.95669 |  |  | New Upgrade
PJM WEST | b4025.3 | Install 138 kV BT CB and associated equipment at Sandwich | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 4/15/2030 |  | PL | 1.9461 |  |  | New Upgrade
PJM WEST | b4025.2 | Convert Mendota Straight Bus to Ring by installing 4 new 138 kV CBs | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 4/15/2030 |  | PL | 10.3651 |  |  | New Upgrade
PJM WEST | b4025.1 | Build new 28 mile transmission line from Mendota to Sandwich. | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 4/15/2030 |  | PL | 159.5677 |  |  | New Upgrade
PJM SOUTH | b4031.3 | At Fork Union substation, upgrade relevant equipment below 2000 A, such as line leads, breakers, switches and CTs to accommodate the upgraded line 5. | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/30/2030 |  | PL | 1 |  |  | New Upgrade
PJM SOUTH | b4031.2 | At Bremo substation, upgrade relevant equipment below 2000 A, such as line leads, breakers, switches and CTs to accommodate the upgraded line 5. | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/30/2030 |  | PL | 1 |  |  | New Upgrade
PJM SOUTH | b4031.1 | Wreck and rebuild line #5 using conductor with minimum summer rating of 393 MVA. | Dominion |  |  | Baseline Load Growth Deliverability & Reliability | 6/30/2030 |  | PL | 5 |  |  | New Upgrade
PJM SOUTH | b4030.9 | Charlottesville - Fork Union 230kV rebuild: Wreck and rebuild approximately 24 miles of Charlottesville - Fork Union 230kV line. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 106.4909 |  |  | New Upgrade
PJM SOUTH | b4030.8 | Yadkin 500kV substation scope: Replace all terminal equipment at Yadkin 500kV substation to be rated to 5000A. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.23692 |  |  | New Upgrade
PJM SOUTH | b4030.7 | Suffolk 500kV substation scope: Replace all terminal equipment at Suffolk 500kV substation to be rated to 5000A. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 5.2252 |  |  | New Upgrade
PJM SOUTH | b4030.6 | Suffolk - Yadkin 500kV rebuild: Rebuild approximately 13.2 miles of Suffolk - Yadkin 500kV Line. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 68.8614 |  |  | New Upgrade
PJM SOUTH | b4030.5 | Chesterfield 230kV substation scope: Install a new 230kV 80kA 4000A circuit breaker at Chesterfield 230kV substation. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.4968 |  |  | New Upgrade
PJM SOUTH | b4030.4 | Chesterfield 230kV substation scope: Replace all terminal equipment, line leads, and bus at Chesterfield 230kV substation to be rated to 4000A. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 3.5107 |  |  | New Upgrade
PJM SOUTH | b4030.3 | Basin 230kV substation scope: Replace all terminal equipment, line leads, and bus at Basin 230kV substation to be rated to 4000A. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.9634 |  |  | New Upgrade
PJM SOUTH | b4030.2 | Chesterfield - Hopewell 230kV reconductor: Reconductor 230kV lines #211 and #228 between the existing Chesterfield - Hopewell 230kV substation. Each line reconductor is approximately 3 miles long. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 6.3403 |  |  | New Upgrade
PJM SOUTH | b4030.16 | Sycamore Springs 230kV substation scope: Reset relays at Sycamore Springs 230kV substation. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.040216 |  |  | New Upgrade
PJM SOUTH | b4030.15 | Mt. Eagle Tap 230kV substation scope: Upgrade disconnect switches at Mt. Eagle Tap 230kV substation to 4000 A. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.64692 |  |  | New Upgrade
PJM SOUTH | b4030.14 | Bremo 230kV substation scope: Replace all terminal equipment at Bremo 230kV substation to support the new conductor ratings of the Fork Union - Bremo 230kV rebuild. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.7951 |  |  | New Upgrade
PJM MA | b3134 | Build a new single circuit 69 kV overhead from existing Kellam substation to new Cheriton substation (21 miles). | ODEC |  |  | TO Criteria Violation | 6/1/2019 | 12/31/2027 | EP | 22 | 43.4 | 12/3/2019 | Scope/Cost Change
PJM SOUTH | b4030.13 | Fork Union 230kV substation scope: Replace all terminal equipment at Fork Union 230kV substation to support the new conductor ratings of the Fork Union - Bremo 230kV rebuild. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.6023 |  |  | New Upgrade
PJM SOUTH | b4030.12 | Fork Union 230kV substation scope: Replace all terminal equipment at Fork Union 230kV substation to support the new line conductor ratings of the Charlottesville - Fork Union 230kV rebuild. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 2.2363 |  |  | New Upgrade
PJM SOUTH | b4030.11 | Charlottesville 230kV substation scope: Replace all terminal equipment at Charlottesville 230kV substation to support the new line conductor ratings of the Charlottesville - Fork Union 230kV rebuild. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 3.3513 |  |  | New Upgrade
PJM SOUTH | b4030.10 | Fork Union - Bremo 230kV rebuild: Wreck and Rebuild approximately 1.74 miles of Fork Union - Bremo 230kV line. | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 10.8053 |  |  | New Upgrade
PJM SOUTH | b4030.1 | Chesterfield - Basin 230kV rebuild: Wreck and rebuild approximately 12.5 miles of Chesterfield - Basin 230kV line | Dominion |  | 2025-W1-911 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 100.3055 |  |  | New Upgrade
PJM MA | b4029.9 | The Montour - Glen Brook 230 kV 1 & 2 DCT line is 24.9 miles long. For this project, the Developer will reconduct 0.70 miles of this route with ACCC 1036/87/392 (2045 kcmil) conductor. Another 5.2 miles of the route will be rebuilt with new steel pole structures and double-bundle 1590 ACSR conductor. The remaining 19 miles of the route is being rebuilt and reconductored as part of Supplemental Project s2373 to address End of Life for CORTEN structures. | PPL |  | 2025-W1-958 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 37.1541 |  |  | New Upgrade
PJM MA | b4029.8 | Address End of Life concerns by rebuilding the existing 38-mile Juniata - Sunbury 500 kV line using single circuit design. | PPL |  | 2025-W1-16 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 162.8871 |  |  | New Upgrade
PJM MA | b4029.7 | Re-termination of the Monroe - Fox Hill and Monroe - Martins Creek 230 kV lines into their new locations in the upgraded 230 kV breaker and a half yard. | PPL |  | 2025-W1-688 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 8.2663 |  |  | New Upgrade
PJM MA | b4029.6 | Upgrade the existing Monroe 230/138 kV Substation to a 2-bay breaker and a half on the 230 kV side (with space to accommodate 2 future bays), and a double-bus double-breaker design on the 138 kV side. | PPL |  | 2025-W1-688 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 30.9466 |  |  | New Upgrade
PJM MA | b4029.5 | Susquehanna - Tomhicken 230 kV 1 & 2 DCT line reconductor: Reconduct both circuits on the existing DCT tower with ACCC 1036/87/392 (2045 kcmil) conductor. | PPL |  | 2025-W1-824 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 29.7337 |  |  | New Upgrade
PJM MA | b4029.4 | Bifurcate the Sunbury - Susquehanna 500 kV line bringing both segments into a new Kelayres 500 kV Station on separate towers. From the bifurcation point, build a 24-mile long extension to Kelayres, resulting in a Sunbury - Kelayres 500 kV line. | PPL |  | 2025-W1-317 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 133.6358 |  |  | New Upgrade
PJM MA | b4029.3 | Bifurcate the Sunbury - Susquehanna 500 kV line. From the bifurcation point, build a 13-mile long extension to Kelayres, resulting in a Susquehanna - Kelayres 500 kV line. | PPL |  | 2025-W1-317 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 20.866 |  |  | New Upgrade
PJM MA | b4029.2 | Add one 500 kV 4,000 amp circuit breaker, two 500 kV 4,000 amp MODs, and a Kelayres 890 MVA 500/230 kV T3 transformer. | PPL |  | 2025-W1-853 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 29.0202 |  |  | New Upgrade
PJM MA | b4029.16 | Reuse existing bay and upgrade to 3,000 amps. Existing bay at Susquehanna vacated by the former Sunbury line. Inspect all facilities, refurbish, and insure bay rating of 3,000 amps. | PPL |  | 2025-W1-588 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 1.2355 |  |  | New Upgrade
PJM MA | b4029.15 | Construct a new breaker and a half bay at Susquehanna T10 230 kV Station and initially populate with two 230 kV 3,000 amp circuit breakers and four 230 kV 3,000 amp MODs, leaving a position for a future breaker to be added. | PPL |  | 2025-W1-588 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 6.6197 |  |  | New Upgrade
PJM MA | b4029.14 | Susquehanna T10 - Susquehanna 230 kV # 3 line: Construct a new Susquehanna T10 - Susquehanna 230 kV # 3 line (approximately 2.7 miles) using an approximately 75% brownfield route, with a short greenfield segment near the Susquehanna station. | PPL |  | 2025-W1-588 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 14.3327 |  |  | New Upgrade
PJM MA | b4029.13 | Glen Brook - Susquehanna T10 1 & 2 DCT line reconductor and Susquehanna T10 - Susquehanna # 3 line | PPL |  | 2025-W1-588 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 2.6281 |  |  | New Upgrade
PJM MA | b4029.12 | Re-terminate high side of T4 transformer into Bay 2E of the 230 kV yard. | PPL |  | 2025-W1-647 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 1.4565 |  |  | New Upgrade
PJM MA | b4029.11 | At the Jenkins 230/69 kV Substation, re-terminate the Jenkins 230/69 kV T2 and T4 transformers into bay positions in the 69 kV and 230 kV yards respectively. Add one new 230 kV 3,000 amp circuit breaker, and two 230 kV 3,000 amp MODs to accommodate the re-termination of the T4 transformer into the east bay position in the existing 230 kV breaker and a half Bay 2. Add two new 69 kV 3,000 amp circuit breakers, and 4 69 kV 3,000 amp switches to accommodate the re-termination of the T2 transformer into a new 69 kV double-bus double-breaker Bay 4. | PPL |  | 2025-W1-647 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 8.7132 |  |  | New Upgrade
PJM MA | b4029.10 | At Glen Brook 230/69 kV Substation, replace ten 230 kV 2,000 amp MODs with 230 kV 3,000 amp MODs. | PPL |  | 2025-W1-958 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 2.4968 |  |  | New Upgrade
PJM MA | b4029.1 | Expand existing Slykerville 230 kV Station to add a 500 kV yard. Build a new Kelayres 500 kV breaker and a half substation. Add two 890 MVA 500/230 kV transformers at Kelayres. | PPL |  | 2025-W1-317 | Baseline Load Growth Deliverability & Reliability | 5/1/2030 |  | PL | 72.9203 |  |  | New Upgrade
PJM MA | b4005.2 | Replace the existing 1590 ACSR single conductor on the Roseland to Laurel Ave 230kV line with a 1590 ACSS single conductor. | PSEG |  | 2025-W1-656 | Baseline Load Growth Deliverability & Reliability | 3/1/2028 |  | PL | 5.0583 |  |  | New Upgrade
PJM MA | b4005.1 | Replace the existing 1590 ACSR single conductor on the Roseland to Livingston 230kV line with a 1590 ACSS single conductor. | PSEG |  | 2025-W1-656 | Baseline Load Growth Deliverability & Reliability | 3/1/2028 |  | PL | 4.8734 |  |  | New Upgrade
PJM MA | b4004.1 | Upgrade existing 1590 ACSR stranded bus on facility. | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.030896 |  |  | New Upgrade
PJM MA | b3942.1 | Replace 2 CFD relays with 2 SEL-487B Bus relays. Install 2 new SEL-451 relays from breaker control of CB 785 and CB 875 respectively. Wiring modifications to existing 220-53 Line relays to all dual overlapping relays on CB 785 for bus protection and line protection. | PECO |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.69105 |  |  | New Upgrade
PJM WEST | b3954.1 | At Thomas Road, replace 69kV circuit switcher XT1 with a 40kA circuit switcher. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.71311 |  |  | New Upgrade
PJM WEST | b4003.5 | Update Relay Settings for the College Corner - Trenton line at DEOK's Trenton Substation. | DEOK |  | 2025-W1-156 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.029103 |  |  | New Upgrade
PJM WEST | b4003.4 | Update Relay Settings for the College Corner - Collinsville line at DEOK's Collinsville Substation. | DEOK |  | 2025-W1-156 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.029103 |  |  | New Upgrade
PJM WEST | b4003.3 | Relay Settings at College Corner station needed due to Duke rebuilding their College Corner - Collinsville 138kV line section. | AEP |  | 2025-W1-156 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.064132 |  |  | New Upgrade
PJM WEST | b4003.2 | Rebuild parts of the College Corner (AEP) - Trenton (DEOK) 138kV circuit that shares a common structure with the College Corner (AEP) - Collinsville (DEOK) circuit from the OH/IN State Line (Tower 10P-X1-129) to Collinsville Substation. AEP owns approximately 0.1 miles of the line from College Corner Substation to the OH/IN State Line. DEOK owns the remaining 24.19 miles from the state line to Trenton Substation. Only the 11.90-mile DEOK section that shares a common structure with College Corner (AEP) - Collinsville (DEOK) will be rebuilt with 954ACSS/TW conductor (@ 200C) and new double circuit structures. The remaining sections from Collinsville - Trenton will be left untouched. DEOK will be doing a route survey to see if easement updates and/or additional structures are required. | DEOK |  | 2025-W1-156 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 13.2359 |  |  | New Upgrade
PJM WEST | b4003.1 | Rebuild the College Corner (AEP) - Collinsville (DEOK) 138kV circuit from the OH/IN State Line (Tower 10P-X1-129) to Collinsville Substation. AEP owns approximately 0.1 miles of the line from College Corner Substation to the OH/IN State Line. DEOK owns the remaining 11.90 miles from the state line to Collinsville Substation. The entire 11.90 miles section that DEOK owns will be rebuilt with 954ACSS/TW conductor (@ 200C) and new double circuit structures. The College Corner (AEP) - Trenton (DEOK) line is on the other side of the double circuit structure and will also be rebuilt. DEOK will be doing a route survey to see if easement updates and/or additional structures are required. | DEOK |  | 2025-W1-156 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 45.1127 |  |  | New Upgrade
PJM WEST | b4002.2 | Adjust the relay settings at Penn Mar, Garrett, and Deep Creek substations to accommodate the new ratings and impedance changes associates with the Garrett- Garrett Tap 115 kV Line rebuild. | PENELEC |  | 2025-W1-692 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 0.13 |  |  | New Upgrade
PJM WEST | b4002.1 | -Rebuild approximately 1.9 miles of 115 kV line with larger conductor -Install OPGW for the static -Install one new SCADA controlled 2000 A disconnect with whips | APS |  | 2025-W1-692 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | PL | 9.01 |  |  | New Upgrade
PJM WEST | b4001.2 | Reconductor new Redbud McCanns Rd 138 kV Line with 795 KCMIL 45/7 ACSS for 0.5 miles from Redbud 138 kV Substation to Str. 175 of the existing Redbud - West Winchester 138 kV Line at approximate coordinates (39.217478, -78.128621). | APS |  | 2025-W1-631 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 5.03 |  |  | New Upgrade
PJM WEST | b4001.1 | Construct the McCanns Rd 138 kV Switching Station and interconnect the existing Redbud – West Winchester 138 kV Line and Bartonville – Stephenson 138 kV Line. | APS |  | 2025-W1-631 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 18.83 |  |  | New Upgrade
PJM MA | b4033.9 | Upgrade Line 6721 and 6778 Relaying to remove load limitation below line conductor capacity | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 1.11 |  |  | New Upgrade
PJM MA | b4033.8 | Build new 69 kV High Capacity Express Transmission Line 6786 on Western side of existing Line 6790 ROW, using TS Sniktau AECC advanced conductor. | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 41.741 |  |  | New Upgrade
PJM MA | b4033.7 | Replace 69 kV Transmission Line 6790 with Higher Capacity Line in East side of same ROW, using TS Sniktau AECC Conductor; Remove existing line 6790 upon completion of replacement line. | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 29.813 |  |  | New Upgrade
PJM MA | b4033.6 | DPL’s Oak Hall Substation 69kV yard shall be rebuilt to a breaker-and-a-half (BAAH) arrangement to accommodate new terminals positions required for the addition of a new Oak Hall – Tasley transmission line. The terminal additions would result in an eight (8) position ring bus; due to DPL planning criteria, this requires conversion to a four leg BAAH. A new control house is required to be installed as part of this ultimate buildout; all new relaying shall be housed in the new control building and be cut-in as appropriate throughout construction phases. Connections will need to be maintained between the existing and old houses for coordination with the 138kV yard. | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 32.46 |  |  | New Upgrade
PJM MA | b4033.5 | Replace Capacitor with New Capacitor rated 14.4 MVAR | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 1.139 |  |  | New Upgrade
PJM MA | b4033.4 | Add New Capacitor bank rated 3.6 MVAR | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 1.185 |  |  | New Upgrade
PJM MA | b4033.3 | Replace Capacitor with New bank rated 14.4 MVAR and Install additional second Capacitor bank rated 7.2 MVAR. | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 2.519 |  |  | New Upgrade
PJM MA | b4033.2 | Convert Tasley Substation to Breaker and a Half configuration with two new breaker bays. Terminate new Line 6786 and Replace Line 6790 with upgraded capacity. Relocate terminals for Lines 6703, 6721, 6778 and 6790 to new bay positions. Upgrade relaying for Line 6778 and 6721 to increase facility ratings to not limit below conductor rating (described in another component). Accommodate addition of two new capacitor banks described in previous substation component. The cost estimate for this component includes the cost for capacitor banks and their installation as well as the relay upgrades. | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 18.829 |  |  | New Upgrade
PJM MA | b4033.10 | Upgrade Line 6721 Relaying to remove load limitation below line conductor capacity | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 0.575 |  |  | New Upgrade
PJM MA | b4033.1 | Replace Capacitor with New bank rated 14.4 MVAR and Install additional second Capacitor bank rated 7.2 MVAR. | ODEC |  |  | TO Criteria Violation | 12/31/2030 |  | PL | 2.64 |  |  | New Upgrade
PJM WEST | b4028.1 | Rebuild 2.3 miles of the Mound Street-St Clair Avenue 138kV UG line with 5000 KCM XLPE cable. | AEP |  | 2025-W1-195 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 41.5861 |  |  | New Upgrade
PJM WEST | b4027.2 | Replace the 2" IPS Sch. 40 conductor with 4" IPS Sch. 40 conductor at Smith Mountain station on the Smith Mountain-Rock Castle branch allowing the branch to exceed a summer emergency rating of 1765 A. | AEP |  | 2025-W1-689 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.28373 |  |  | New Upgrade
PJM WEST | b4027.1 | Sag Study the Smith Mountain - Moneta 138 kV line. Approximately 14 structures will need to be added in existing Rights of Way to increase the sag along the existing centerline such that the higher requested ampacity can be achieved along the corridor and maintain safety clearances. | AEP |  | 2025-W1-689 | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 9.5961 |  |  | New Upgrade
PJM WEST | b4026.2 | Rebuild approximately 11.1 miles of 69kV line from Sherwood to Auglaize station. | AEP |  | 2025-W1-724 | TO Criteria Violation | 4/15/2030 |  | PL | 21.5096 |  |  | New Upgrade
PJM WEST | b4026.1 | Rebuild approximately 3.5 miles of 69kV line from Platter Creek to Sherwood station. | AEP |  | 2025-W1-724 | TO Criteria Violation | 4/15/2030 |  | PL | 7.1699 |  |  | New Upgrade
PJM MA | b4024.2 | Upgrade breaker, rigid bus, relay, and disconnect switch at Laurel Substation on the Sharptown - Laurel Facility. | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.703 |  |  | New Upgrade
PJM MA | b4024.1 | Rebuild existing Sharptown - Laurel 69kV circuit utilizing 954 ACSR "Rail" 45/7 conductor. | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 36.5463 |  |  | New Upgrade
PJM MA | b4023.1 | Upgrade existing 500 & 750 SDCU on Vienna side of Vienna - Loretto facility with 2x954 ACSR. Replace 3 - 138kV 600A disconnect switches with 2000A rated units. | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 12/1/2030 |  | PL | 1.8141 |  |  | New Upgrade
PJM MA | b4022.1 | Replace approx. 2 miles per circuit of existing HPFF cables with new 3500 KCM CU LPP HPFF cables. | BGE |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 58.4858 |  |  | New Upgrade
PJM MA | b4021.3 | Reconductor 69kV line from Prospect Park to North Paterson with a high-capacity conductor, including installing new composite poles and manholes along the line as required. | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 13.87 |  |  | New Upgrade
PJM MA | b4021.2 | Upgrade the Pfisterer connection inside of North Paterson to accept new high-capacity cable, reconfigure duct banks in North Paterson to accommodate new high-capacity cable | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 1.1665 |  |  | New Upgrade
PJM MA | b4021.1 | Upgrade the Pfisterer connection inside of Prospect Park to accept new high-capacity cable, modify conduit as needed | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.66626 |  |  | New Upgrade
PJM MA | b4019.3 | Reconductor 69kV line from Rahway to Roselle Station. High capacity conductor to be rated at least 1100 Summer Normal and 1200 Summer Emergency. 2 miles of OH wreck and rebuild 2.5 miles of OH new construction 0.2 miles of UG Replace fiber as required. | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 27 |  |  | New Upgrade
PJM MA | b4019.2 | Replace/update riser structure, pot head, cable and sweeps as required to accept high-capacity conductor at Roselle 69kV. Rebuild duct banks as needed. | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 1.35 |  |  | New Upgrade
PJM MA | b4019.1 | Replace/update riser structure, pot head, cable and sweeps as required to accept high-capacity conductor at Rahway 69kV. Rebuild duct banks as needed | PSEG |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 1.05 |  |  | New Upgrade
PJM MA | b4018.9 | Loop the Leisure Village-South Lakewood 34.5 kV F214 line into the new 34.5 kV ring bus station, approximately 0.1 miles. To the north, the existing line is constructed on double circuit wood monopole structures in a vertical configuration. The existing line shares structures with the Larrabee-Metedeconk 34.5 kV E213 line. To the south, the existing line is constructed on single circuit wood monopole structures in a vertical configuration. Installs (0.1) miles of 3-phase 795 ACSR conductor shielded by (1) 7#9 Alumoweld wire (3) structures: (1) SC wood monopole deadend structure, like TR-034030, direct embed (1) SC steel monopole angle structure, like TR-069015, drilled shaft foundation (1) SC steel monopole deadend structure, like TR-069030, drilled shaft foundation Hardware for (2) DC steel monopole deadend structures, like TR-115370 and TR-115375 Substation deadend insulator assemblies at (2) locations Removals (0.1) miles of 3-phase 565 ACSR conductor shielded by (1) Alumoweld wire (1) wood monopole structure, direct embed | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.91921 |  |  | New Upgrade
PJM MA | b4018.8 | Build a new 34.5 kV Ring Bus switching station (Adjacent to Vermont Avenue Substation) Install (1 Lot) of cable trench Install (1 Lot) of conduit, grounding & foundations for new equipment. Install (1) Prefabricated Control Enclosure, 22'x42' Install (2) 34.5 kV A-frame Deadend Structures Install (2) 34.5 kV H-frame Deadend Structures Install (5) 69 kV Circuit Breakers Install (11) 34.5 kV GOAB Disconnect Switches Install (5) 34.5 kV MOAB Disconnect Switches Install (5) 3-phase sets 34.5 kV CVT's Install (5) 3-phase sets of 34.5 kV Surge Arresters Install (2) 34.5 kV SSVT's Install (1 Lot) of rigid bus, connectors & support structures. Install (1 Lot) of fencing. Install security system. Install (5) Standard breaker panels, consisting of (1) SEL-451 Install (3) Standard line panels, consisting of (2) SEL-421 relays, over fiber Install (2) Standard bus diff panels, consisting of (2) SEL-487B for high side lead protection Add (2) SEL-451 for high side breaker failure protection Install (1) RTAC, HMI & GPS panel | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 13.3276 |  |  | New Upgrade
PJM MA | b4018.7 | Reconfigure 34.5 kV switchyard at Metedeconk Substation to a breaker-and-a-half yard. Install (1 Lot) of cable trench Install (1 Lot) of conduit, grounding & foundations for new equipment. Install (1) Prefabricated Control Enclosure 22'x42' Install (3) 34.5 kV A-frame Deadend Structures Install (3) 34.5 kV Pothead Risers Install (9) 69 kV Circuit Breakers Install (18) 34.5 kV GOAB Disconnect Switches Install (6) 34.5 kV MOAB Disconnect Switches Install (6) 3-phase sets of 34.5 kV CVT's Install (9) 34.5 kV Surge Arresters Install (2) 34.5 kV SSVT's Install (1 Lot) of Rigid Bus, Connectors & Support Structures Install (1 Lot) of Fencing Install Security System Install (9) Standard Breaker Panels, consisting of (1) SEL-451 Install (3) Standard Line Panels, consisting of (2) SEL-421 relays, over fiber Install (5) Standard Bus Diff Panels, consisting of (2) SEL-487B relays (2) for bus protection (3) for high side lead protection Install (1) RTAC, HMI & GPS panel | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 2.1788 |  |  | New Upgrade
PJM MA | b4018.6 | Metedeconk 34.5 kV Breaker-and-a-half switchyard line terminal and new 34.5 kV Ring Bus station line terminal at Leisure Village Substation. Remove (1) existing relay panel Change drawings and update nameplates (on the South Lakewood 34.5 kV F214 Line Terminal) for the new terminal designation of the new 34.5 kV Ring bus substation. Install (1) SEL-421 Install (1 Lot) of Control Cables Revise relay settings for existing SEL-421 | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.15256 |  |  | New Upgrade
PJM MA | b4018.5 | Remove equipment and add breakers and switches at Metedeconk Substation. Install (1 Lot) of conduit, grounding & foundations for new equipment. Install (2) 69 kV Circuit Breakers, 40 kA, 3000 A Install (2) 34.5 kV GOAB Disconnect Switches, 1200 A. Install (2) Standard distribution transformer protection panels. Remove equipment to isolate transformers: (1) 34.5 kV Bus Tie Breaker (3) 34.5 kV Disconnect Switches (Stands to be retained to act as bus support stand) (2) 34.5 kV fused disconnects | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 14.4634 |  |  | New Upgrade
PJM MA | b4018.4 | Metedconk 34.5 kV Breaker-and-a-half switchyard line terminal and new 34.5 kV ring bus station line terminal at Larrabee Substation Terminate new line conductor (on the Metedconk 34.5 kV E213 Line Terminal) Terminate new line conductor (on the Metedconk 34.5 kV W127 Line Terminal) Replace limiting 397.5 AAC Conductor with conductor rated at least 70/85/79/100 MVA (SN/SSTE/WN/WSTE) (on the Metedconk 34.5 kV W127 Line Terminal) Revise relay settings (on the Metedconk 34.5 kV E213 Line Terminal and the Metedconk 34.5 kV W127 Line Terminal) | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.12617 |  |  | New Upgrade
PJM MA | b4018.3 | Terminate 34.5 kV lines to new 34.5 kV ring bus station Change drawings and nameplates for new line terminal names. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.22219 |  |  | New Upgrade
PJM MA | b4018.2 | New 34.5 kV switching station terminal at South Lakewood Substation. Remove (2) existing relays Change drawings and update nameplates (on the Leisure Village 34.5 kV F214 Line Terminal) for the new terminal designation of the new 34.5 kV switching station Install (1) SEL-421 Install (1) SEL-451 Install (1 Lot) of Control Cables | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.15131 |  |  | New Upgrade
PJM MA | b4018.13 | Install a new tie line from the existing Vermont Avenue Substation to the new 34.5 kV ring bus station, approximately 0.1 miles Install: 0.1 miles of 3-phase 795 ACSR conductor shielded by (1) 7#9 Alumoweld wire (2) SC steel monopole deadend structures, like TR-069025, drilled shaft foundations Substation deadend insulator assemblies at (2) locations | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.68325 |  |  | New Upgrade
PJM MA | b4018.12 | Install a new tie line from the existing Vermont Avenue Substation to the new 34.5 kV ring bus station, approximately 0.1 miles. Install: 0.1 miles of 3-phase 795 ACSR conductor shielded by (1) 7#9 Alumoweld wire (2) SC steel monopole deadend structures, like TR-069025, drilled shaft foundations Substation deadend insulator assemblies at (2) locations | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.75043 |  |  | New Upgrade
PJM MA | b4018.11 | Install new hardware and wire on the Larrabee - Point Pleasant No. 2 34.5 kV R44 line to support the rebuild project, approximately 2.6 miles The existing line is constructed on double circuit wood monopoles structures in a vertical configuration. The existing line shares structures with the Larrabee-Metedeconk 34.5 kV E213 line. Install: 2.6 miles of 3-phase 795 ACSR conductor (1) SC steel monopole deadend structure, like TR-069030, drilled shaft foundation Hardware for (57) DC LD steel monopole tangent structures, like TR-034110 Hardware for (6) DC steel monopole angle structures, like TR-115365 Hardware for (8) DC steel monopole deadend structures, like TR-115370 and TR-115375 Substation deadend insulator assemblies at (1) location Remove: 2.6 miles of 3-phase 556.5 ACSR conductor | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 17.7989 |  |  | New Upgrade
PJM MA | b4018.10 | Install new hardware and wire on the Herbertsville - Larrabee 34.5 kV Q43 line to support the rebuild project of approximately 2.6 miles The existing line is constructed on double circuit wood monopoles structures in a vertical configuration. The existing line shares structures with the Larrabee-Metedconk 34.5 kV W127 line. Install: 2.6 miles of 3-phase 795 ACSR conductor (1) SC steel monopole deadend structure, like TR-069030, drilled shaft foundation Hardware for (56) DC LD steel monopole tangent structures, like TR-034110 Hardware for (7) DC steel monopole angle structures, like TR-115365 Hardware for (6) DC steel monopole deadend structures, like TR-115370 and TR-115375 Substation deadend insulator assemblies at (1) location Remove: 2.6 miles of 3-phase 556.5 ACSR conductor | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 14.8163 |  |  | New Upgrade
PJM MA | b4018.1 | Purchase land needed to support construction of new 34.5 kV switching station. This includes purchase of (3) parcels in New Jersey. Parcel #: 15 01092-0000-00001 Parcel #: 15 01092-0000-00009 Parcel #: 15 01091-0000-00001 Real Estate Assumptions: 0.53 acres needed for the new 34.5 kV switching station. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.14561 |  |  | New Upgrade
PJM MA | b4017.6 | At Cookstown Substation: Below Grade: Install (1 Lot) of conduit, grounding, cable trench & foundations for substation expansion oAbove Grade: Install (1) 34.5 kV Box structure bay (Modeled as H-Frame structure) Install (1) 34.5 kV Circuit breaker Install (2) 34.5 kV GOAB disconnect switches Install (1) 34.5 kV MOAB disconnect switch Install (3) 34.5 kV Surge Arresters Install (3) 34.5 kV CVTs Install (1 Lot) of Conductors and Connectors for Jumpers Install (1 Lot) of rigid bus, connectors & support insulators Relaying & Control: Install (2) FE Standard Line Relay Panels each consisting of (1) SEL-421 and (1) SEL-411L, over fiber Install (2) FE Standard Breaker Panels each consisting of (1) SEL-451 Install (1) FE Standard Bus Panel consisting of (2) SEL-487B Install (1 Lot) of Control Cables | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 2.3593 |  |  | New Upgrade
PJM MA | b4017.5 | Rebuild the Cookstown – Van Hiseville 34.5 kV V22 line from Str #91445 to Greater Adventure Substation as double circuit, approximately 5.2 miles. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 17.9341 |  |  | New Upgrade
PJM MA | b4017.4 | Rebuild the Cookstown – Windsor 34.5 kV H60 line from Cookstown Sub to Str #58 as double circuit, approximately 4.7 miles. Terminate new line into Cookstown Substation. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 14.5853 |  |  | New Upgrade
PJM MA | b4017.3 | Relay Settings for the Great Adventure 34.5 kV Breaker-and-a-half Substation at Windsor Substation Revise relay settings (on the Cookstown 34.5 kV H60 Line Terminal) | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.076501 |  |  | New Upgrade
PJM MA | b4017.2 | Great Adventure 34.5 kV Breaker-and-a-half Substation. Install (1 Lot) of Below Grade Conduit, Grounding Wire, Foundations and Connectors Insall (185' x 185') of Grading, Grounding and Stone Install (320') of Cable Trench Above Grade: Install (1 Lot) of fencing Install (1) Prefabricated Control Enclosure 22'x42' Install (4) 34.5 kV A-Frame Dead-end Structures Install (11) 34.5 kV Circuit Breakers Install (7) 34.5 kV MOAB Disconnect Switches, 2000A Install (23) 34.5 kV GOAB Disconnect Switches, 2000A Install (21) 34.5 kV Surge Arresters Install (27) 34.5 kV CVTs Install (1 Lot) of Conductors and Connectors for Jumpers Install (1 Lot) of rigid bus, connectors & support structures. Install (4) 3-phase sets of Free Standing CTs Relaying & Control: Install (13) FE Standard Breaker Panels, consisting of (1) SEL-451 relay Install (7) FE Standard Line Relay Panels, consisting of (2) SEL-421 relays, over fiber. Install (4) FE Standard Bus Diff Panels, consisting of (2) SEL-487B relays, for Bus A&B and Cap Bank Install (2) FE Standard Bus Diff Panels, consisting of (2) SEL-487B and (1) SEL-451 relays, for Transformer Bank 1 & 2 Install (1 Lot) of Control Cables Estimated (2) in-sub fiber run to provide communications and control to the new Six Flags customer POI. Estimated (6) miles of ADSS fiber underbuild on the V22 line to connect to the fiber backbone. Estimated (1) mile of ADSS fiber on the V22 line to connect to the fiber backbone at Structure 91445. Estimated (5) miles of ADSS fiber underbuild to terminate at Cookstown on line H60. Estimated (2) miles of ADSS fiber between Structure 58 and the V22 line. Estimated (7) miles of ADSS fiber between Van Hiseville Substation and the V22 line. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 26.1663 |  |  | New Upgrade
PJM MA | b4017.1 | Great Adventure 34.5 kV Breaker-and-a-half Substation at Van Hiseville Substation. Relaying & Control: Change drawings and update nameplates on the Cookstown 34.5 kV V22 (to be Great Adventure) Line Terminal Install (1) FE Standard Line Relay Panel consisting of (2) SEL-421 Install (1) FE Standard Breaker Panel consisting of (1) SEL-451 Install (1 Lot) of Control Cables | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.55392 |  |  | New Upgrade
PJM MA | b4016.4 | Rebuild a section of the Englishtown - Monroe Junction 34.5 kV H34 Line that is mutual with the Costco - Monroe Junction 34.5 kV N40 Line near Monroe Junction Substation, approximately 0.4 miles. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.76263 |  |  | New Upgrade
PJM MA | b4016.3 | Install 1 relay and revise relay settings at Costco Substation Revise relay settings (On the Monroe Junction 34.5 kV N40 Line terminal) Install (1) SEL-421 PR relay (In the Monroe Junction 34.5 kV N40 Line panel) | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.25186 |  |  | New Upgrade
PJM MA | b4016.2 | Terminate new line conductor. Replace (1 Lot) of limiting conductor (397.5 ACSR), with conductor rated to meet or exceed 55/67/63/79 MVA (SN/SSTE/WN/WSTE) Revise relay settings (On the Costco 34.5 kV N40 Line terminal) | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.2073 |  |  | New Upgrade
PJM MA | b4016.1 | Rebuild the Jamesburg - Monroe 34.5 kV N40 Line from Jamesburg Substation to Monroe Junction Substation, approximately 1.2 miles. | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 5.1329 |  |  | New Upgrade
PJM MA | b4015.1 | At Long Branch Substation replace the Allenhurst 34.5 kV V74 Line Terminal disconnect switch Install (1 Lot) of Grounding Wire and Connectors Install (1 Lot) of Below Grade Conduit Replace (1) 34.5 kV Disconnect Switch (D28), with (1) 34.5 kV Manual Group Operated Disconnect Switch, 1200A (On the Allenhurst 34.5 kV V74 Line Terminal) Install (1 Lot) of Conductors and Connectors for Jumpers | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.53241 |  |  | New Upgrade
PJM MA | b4014.1 | 34.5 kV Cap Bank Addition at Sussex Substation. Install (1 Lot) of conduit, grounding and foundations for new capacitor bank. Install (1) 34.5 kV Disconnect switch, 1200A. Install (1) 34.5 kV Capacitor bank, 5.4 MVAR Install (1) 34.5 kV 3-PH Cap switcher, with 30 Ohm pre-insertion resistor. Install (3) 34.5 kV Free standing CT's Install (1 Lot) of conductor, rigid bus, connectors & support structures. Install (1) Standard cap bank panel, consisting of (2) SEL-487V & (1) SEL-451 relays | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 2.2755 |  |  | New Upgrade
PJM MA | b4013.1 | 34.5 kV Cap Bank Addition at Colts Neck Substation Install (1 Lot) of foundations, conduit, and grounding for the new equipment Install (1 Lot) of fencing, grading, and ground grid for the yard Install (1) 34.5 kV Cap Switcher, 1200A Install (1) 34.5 kV MOAB Disconnect Switch Install (1) 3-phase set of 34.5 kV Surge Arresters Install (1) 3-phase set of 34.5 kV Free Standing CTs Install (1) 34.5 kV Cap Bank, 10.8 MVAR Install(1 Lot) of Connectors and Jumpers for Cables Install (1 Lot) of Rigid Bus and Support Relaying & Control: Install (1) FE Standard Dual Cap Bank Relay Panel consisting of (2) SEL-487V Install (1) FE Standard Breaker Panel consisting of (1) SEL-451 Install (1 Lot) of Control Cables | JCPL |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 2.6939 |  |  | New Upgrade
PJM MA | b4012.1 | Belleville – Center Union 46 kV Line -Replace structures and use 795 ACSR 26/7 conductor on spans D-356 through D-360 | PENELEC |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 2.7193 |  |  | New Upgrade
PJM MA | b4011.3 | Rebuild the Jackson - North Hanover 115 kV 968 Line as a double circuit, approximately 13.2 miles, using 954 ACSR 45/7. The line will be energized in a six-wire configuration. | ME |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 57.6529 |  |  | New Upgrade
PJM MA | b4011.2 | Replace limiting conductors, line relaying, circuit breaker and two 115 kV disconnect switches at Jackson on the North Hanover terminal. | ME |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.57372 |  |  | New Upgrade
PJM MA | b4011.1 | Install new 115 kV capacitor, replace limiting conductors, line relaying, and disconnect switches at North Hanover on the Jackson terminal. | ME |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 3.5589 |  |  | New Upgrade
PJM MA | b3987.1 | Replace East Flemington 34.5 kV circuit breakers C731, V724, A729, TC, H736, AV, YH, and Y727 with 40 kA, 3000 A breakers. | JCPL |  |  | Short Circuit | 6/1/2030 |  | PL | 3.4577 |  |  | New Upgrade
PJM MA | b3986.1 | Replace Windsor 34.5 kV Breakers: KQ Q143 324-B-25 (J136-1) 324-B-22 (J2) 324-B-31 (MG) 324-B-34 (K137-1) 324-B-19 (BK2) 324-B-28 (M65-1) 324-B-16 (G215-1) BK4 324-B-7 (H4) 324-B-8 (H60) 324-B-54 (BK5_BBUS) 324-B-51 (BK5_ABUS) | JCPL |  |  | Short Circuit | 6/1/2029 |  | PL | 8.363 |  |  | New Upgrade
PJM WEST | b3980.3 | Groton Substation: - Revise relay settings | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3980.2 | Bellevue Substation: - Replace (3) 69 kV disconnect switches - Revise relay settings - Replace limiting substation conductor | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.47 |  |  | New Upgrade
PJM WEST | b3980.1 | Bellevue-Groton 69 kV Line: - Rebuild 4 miles of the Bellevue - Groton 69 kV Line | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 9.53 |  |  | New Upgrade
PJM WEST | b3979.3 | Abbe-Johnson No.1 69 kV Line (Spring Valley-Lorain College) - Replace (2) 69 kV disconnect switches | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.44 |  |  | New Upgrade
PJM WEST | b3979.2 | Abbe-Johnson No.1 69 kV Line (Elyria Water P.C.-Spring Valley): - Replace (1) 69 kV Disconnect Switch | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.71 |  |  | New Upgrade
PJM WEST | b3979.1 | Abbe-Johnson No.1 69 kV Line (Johnson - Elyria Water P.C.): - Reconductor one span of transmission line between Johnson Substation and Elyria Water P.C. - Replace (1) 69 kV Disconnect Switch - Upgrade (1) Thermal Relay - Modify Elyria Loop Tap configuration - Install (1) 69 kV Disconnect Switch | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 2.07 |  |  | New Upgrade
PJM WEST | b3978.2 | Replace Limiting Terminal Equipment at Lakeview Substation - (2) Thermal Relays - (2) 138 kV Disconnect Switches - limiting Substation Conductor | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.32 |  |  | New Upgrade
PJM WEST | b3978.1 | - Reconductor 1 span of transmission line outside Ottawa Substation - Reconductor 1 span of transmission line outside Lakeview Substation | ATSI |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.09 |  |  | New Upgrade
PJM WEST | b3977.1 | At Meadow Brook: - Install conduit and grounding for new equipment. - Install (1) lot of cables and grounding for new equipment. - Replace (1) 138 kV wave trap on the West Winchester line terminal. | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 0.35 |  |  | New Upgrade
PJM WEST | b3976.1 | At Bedington: - Install foundation, conduit, and grounding for new equipment. - Install (3) 138 kV surge arresters. - Replace (1) existing 138 kV CVT with (3) 138 kV CVT's. - Replace (1 Lot) of limiting conductor. - Install (1 Lot) of cables and grounding. - Replace (1) existing 138kV Eagle line terminal relay panel and breaker failure, with (1) standard line relaying panel consisting of (1) SEL-421, (1) SEL-411L, and (1) SEL-451. | APS |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.96 |  |  | New Upgrade
PJM WEST | b3975.1 | Install a new 138/69 kV transformer at Catawba station with a high side Circuit Switcher and a low side Circuit Breaker. | AEP |  |  | TO Criteria Violation | 12/1/2030 |  | PL | 7.774 |  |  | New Upgrade
PJM WEST | b3974.1 | Replace circuit breaker R with a new 69kV, 40 kA circuit breaker. | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 0.85 |  |  | New Upgrade
PJM WEST | b3972.1 | Perform a ratings study and clearance mitigation on the ~5.55-mile section of sag derated 556.5 ACSR 26/7 DOVE conductor (East Lima – STR 28) between the East Lima – Haviland 138 kV circuit on the East Lima – West Lima 138 kV line. | AEP |  |  | Baseline Load Growth Deliverability & Reliability | 4/15/2030 |  | PL | 6.8 |  |  | New Upgrade
PJM WEST | b3971.1 | At Haviland, Reconductor Bus#1 Sub cond 500 MCM CU 37 Str towards Haviland Bus#2 and Reconductor Haviland Bus#2 500 KCM CU, 37-Str. & 795 KCM AAC, 37-Str. towards Timber SW 138kV. | AEP |  |  | Baseline Load Growth Deliverability & Reliability | 12/1/2030 |  | PL | 1.4676 |  |  | New Upgrade
PJM WEST | b3970.1 | Rebuild Line: ~2.87 miles Kenton - South Kenton 69kV | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 13.1925 |  |  | New Upgrade
PJM WEST | b3969.1 | Replace Findlay Center Transformer #1 with a 138/69/34.5 90 MVA Unit. Replace the TR1 LS Disconnect Switch. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 3.9365 |  |  | New Upgrade
PJM WEST | b3968.1 | Replace North Newark TR#1 with a 90 MVA bank. DICM expansion will be required. Replace Motor Operators on High side switch “Z”. Install (2) 138kV disconnects on existing 138kV lattice box bay. Install (2) 69kV disconnects on existing 69kV H-frame structure. | AEP |  |  | TO Criteria Violation | 12/1/2030 |  | PL | 6.3295 |  |  | New Upgrade
PJM WEST | b3967.1 | Replace the existing Cambridge 34.5kV Circuit Breaker F with a 40kA, 3000A unit | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.79762 |  |  | New Upgrade
PJM WEST | b3966.1 | Replace 138 kV circuit breakers A, AA, D, E, F, XT1, and XT2 with 63 kA fault current capable counterpart. Reroute one line entrance in the station to make more room for the larger breakers. | AEP |  |  | Short Circuit | 9/30/2030 |  | PL | 3.5639 |  |  | New Upgrade
PJM WEST | b3965.1 | Replace 138 kV circuit switchers XT1, XT3, XT2, and XT4 with 63kA fault current capable counterpart. | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 4.6025 |  |  | New Upgrade
PJM WEST | b3964.1 | The 138kV circuit switcher XT3 will be replaced with a 63 kA breaker. | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 0.93925 |  |  | New Upgrade
PJM WEST | b3963.1 | Replace 138 kV circuit breakers 102, 103 and circuit switcher XT4 with 63 kA fault current capable breakers. | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 2.8931 |  |  | New Upgrade
PJM WEST | b3962.1 | Replace 138 kV circuit breakers CB-H014F2 and CB-H014F5 with 63 kA fault current capable breakers | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 0.84614 |  |  | New Upgrade
PJM WEST | b3961.1 | Replace station terminal equipment: South Side Lima 34.5 kV replace 4/0 AAC, 7-Str. Replace 34.5KV CB-L jumpers and 34.5KV Sterling line riser. | AEP |  |  | TO Criteria Violation | 12/1/2030 |  | PL | 0.084626 |  |  | New Upgrade
PJM WEST | b3960.1 | Replace 138 kV, 40kA circuit breaker DD with higher fault current capable counterpart (63kA). The new CB will have a larger footprint which will require the shifting of nearby equipment. | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 0.77267 |  |  | New Upgrade
PJM WEST | b3959.1 | The line section overloading is roughly ~0.8 miles consisting of 336 ACSR 30/7 Oriole from structure 44 to Lick station. Reconductor limiting line conductor on the Lick-Ironman 69kV circuit to match the rest of the line. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 1.0995 |  |  | New Upgrade
PJM WEST | b3958.1 | Perform sag study mitigations on ~1.4 miles of line from str. 8 to str 21 to bring conductor to full 142 MVA SE rating. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.3605 |  |  | New Upgrade
PJM WEST | b3957.1 | At Haviland substation, replace TR#4 with 138/69/12kV 130MVA bank, along with associated equipment such as the Switch (600A), Sub cond 795 AAC 37 Str., and Sub cond 300 MCM CU bus equipment. | AEP |  |  | TO Criteria Violation | 12/1/2030 |  | PL | 5.8704 |  |  | New Upgrade
PJM WEST | b3956.1 | Upgrade 336.4 ACSR 26/7 station conductor at Galloway 69kV. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.18065 |  |  | New Upgrade
PJM WEST | b3955.2 | Install additional 2-138kV circuit breakers at Milepost substation to allow for the Robert - Wilson 138kV line to come into the milepost substation. DICM will need an expansion for additional relaying panels. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 3.8448 |  |  | New Upgrade
PJM WEST | b3955.1 | Build ~0.8 mile 138kV double circuit extension from Roberts - Wilson 138kV line into the Milepost 138kV substation. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 8.3256 |  |  | New Upgrade
PJM WEST | b3953.1 | Replace 138kV circuit switcher XT3 with a higher fault current capable circuit breaker at New Carlisle.? | AEP |  |  | Short Circuit | 6/1/2030 |  | PL | 1.0247 |  |  | New Upgrade
PJM WEST | b3952.1 | Replace 138 kV, 3000 A circuit breakers H and H1 with 4000 A circuit breakers. | AEP |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2030 |  | PL | 1.5138 |  |  | New Upgrade
PJM WEST | b3951.1 | To solve the voltage violations, a 69kV circuit switcher and a 11.5 MVar capacitor bank will be installed on the 69kV bus at Falcon station. Falcon station will need to be expanded to fit the capacitor bank. | AEP |  |  | TO Criteria Violation | 4/15/2030 |  | PL | 3.35 |  |  | New Upgrade
PJM WEST | b3950.1 | Adjust existing Tazewell 138/34.5 kV transformer tap to 1:1 to help mitigate voltages on the 34.5 kV bus. | AEP |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3949.2 | Change the XF tap settings at Huff Creek station to boost the sub-transmission voltage. | AEP |  |  | TO Criteria Violation | 4/15/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3949.1 | Change XF tap settings at Chauncey station to boost the sub-transmission voltage. | AEP |  |  | TO Criteria Violation | 4/15/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3948.1 | Replace the existing 9.6 MVar 69kV capacitor bank at Johns Creek station with a 17.2 MVar capacitor bank. Circuit switcher "AA" will also be replaced. | AEP |  |  | TO Criteria Violation | 4/15/2030 |  | PL | 1.477 |  |  | New Upgrade
PJM WEST | b3947.1 | Remove cans on existing Baileysville 46 kV Cap Bank to reduce it to 7.2 MVAR | AEP |  |  | TO Criteria Violation | 12/1/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3946.2 | Adjust the existing Hartland 46 kV cap bank Vhi setting to 1.04 | AEP |  |  | TO Criteria Violation | 4/15/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3946.1 | Adjust existing Jarrett 138/46 kV transformer tap to 1:1 to boost voltages on the sub-transmission network. | AEP |  |  | TO Criteria Violation | 4/15/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3945.1 | Adjust Mullens 138 kV Cap Bank Vhi setting to 1.04. Adjust protection settings as needed at the station. | AEP |  |  | Baseline Load Growth Deliverability & Reliability | 12/1/2030 |  | PL | 0.1 |  |  | New Upgrade
PJM WEST | b3944.1 | Rebuild the McGuffey to Locust 69kV line (~1.35 miles) with 954ACSR Rail Conductor and OPGW. The (54) wood poles will be replaced with light duty, steel poles. The rebuild will take place in the existing right-of-way and the distribution underbuilds will also be restored. Conductor drops going into McGuffey and Locust substations will be replaced with 954 AAC conductor. | DEOK |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 5.3156 |  |  | New Upgrade
PJM WEST | b4006.1 | Install 765/345 kV TR 91 and associated 765 kV and 345 kV circuit breakers at Wilton Center. | ComEd |  | 2025-W1-906 | Baseline Load Growth Deliverability & Reliability | 12/1/2030 |  | PL | 45.8052 |  |  | New Upgrade
PJM WEST | b3982.1 | Disconnect and remove the 34 kV tertiary cap bank on the Cherry Valley 345/138 kV transformer TR 82 and install a 138 kV bus 3 cap bank and associated equipment at Cherry Valley substation. | ComEd |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 7.7349 |  |  | New Upgrade
PJM WEST | b3981.1 | Install a new 345/138 kV TR83 at Elk Grove and associated equipment. Install three 138 kV and one 345 kV circuited breakers and associated equipment at Elk Grove substation. | ComEd |  |  | TO Criteria Violation | 6/1/2030 |  | PL | 28.9573 |  |  | New Upgrade
PJM WEST | b3943.1 | Install a new 345/138 kV transformer TR 84, and associated equipment at State Line substation. Install two 345 kV circuit breakers, one 138 kV circuited breaker and associated equipment, also replace the 138 kV BT 732 circuit breaker at State Line substation. | ComEd |  |  | Baseline Load Growth Deliverability & Reliability | 12/1/2030 |  | PL | 20.8072 |  |  | New Upgrade