## Appendix
Region | Upgrade ID | Description | Transmission Owner | Immediate Need | Project Submittal Number | Drivers | Required In-Service Date | Revised In-Service Date | Status | TEAC Date | Latest TEAC Date | Initial TEAC Cost ($M) | Latest TEAC Cost ($M) | Board Approval Date | Issue Category
PJM MA | b3794.1 | Replace existing Waldwick 230 kV 50 MVAR fixed shunt reactor with a 230 kV 150 MVAR variable shunt reactor. | PSEG |  | 2023-W1-107 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 | 9/3/2029 | UC | 10/31/2023 | 7/7/2026 | 13.6 | 21.9 | 2/28/2024 | Scope/Cost Change
PJM MA | b3794.2 | Replace existing Waldwick 345 kV 100 MVAR fixed shunt reactor with a 345 kV 150 MVAR variable shunt reactor. | PSEG |  | 2023-W1-107 | Baseline Load Growth Deliverability & Reliability | 6/1/2028 | 10/2/2028 | UC | 10/31/2023 | 7/7/2026 | 16 | 23.5 | 2/28/2024 | Scope/Cost Change
PJM SOUTH | b3800.243 | Rebuild 7.26 miles of existing 500 kV circuit from Dickerson Station H to Ed's Ferry area to accommodate the new 500 kV circuit between Doubs and Aspen. (The 500 kV portion of the work) | PEPCO |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 10/31/2023 | 10/6/2026 | 37.2 | 26.53 | 12/11/2023 | Scope/Cost Change
PJM SOUTH | b3800.244 | Rebuild 7.26 miles of existing 230 kV circuit from Dickerson Station H to Ed's Ferry area to accommodate the new 500 kV circuit between Doubs and Aspen. (The 230kV portion of the project) | PEPCO |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 10/31/2023 | 10/6/2026 | 18.6 | 65.06 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.27 | High Ridge 500 kV substation (cut into Brighton-Waugh Chapel 500 kV line) - Waugh Chapel side. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 33.67 | 40.16 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.28 | High Ridge 500 kV substation (cut into Brighton-Waugh Chapel 500 kV line) -Brighton side. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 33.67 | 40.16 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.29 | High Ridge termination for the North Delta-High Ridge 500 kV line. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 33.67 | 40.16 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.30 | High Ridge - Install two 500/230 kV transformers. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 22.11 | 78.34 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.31 | Build new North Delta-High Ridge 500 kV line. | PECO |  | 2022-W3-344 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 13.36 | 71.2 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.32 | Build new North Delta-High Ridge 500 kV line. (~59 miles). | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 407.11 | 810.14 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.34 | Rebuild 5012 (existing Peach Bottom-Conastone) (new Graceton-Conastone) 500 kV line on single circuit structures within existing ROW and cut into North Delta 500 kV and Gracetone 500 kV stations. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 70 | 61.17 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.35 | Rebuild 5012 (existing Peach Bottom-Conastone) (new North Delta-Graceton PECO) 500 kV line on single circuit structures within existing ROW and cut into North Delta 500 kV and Gracetone 500 kV stations. | PECO |  | 2022-W3-344 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 29.86 | 60.9 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.36 | Rebuild 5012 (existing Peach Bottom-Conastone) (new North Delta-Graceton BGE) 500 kV line on single circuit structures within existing ROW and cut into North Delta 500 kV and Gracetone 500 kV stations. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 10.44 | 21.32 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.37 | Replace terminal equipment limitations at Conastone 500 kV - on the (existing Peach Bottom-Conastone) or (new Graceton-Conastone) 500 kV line. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 4.93 | 6.27 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.38 | Chalk Point-Cheltanham 500 kV (5073) - Replace relay at Chalk Point 500 kV. | PEPCO |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 0.34 | 0.76 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.4 | New Otter Creek to Doubs 500 kV line (MD Border-PSEG Demarcation Point). Rebuild and expand existing ~1.6 miles of Otter Creek-Conastone 230 kV line to become a double-circuit 500 and 230 kV lines. | BGE |  | 2022-W3-374 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 11.11 | 33.73 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.41 | Conastone-Brighton 500 kV (5011 circuit) - Replace terminal equipment limitations at Conastone 500 kV. | BGE |  | 2022-W3-660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 7.16 | 8.01 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.42 | Peach Bottom North bus upgrade - Replace 11 – Instances of strain bus conductor used for breaker drops or CT drops, 7 – 500 kV disconnect switches, 7 – Free Standing CTs, 1 – 500 kV breaker, 2 – Breaker relays or meters. | PECO |  | 2022-W3-344 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 12/5/2023 | 10/6/2026 | 2.7 | 7.27 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.44 | North Delta termination for the North Delta-High Ridge 500 line (PECO work). | PECO |  | 2022-W3-344 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 10/31/2023 | 10/6/2026 | 3.4 | 5 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.45 | North Delta 500 kV termination for the Rock Springs 500 kV line (5034/5014 line) (PECO work). | PECO |  | 2022-W3-344, DENL | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 10/31/2023 | 10/6/2026 | 10.2 | 1.9 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.47 | Build new Peach Bottom South-North Delta 500 kV line – cut in to Peach Bottom tie No. 1 and extending line to North Delta (~1.25 miles new ROW). | PECO |  | 2022-W3-344 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 10/31/2023 | 10/6/2026 | 5.5 | 21.4 | 12/11/2023 | Scope/Cost Change
PJM MA | b3800.52 | Reconfigure Peach Bottom North and South yards to allow for termination of 500 kV lines from Peach Bottom to North Delta. North Delta 500 kV termination for the new Peach Bottom-North Delta 500 kV line. | PECO |  | 2022-W3-344/660 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | EP | 10/31/2023 | 10/6/2026 | 7.86 | 21.5 | 2/28/2024 | Scope/Cost Change
PJM WEST | n104.1 | a new three (3) circuit breaker 138 kV station, Snowhill, physically configured in a breaker and half bus arrangement but operated as a ring-bus | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 6.5353 |  |  | Cancelled
PJM WEST | n104.2 | Connect Snowhill 138 kV Station to Existing Transmission Circuit, Update Remote End Protective Relay Settings | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.8126 |  |  | Cancelled
PJM WEST | n104.3 | Replace Protective Relays at Strawton 138 kV Station | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.1987 |  |  | Cancelled
PJM WEST | n104.4 | Install Two (2) Fiber-Optic Paths to facilitate relaying between Snowhill, Deer Creek, and Strawton 138 kV Stations | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.2403 |  |  | Cancelled
PJM WEST | n104.5 | Replace Three (3) Structures, Six (6) Spans of Conductor along the Deer Creek - Makahoy 138 kV Circuit | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.6282 |  |  | Cancelled
PJM WEST | n5350.2 | Ameren End: Build a new 345 kV line from Bunsonville-Eugene | AEP |  |  |  | 6/1/2021 |  | Cancelled | 10/12/2017 | 10/12/2017 | 57.5 |  |  | Scope/Cost Change
PJM SOUTH | n6287.1 | Add additional 230kV breaker at Trowbridge to prevent loss of TX#1 upon fault on 230kV line 2034 in stuck breaker scenario | Dominion |  |  |  | 6/21/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.62 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n6497.2 | Replace 6, 3000A Rockport CTs on the Rockport - Jefferson 765 kV line | AEP |  |  |  | 12/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 4.8 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n6526.2 | Sag Study will be required on ACSR ~ 954 ~ 45/7, 18.3 miles line between South Berwick and Galion .The cost is expected to be 73,200.New Ratings after sag study : S/N: 1409 MVA S/E: 1887 MVA.Rebuild/Reconductor, cost : $ 36.6 million | AEP | [5 empty] | Cancelled | 10/3/2023 | 10/3/2023 | 0.732 |  | 2/26/2025 | Cancelled
PJM SOUTH | n6618.1 | Split the 115 kV Bus at Hathaway into two separate buses with a 115 kV Line on each bus and close the tie switch between Line 55 & 80. Line #1001 is opened at Battleboro thus making Line #1001 radial from Chestnut Substation | Dominion |  |  |  | 12/31/2022 | 12/31/2022 | Cancelled | 11/1/2022 | 11/1/2022 | 0.020749 |  | 2/26/2025 | Cancelled
PJM WEST | n6634.1 | New 138 kV Switching Station - Construct a new three (3) circuit breaker 138 kV switching station physically configured in a breaker and half bus arrangement but operated as a ring-bus for AC2-061 interconnection | AEP |  |  |  |  | 7/1/2020 | Cancelled | 10/8/2024 | 10/8/2024 | 6 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n6634.2 | Install 138 kV Revenue Metering at Hillsboro-Clinton County 138 kV | AEP |  |  |  |  | 7/1/2020 | Cancelled | 10/8/2024 | 10/8/2024 | 0.25 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n6634.3 | Install Hillsboro-Clinton County 138 kV transmission line cut In | AEP |  |  |  |  | 7/1/2020 | Cancelled | 10/8/2024 | 10/8/2024 | 1 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n6634.4 | Upgrade line protection and controls at the Hillsboro 138 kV substation to coordinate with the new AC2-061 138 kV switching station. | AEP |  |  |  |  | 7/1/2020 | Cancelled | 10/8/2024 | 10/8/2024 | 0.25 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n6741.2 | 1) A sag study will be required on the 9.5 miles of ACSR ~ 954 ~ 45/7 ~ Bundled - Conductor Section 1 to mitigate the overload. Depending on the sag study results, the cost for this upgrade is expected to be between $38,000 (no remediation required, just sag study) and $19 million (complete line reconductor/rebuild). New rating after sag study: S/N:1409 S/E: 1887 . Time Estimate: a) Sag Study: 6-12 months. b) Rebuild: The standard time required for construction differs from state to state. | AEP | [5 empty] | Cancelled | 10/8/2025 | 10/8/2025 | 0.038 |  | 11/18/2025 | Cancelled
PJM WEST | n6769.1 | Upgrade/Replace 3-345kV 1600A switches at Beatty station | AEP | [5 empty] | Cancelled | 10/8/2024 | 10/8/2024 | 1.5 |  | 2/26/2025 | Cancelled
PJM MA | n7127.4 | Replace line trap at East Towanda 230 kV substation | PENELEC |  |  |  | 5/31/2022 | 5/31/2022 | Cancelled | 10/8/2024 | 10/8/2024 | 0.225 |  | 2/26/2025 | Scope/Cost Change
PJM MA | n7127.5 | Adjust/replace metering and line relaying at East Towanda 230 kV substation | PENELEC |  |  |  | 5/31/2022 | 5/31/2022 | Cancelled | 10/8/2024 | 10/8/2024 | 0.5 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n9322.0 | Replace (4) disconnect switches, (4) breaker leads, and (1) meter, and reconductor (2) transmission line drops on Morocco 345 kV line terminal at Allen Junction | ATSI | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9204.0 | Wreck and rebuild 1.63 miles of line 238 between AE2-033 tap and Sapony with (2) 768.2 ACSS/TW (20/7) "MAUMEE" @ 250C | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9201.0 | Replace Wave Trap at Carson 230 kV (Carson - Sapony). | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9200.0 | Wreck and rebuild 10.62 miles of line 238 between Sapony and Carson with (2) 768.2 ACSS/TW (20/7) "MAUMEE" @ 250C | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | n9269.0 | Reconductor AD1-100 Tap - Wilton 345 kV line | ComEd | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | n7925.1 | Reconductor/rebuild 0.82 miles of ACAR ~ 1024.5 ~ 30/7 ~ RAIL1 conductor section 5 | AEP |  |  |  | 12/31/2023 |  | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n6872 | Wreck and rebuild 15.09 miles of line 238 between Clubhouse and AE2-033 tap with (2) 768.2 ACSS/TW (20/7) at 250C. | Dominion |  |  |  | 6/1/2023 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | s4057.1 | Construct a 138 kV tap near structure #111 on the Cecil - Weirton - Windsor (Buffalo Junction) 138 kV Line. Install two 1200 A switches at the tap location. Construct 1 to 2 spans of transmission line from the new tap to the customer site. Install one 1200 A switch at the tap point. Install 138 kV revenue metering and adjust relay settings at Cecil, Weirton, and Windsor substations. | APS |  |  | Customer Service |  |  | EP | 6/17/2026 | 6/17/2026 |  |  |  | New Upgrade
PJM WEST | s3876.1 | Tap the Kiski Valley-North Washington 138 kV Line Install three SCADA controlled switches at tap location Construct 1-2 spans of transmission line conductor from tap location to customer POI Install 138 kV revenue metering within customer substation Adjust relay settings at Kiski Valley and North Washington substations Transmission Line Ratings: Kiski Valley - Customer Tap 138 kV Line After Proposed Solution: 153 / 1 53 / 153 / 153 MVA (SN/SE/WN/WE) Customer Tap - North Washington 138 kV Line After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Customer Service^Other |  |  | EP | 10/17/2025 | 10/17/2025 |  |  |  | New Upgrade
PJM MA | s4059.1 | Install new 115/13 kV transformer 110-3 | BGE |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 0 |  |  | New Upgrade
PJM MA | s3912.1 | Tap existing Lackawanna - Brookside 69kV line. Extend circuit as double circuit transmission line with existing Lackawanna - Greenfield, approximately 15.6 miles to Tinker 69-12kV Substation transformer bay 2. Utilize 556 ACSR | PPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 4/14/2026 | 4/14/2026 | 34.6 |  |  | New Upgrade
PJM WEST | s3936.1 | At Smithton Substation: - Eliminate the normally open bus tie configuration by installing two 138 kV line breakers and a bus tie breaker. - Re-terminate the connection from Smithton Substation to the Charleroi - Mitchell - Yukon (Shepler Hill Jct) 138 kV Line. - Remove the connection from Smithton Substation to the Smithton Tap that is currently connected to the Allenport - Iron Bridge - Yukon 138 kV Line. Transmission Line Ratings: Charleroi - Belmon 138 kV Line: Before Proposed Solution: 274 / 287 / 287 / 287 MVA (SN/SE/WN/WE) After Proposed Solution: 297 / 365 / 345 / 441 MVA (SN/SE/WN/WE) Belmon - Shepler Hill Jct 138 kV Line: Before Proposed Solution: 269 / 335 / 326 / 380 MVA (SN/SE/WN/WE) After Proposed Solution: 297 / 358 / 345 / 410 MVA (SN/SE/WN/WE) Shepler Hill Jct - Smithton 138 kV Line: Before Proposed Solution: 309 / 376 / 349 / 445 MVA (SN/SE/WN/WE) After Proposed Solution: 309 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Smithton - Yukon 138 kV Line: Before Proposed Solution: 294 / 350 / 349 / 401 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Shepler Hill Jct - Mitchell 138 kV Line: Before Proposed Solution: 292 / 292 / 292 / 292 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/17/2026 | 7/17/2026 | 0 |  |  | New Upgrade
PJM MA | s3951.1 | Replace Granite 230/115 kV transformer 230-1 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 13.1 |  |  | New Upgrade
PJM MA | s3950.1 | Rebuild 2.67 miles of the existing lattice towers and conductors on the 110529/110530 line between Granite and Chestnut Hill stations. | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 13.4 |  |  | New Upgrade
PJM MA | s3949.1 | Rebuild existing 4.7 mile Perryman to Edgewood 115 kV line 110620 and 110621 circuits. | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 36.27 |  |  | New Upgrade
PJM MA | s3899.1 | Construct a new 66/13kV single transformer substation. Load will be permanently transferred onto the new substation that will alleviate the loading concerns at Swoyersville Substation. Additional feeds from this new substation will address distribution reliability issues an several worst performing feeders. | UGI |  |  | Customer Service^Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | EP | 3/18/2026 | 3/18/2026 | 6.5 |  |  | New Upgrade
PJM MA | s3809.1 | 69kV Circuit - Gloucester to Lawnside | PSEG |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 1/15/2026 | 1/15/2026 | 42.8 |  |  | New Upgrade
PJM MA | s3808.1 | 69kV transmission line between Sand Hills to Customer. | PSEG |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 1/15/2026 | 1/15/2026 | 25.1 |  |  | New Upgrade
PJM MA | s3735.1 | Install two (2) 230-13kV transformers and associated equipment. | PSEG |  |  | Customer Service^Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 7/8/2025 | 7/8/2025 | 27.2 |  |  | New Upgrade
PJM WEST | s4064.4 | Install (1) 80 kA, 4000 A 138 kV circuit breaker to connect Badger – Fiesta line. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 1.519 |  |  | New Upgrade
PJM WEST | s4064.3 | Install (1) 80 kA, 4000 A 138 kV circuit breaker to connect Badger – Fiesta line. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 1.475 |  |  | New Upgrade
PJM WEST | s4064.2 | Construct a greenfield ~1.5 mile of single circuit line, utilizing 2-bundled ACSR Falcon 1590 (54/19) conductor, connecting Badger and Fiesta stations. This scope addresses the expected overload on the existing 450MVA-345/138 kV transformer at Jug St station under a N-1-1 contingency scenario with the increased load at Horizon station. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 11.39 |  |  | New Upgrade
PJM WEST | s4064.1 | Due to the increased additional distribution capacity request, AEP Ohio would be adding three more distribution banks to the proposed (submitted under PJM s3442.4) Horizon station by adding (4) 80 kA, 4000 A 138 kV circuit breakers. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 3.67 |  |  | New Upgrade
PJM SOUTH | n9432.0 | Expand the existing Moyock 230 kV substation by adding one new circuit breaker. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.663 |  |  | New Upgrade
PJM MA | s4044.1 | Upgrade 230 kV Burches Hill – Palmer Corner relays and associated relay settings. The relay replacement will increase the ratings on Burches - Palmer Corner to 1089/1198/1145/1251/1134/1242 MVA (SN/SE/WN/WE/LLN/LLE). | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/7/2026 | 4/7/2026 | 0.5 |  |  | New Upgrade
PJM MA | s4035.2 | Phase 2: Build a new 69kV 6-position ring bus substation, bisecting the existing 69kV Beckett – Churchtown line. Install new radial feed to the customer site from the new substation and two positions for new 69/12kV distribution transformers. | ACE |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 16 |  |  | New Upgrade
PJM MA | s4035.1 | Phase 1: Install a temporary radial 69kV feed to the customer location by tapping into the existing 69kV Beckett - Churchtown line. | ACE |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 0 |  |  | New Upgrade
PJM MA | s3788.1 | Upgrade bus conductor at Keeney 138 kV from 954 ACSR to 2-954 ACSR. Ratings on the Keeney 138 kV to Keeney EHV line will be increased to 392/478/540/449/478/550 MVA (SN/SE/SLD/WN/WE/WLD) | DPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 10/16/2025 | 10/16/2025 | 0.15 |  |  | New Upgrade
PJM MA | s3785.1 | Install (2) new 2000A 138 kV breakers on the Red Lion 138kV ring bus to create a position for the new transformer | DPL |  |  | Customer Service |  |  | EP | 9/18/2025 | 9/18/2025 | 4.9 |  |  | New Upgrade
PJM WEST | s3602.2 | OVEC will construct their section of the new substation with six 4000 A, 63 kA, 345 kV circuit breakers and a control building to house OVEC’s communications, protection and controls equipment. The OVEC Pierce-Kyger Creek circuit is 6-wired on double circuit structures that run near the new substation. OVEC will perform work at Pierce to split the 6-wired circuit into two independent circuits, each connecting into an independent position. Near Turner, OVEC will intercept and extend the two circuits approximately 1.2 miles to the new substation using bundled 954 ACSR. These circuits will connect into two positions and exit from the remaining two positions in OVEC’s section of the new substation, creating four circuits. Near AEP Don Marquis OVEC will split the 6-wired Pierce-Kyger Creek circuit, terminating one side at Don Marquis. The remaining section of this circuit to Kyger Creek will be retired. | DEOK | X |  | Customer Service |  |  | Cancelled | 1/7/2025 | 1/7/2025 | 56.5 |  |  | Cancelled
PJM WEST | s3602.1 | The customer will initially take 10 MW of distribution service. The potential transmission solution requires work to be performed by three utilities, Duke Energy Ohio & Kentucky (Duke), Ohio Valley Electric Corporation (OVEC) and American Electric Power (AEP). Build a new 345kV breaker-and-a-half substation named Turner on the customer’s site. Turner will be a shared asset between Duke and OVEC. The Duke section will consist of twelve circuit breakers, with two of the breakers being used as bus ties to the OVEC section. Four positions in the Duke section will be used to connect four radial feeds to the customer. Two positions will be used to loop Duke’s Hillcrest-Stuart 345 kV circuit in and out of the station. The OVEC section will have six breakers. Two positions will terminate two independent feeders from OVEC Pierce substation. The two remaining positions will be used to terminate a circuit to OVEC Kyger Creek and a circuit to AEP Don Marquis. AEP will install a new circuit breaker at Don Marquis to create a new position for the circuit. Duke will construct its section of the new substation with ten 3000 A, 50 kA, 345 kV circuit breakers to be used for the circuit positions, two 4000 A, 50 kA, 345 kV circuit breakers to be used for bus ties, and a control building to house Duke Energy’s communications, protection and controls equipment. Duke will intercept the nearby Hillcrest-Stuart circuit and extend it approximately 0.6 miles to the new substation using bundled 1024 ACAR conductor. | DEOK | X |  | Customer Service |  |  | Cancelled | 1/7/2025 | 1/7/2025 | 63 |  |  | Cancelled
PJM WEST | n9660.0 | Perform relay upgrades at TSS 56 North Aurora substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.26804 |  |  | New Upgrade
PJM WEST | n9659.0 | Perform relay upgrades at TSS 189 Crego Rd substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.26804 |  |  | New Upgrade
PJM MA | n9624.0 | Revise relay settings at Bear Rock. | MAIT | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.050758 |  |  | New Upgrade
PJM MA | n9623.0 | Revise relay settings at Johnstown. | MAIT | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.051147 |  |  | New Upgrade
PJM MA | n9622.0 | Revise relay settings Fiddlers Green. | MAIT | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.051147 |  |  | New Upgrade
PJM WEST | n9579.0 | Remote Relay at ESSB-427 Titan Tire | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.14341 |  |  | New Upgrade
PJM WEST | n9567.0 | Proposed AF2-359 345 kV Station: Review and revise the protective relay settings at the AF2-359 proposed 345 kV Station to account for the additional generation of AG1-436. o Settings will need to be revised for each generation project (AG1-436 & AG1-447) unless they share an in-service date. | AEP | [5 empty] | EP | 11/3/2026 | 10/30/2028 | 0.060764 |  |  | New Upgrade
PJM WEST | n9566.0 | Proposed AF2-359 345 kV Station: Review and revise the protective relay settings at the AF2-359 proposed 345 kV Station to account for the additional generation of AG1-447. o Settings will need to be revised for each generation project (AG1-436 & AG1-447) unless they share an in-service date. | AEP | [5 empty] | EP | 11/3/2026 | 10/30/2028 | 0.060764 |  |  | New Upgrade
PJM WEST | n9565.0 | Upgrade TSS 177 Burnham substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 7.072 |  |  | New Upgrade
PJM WEST | n9547.0 | Construct a new 138 kV breaker-and-a-half interconnection substation, TSS 978 MIller Road, tapping the L.14609 138 kV line. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 26.8763 |  |  | New Upgrade
PJM WEST | n9546.0 | Cut L14609 138kV line to loop into the new TSS 978 Miller Road interconnection substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 5.8838 |  |  | New Upgrade
PJM WEST | n9545.0 | Perform relay upgrades at TDC 527 Plano West Substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.94224 |  |  | New Upgrade
PJM WEST | n9544.0 | Perform relay upgrades at TSS 167 Plano Substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.68911 |  |  | New Upgrade
PJM WEST | n9543.0 | Perform relay upgrades at TSS 146 Sandwich Substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.17038 |  |  | New Upgrade
PJM WEST | n7165.1 | Replace T-line drops at All Dam 6 | APS |  |  |  | 6/1/2028 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n9542.0 | Build new fiber path (estimated ~6.5 miles) from TSS 978 Miller Road Substation to TDC 527 Plano West and new fiber (estimated ~ 5.5 miles) from TSS 978 Miller Road Substation to Sta 1 LaSalle Substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 6.7569 |  |  | New Upgrade
PJM WEST | n9456.0 | Cut existing L11106 138 kV transmission line between existing structures 245 and 246 to loop into the new TSS 956 Rimsnider Road Substation and break into new L95602. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.0323 |  |  | New Upgrade
PJM WEST | n9455.0 | Perform relay and communication upgrades at TSS 113 Waterman 138 kV | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.40568 |  |  | New Upgrade
PJM WEST | n9454.0 | Perform relay and communication upgrades at TDC 569 Sugar Grove 138 kV | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.40235 |  |  | New Upgrade
PJM WEST | n6260.1 | Replace the Pontiac 345 kV breaker BT 4-5 to upgrade the Pontiac - Loretto 345 kV line. | ComEd |  |  |  | 12/31/2019 |  | EP | [5 empty] | New Upgrade
PJM WEST | n9453.0 | Extend distribution power to tie in the auxiliary power for the new interconnection substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.5625 |  |  | New Upgrade
PJM WEST | n7166.1 | Replace 4/0 CU line exit at All Dam 6 Tap. | APS |  |  |  | 6/1/2028 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n9452.0 | Fiber Installation from TSS 956 Rimsnider Rd to TSS 113 Waterman | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.2774 |  |  | New Upgrade
PJM WEST | n7166.2 | Reconductor 7.6 miles of 4/0 CU from All Dam 6 Tap to structure 84 (66 spans). | APS |  |  |  | 6/1/2028 |  | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9429.0 | Re-arrange line #35 to loop into and out of the new AE2-283 single breaker 69 kV tap | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.5215 |  |  | New Upgrade
PJM SOUTH | n9419.0 | Tap 115k Line #33 between proposed structure 33/945 and Dryburg Substation for new interconnection substation. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.9572 |  |  | New Upgrade
PJM SOUTH | n9417.0 | Build a new 230 kV three-breaker ring switching station located along VEPCO's new 230 kV line from Farmville Substation to Finneywood Substation. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 12.9251 |  |  | New Upgrade
PJM SOUTH | n9416.0 | Re-arrange line #TBD to loop into and out of the new three-breaker AG1-285 230 kV switching station. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 6.0291 |  |  | New Upgrade
PJM SOUTH | n9415.0 | Re-arrange line #1007 to loop into and out of the new three-breaker AF1-294/AF2-115/AG1-021 115 kV switching station (including fiber) | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.7816 |  |  | New Upgrade
PJM SOUTH | n9414.0 | Remote Relay at Dennisville Road Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.14416 |  |  | New Upgrade
PJM SOUTH | n9413.0 | Remote Relay at Lone Pine Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.18642 |  |  | New Upgrade
PJM SOUTH | n9411.0 | Build a new 500 kV three-breaker ring switching station located along Dominion’s existing 500 kV, 556 line from Clover Substation to Finneywood Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 26.7413 |  |  | New Upgrade
PJM SOUTH | n9410.0 | Re-arrange line #556 to loop into and out of the new three-breaker AF2-042 500 kV switching station | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 9.2364 |  |  | New Upgrade
PJM SOUTH | n9409.0 | Remote Relay work at Clover Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.17809 |  |  | New Upgrade
PJM SOUTH | n9408.0 | Remote Relay work at Finneywood Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.13584 |  |  | New Upgrade
PJM WEST | n9363.0 | Construct substation upgrades at TSS199 Kensington Road including relocating/upgrading L19901 and L19902 lines | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 21.9994 |  |  | Cancelled
PJM WEST | n9362.0 | Relocate/upgrade L19906 138 kV line with approximately 0.15 new circuit miles to TSS 199 Kensington Road. | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 3.9082 |  |  | Cancelled
PJM WEST | n9361.0 | Relocate/upgrade L19907 138 kV line with approximately 0.04 new circuit miles to TSS 199 Kensington Road. | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 1.8945 |  |  | Cancelled
PJM WEST | n9359.0 | Perform Relaying Upgrades at TSS70 Bradley | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 0.26349 |  |  | Cancelled
PJM WEST | n9358.0 | Perform Relaying Upgrades at TSS86 Davis Creek | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 0.26349 |  |  | Cancelled
PJM WEST | n9357.0 | Perform Relaying Upgrades at STA4 Quad Cities | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 0.26349 |  |  | Cancelled
PJM WEST | n9356.0 | Relocate fiber optic cables for L19901 to TSS938 Pilot Hill and L19902 to TSS949 Kelly Creek | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 0.54903 |  |  | Cancelled
PJM SOUTH | n9355.0 | Remote Relay at Substation Altavista | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.1761 |  |  | New Upgrade
PJM SOUTH | n9354.0 | Remote Relay at Substation Otter River | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.12885 |  |  | New Upgrade
PJM SOUTH | n9353.0 | Remote Relay at Substation Perth | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.18136 |  |  | New Upgrade
PJM SOUTH | n9352.0 | Re-arrange line #31 to loop into and out of the new three-breaker AE2-291 115 kV switching station | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.6184 |  |  | New Upgrade
PJM SOUTH | n9351.0 | Build a new 115 kV three-breaker ring switching station located along VEPCO’s existing 115 kV, 31 line from Altavista Substation to Perth Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 11.568 |  |  | New Upgrade
PJM WEST | n9348.0 | Proposed AF1-119 345 kV Station: Review and revise the protective relay settings to account for the additional generation of AG1-433. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM SOUTH | n8316 | AG1-153 Breaker Addition | Dominion |  |  |  | 12/1/2023 |  | EP | 11/3/2026 | 11/3/2026 | 3.393 |  |  | New Upgrade
PJM WEST | n5908 | Transmission Line (L91907) Sag Mitigation | ComEd |  |  |  | 11/15/2019 | 12/31/2025 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | s4042.1 | Replacement of relays at Crescentville and Waneeta, CTs and PTs at Crescentville, and removal of wave trap at Crescentville. Thermal ratings on the 130-03 Waneeta - Crescentville line will increase to 272/344/412 MVA (SN/SE/SLD) and 282/351/441 MVA (WN/WE/WLD). | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/18/2026 | 3/18/2026 | 0.675 |  |  | New Upgrade
PJM MA | s4041.1 | Replacement of the 230/138kV Master #8 transformer with a new transformer and replacement of secondary wiring. The thermal rating of the transformer will increase to 402/461/540/452/546/604 (SN/SE/SLD/WN/WE/WLD) | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 3/18/2026 | 3/18/2026 | 3.5 |  |  | New Upgrade
PJM MA | s4040.1 | Rebuild the 230 kV 220-10 Buxmount – Whitpain line with new galvanized steel monopoles, 959.6 kcmil ACSS/TW Suwannee conductor, and new OPGW shield wire.? Line ratings in MVA increase to 1111/1365/1373/1545 (SN/SE/WN/WE) | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/10/2026 | 3/10/2026 | 54 |  |  | New Upgrade
PJM MA | s4039.1 | Rebuild the 230 kV 220-14 Plymouth Meeting – Whitpain line with new steel double-circuited monopoles, bundled 959.6 kcmil ACSS/TW Suwannee conductor, and new OPGW shield wire.? Line ratings in MVA increase to 1523/1767/1597/1843 (SN/SE/WN/WE). | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/10/2026 | 3/10/2026 | 44 |  |  | New Upgrade
PJM MA | s4038.1 | Rebuild the 230 kV 220-13 Plymouth Meeting – Whitpain line with new steel double-circuited monopoles, bundled 959.6 kcmil ACSS/TW Suwannee conductor, and new OPGW shield wire.? Line ratings in MVA increase to 1523/1767/1597/1843 (SN/SE/WN/WE). | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/10/2026 | 3/10/2026 | 44 |  |  | New Upgrade
PJM MA | s4037.1 | Upgraded 69 kV Cheswold – Kent Relays, and associated relay settings. The Relay replacement will result in increasing the associated facility ratings on Cheswold - Kent facility. The Relay replacement will result in increasing the associated facility ratings to 137/174/200 MVA (SN/SE/SLD) and 158/195/224 MVA (WN/WE/WLD) | DPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/14/2026 | 5/14/2026 | 0.625 |  |  | New Upgrade
PJM MA | s4036.1 | Install new 2000A 69kV breaker on the Silverside 69kV ring bus, as well as associated disconnect switches, relays, and metering equipment. Relocate Carrcroft-Silverside 69kV line terminal to newly created position and reposition T2 distribution transformer between this line and the Edgemoor-Silverside 69kV line terminal. Remove redundant 69kV breaker located at Edgemoor-Silverside 69kV line terminal, currently shared with T2 distribution transformer. | DPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 2/12/2026 | 2/12/2026 | 1.93 |  |  | New Upgrade
PJM SOUTH | n9681.0 | Reconductor 1.04 mile segment of Carson - Chaparall 230 kV Line 249 between structures 86 and 93 with (2) 768.2 ACSS Maumee at 250 degree C. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.042 |  |  | New Upgrade
PJM SOUTH | n9630.0 | Construct a new 230 kV line from the AG1-285 substation to the Finneywood 230 kV Substation. Expand AG1-285 substation and add two (2) new 230/115 kV transformers. | Dominion |  |  |  | 12/31/2029 |  | EP | 11/3/2026 | 11/3/2026 | 71.6978 |  |  | New Upgrade
PJM SOUTH | n9207.0 | Replace 6ELMONT 230 kV to 8ELMONT 500 kV circuit 1 with larger transformer (3-480 MVA single phase transformer). | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 38.2545 |  |  | New Upgrade
PJM WEST | s4026.4 | New 69 kV distribution station built at Thunder Ridge site. This distribution station is being built to retire the existing Jenny Wiley distribution station and its associated tap line which are reaching end-of-life | EKPC |  |  | Operational Flexibility and Efficiency |  |  | EP | 11/14/2025 | 11/14/2025 | 0 |  |  | New Upgrade
PJM WEST | s4026.3 | New ~5 mile 795 ACSR 69 kV tie-line from EKPC Thunder Ridge 69 kV-AEP Dewey Dam 69 kV | EKPC |  |  | Operational Flexibility and Efficiency |  |  | EP | 11/14/2025 | 11/14/2025 | 5.34 |  |  | New Upgrade
PJM WEST | s4026.2 | To accommodate new interconnection with AEP at Dewey Dam 69 kV station, AEP proposed the following solution Install one 69 kV circuit breaker, associated metering, and line exit at Dewey Station Install one 69 kV span from Dewey station to delineation pole Expand the existing control house Expand the 69 kV bus and install one new 69 kV box bay | EKPC |  |  | Operational Flexibility and Efficiency |  |  | EP | 11/14/2025 | 11/14/2025 | 2.5 |  |  | New Upgrade
PJM WEST | n8029.1 | Attachment facility line and Revenue Metering Installation | AEP |  |  |  | 12/31/2022 |  | Cancelled |  |  | 1.082 |  |  | Cancelled
PJM WEST | n8029.2 | 3 breaker 345 kV Switching station | AEP |  |  |  | 12/31/2022 |  | Cancelled |  |  | 17.44 |  |  | Cancelled
PJM WEST | s4056.1 | -Install two main-line switches and one radial tap switch on the Clark - North Hampton 69 kV Line -Construct approximately 200 feet of transmission line to the customer substation -Adjust relay settings at North Hampton and Clark substations -Install revenue metering | ATSI |  |  | Customer Service |  |  | EP | 12/12/2025 | 12/12/2025 | 2.25 |  |  | New Upgrade
PJM WEST | n8029.3 | Construct a new loop-in tap line | AEP |  |  |  | 12/31/2022 |  | Cancelled |  |  | 1.21 |  |  | Cancelled
PJM WEST | n8029.4 | Modify relay settings | AEP |  |  |  | 12/31/2021 |  | Cancelled |  |  | 0.045 |  |  | Cancelled
PJM WEST | s4055.1 | On the London - Tangy 138 kV Line: - Install two main-line switches and one tap switch - Construct approximately 3.3 miles of 138 kV transmission line - Adjust relay settings at London and Tangy substations - Install revenue metering | ATSI |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 1.41 |  |  | New Upgrade
PJM WEST | s4054.1 | 138 kV Transmission Line Tap - Install two main-line switches and one tap switch - Construct approximately 1.3 miles of 138 kV transmission line - Adjust relay settings at Carlisle and Johnson substations - Install revenue metering | ATSI |  |  | Customer Service |  |  | EP | 10/17/2025 | 10/17/2025 | 2.08 |  |  | New Upgrade
PJM WEST | s4052.1 | Install a temporary tap on the Cloverdale - Torrey 138 kV Line and the Canton Central - Cloverdale 138 kV Line and construct two line extensions of 0.2 miles each for two new delivery points to the customer. Customer to pay full cost Transmission Line Ratings: Cloverdale - Torrey 138 kV Line: - Before Proposed Solution: 200 / 242 / 226 / 286 MVA (SN/SE/WN/WE) - After Proposed Solution: 200 / 242 / 226 / 286 MVA (SN/SE/WN/WE) Canton Central - Cloverdale 138 kV Line: - Before Proposed Solution: 161 / 194 / 182 / 230 MVA(SN/SE/WN/WE) - After Proposed Solution: 161 / 194 / 182 / 230 MVA(SN/SE/WN/WE) | ATSI |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 0 |  |  | New Upgrade
PJM WEST | s4028.1 | Due to new delivery point of Logistics Dr #2, a new 69-26.4 kV 18/24/30 MVA Logistics Dr #2 distribution station will be built | EKPC |  |  | Customer Service |  |  | EP | 6/13/2025 | 6/13/2025 | 0 |  |  | New Upgrade
PJM SOUTH | s3882.5 | Split the 230kV bus at Possum Point to reduce short circuit issues. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3882.4 | Upgrade Ladysmith 40kA breakers to 63kA breakers to resolve short circuit issues. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3882.3 | upgrade 40ka breakers to 63ka | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3882.2 | Construct new Ruther Glen 230kV substation with 6 breaker ring bus configuration. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 15 |  |  | New Upgrade
PJM SOUTH | s3882.1 | Cut existing 230kV Line 256 (Ladysmith CT to Four Rivers) and extend double circuit 230kV lines approximately three miles to proposed Ruther Glen substation. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 40 |  |  | New Upgrade
PJM SOUTH | s3881.5 | Split the 230kV bus at Possum Point to resolve over duty breakers | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3881.4 | Upgrade Ladysmith 40kA breakers to 63kA | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3881.3 | Upgrade Fredericksburg 40kA breakers to 63kA | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3881.2 | Cut existing 230kV Line 256 (Ladysmith CT to Four Rivers) and extend double circuit 230kV transmission lines for approximately two miles to proposed Carmel Church substation. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 25 |  |  | New Upgrade
PJM SOUTH | s3881.1 | Construct new Carmel Church 230kV substation with 4 breaker ring bus configuration. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 15 |  |  | New Upgrade
PJM WEST | s3835.1 | Rebuild the Renaker-3M-Cynthiana Junction 69kV line sections | EKPC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/11/2025 | 4/11/2025 | 8.9 |  |  | New Upgrade
PJM SOUTH | s3732.7 | Convert Possum Point 230kV yard to GIS rated at 80kA | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3732.6 | Convert Ladysmith breakers from 40 to 63kA | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3732.5 | convert Fredericksburg breakers from 40 to 63kA | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3732.4 | Proposed Solution - Phase1 (01/2028): Rebuild approximately 6.5 miles of the existing 230kV Line #2090 between Summit DP and Fredericksburg Sub with double-circuit structures using a higher capacity conductor and associated substation equipment to achieve a minimum normal summer rating of 1573 MVA. Reconductor the first circuit of the Line #2089 from Ladysmith to Ladysmith CT for approximately 4 miles to achieve a minimum normal summer rating of 1573 MVA. Reconductor the second circuit of the Line #2089 from Ladysmith to Structure #2089/19 for approximately 3.3 miles to achieve a minimum normal summer rating of 1573 MVA. The rest of the Line #2089 on one side of the structures remains idle from Structure #2089/19 to Ladysmith CT Station. Construct a new 230kV Line from Structure #2089/19 to Structure #2090/106 for approx. 4.5 miles using double-circuit structures.Install the second circuit between existing Structure #2090/107, New Post Sub, Lee's Hill Sub, and Fredericksburg Sub by utilizing the vacant arms positions on the double-circuit structures in the corridor. The termination points of the new line will be Ladysmith, New Post, Lee's Hill, and Allman. Install two 500kV, 150 MVAr Capacitor Banks At Ladysmith Sub. Proposed Solution - Phase2 (07/2029): Expand Kraken 500kV Switching Station by cutting the existing 230kV Lines #2090 and #256, and future 230kV Line from Ladysmith to Allman constructed in Phase1. Rebuild Line #256 from St. Johns to Four Rivers for approx. 14.9 miles using double circuit monopoles. One circuit will be installed initially. Rebuild Line #2032 from Four Rivers to Elmont for approx. 9 miles using double circuit monopoles. One circuit will be installed initially. Wreck the 115kV Lines #47 (Fredericksburg-Four Rivers), #1008 (Pinewood-Four Rivers), #73 (Four Rivers-Elmont), 1013 (Pinewood-N. Doswell) Construct a new double circuit 230kV from Kraken to Allman.Construct a new 230kV circuit from Kraken to Elmont for approx. 31mi using double circuit monopoles. One circuit will be installed initially.Pinewood station should be converted to 230kV four-breaker ring station. Cut the Converted 230kV line near St. Johns and extend a double-circuit 230kV to Ruther Glen Sub. Necessary changes to the customer delivery points will be considered. | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3732.3 | Proposed Solution - Phase1 (01/2028): Rebuild approximately 6.5 miles of the existing 230kV Line #2090 between Summit DP and Fredericksburg Sub with double-circuit structures using a higher capacity conductor and associated substation equipment to achieve a minimum normal summer rating of 1573 MVA. Reconductor the first circuit of the Line #2089 from Ladysmith to Ladysmith CT for approximately 4 miles to achieve a minimum normal summer rating of 1573 MVA. Reconductor the second circuit of the Line #2089 from Ladysmith to Structure #2089/19 for approximately 3.3 miles to achieve a minimum normal summer rating of 1573 MVA. The rest of the Line #2089 on one side of the structures remains idle from Structure #2089/19 to Ladysmith CT Station. Construct a new 230kV Line from Structure #2089/19 to Structure #2090/106 for approx. 4.5 miles using double-circuit structures.Install the second circuit between existing Structure #2090/107, New Post Sub, Lee's Hill Sub, and Fredericksburg Sub by utilizing the vacant arms positions on the double-circuit structures in the corridor. The termination points of the new line will be Ladysmith, New Post, Lee's Hill, and Allman. Install two 500kV, 150 MVAr Capacitor Banks At Ladysmith Sub. Proposed Solution - Phase2 (07/2029): Expand Kraken 500kV Switching Station by cutting the existing 230kV Lines #2090 and #256, and future 230kV Line from Ladysmith to Allman constructed in Phase1. Rebuild Line #256 from St. Johns to Four Rivers for approx. 14.9 miles using double circuit monopoles. One circuit will be installed initially. Rebuild Line #2032 from Four Rivers to Elmont for approx. 9 miles using double circuit monopoles. One circuit will be installed initially. Wreck the 115kV Lines #47 (Fredericksburg-Four Rivers), #1008 (Pinewood-Four Rivers), #73 (Four Rivers-Elmont), 1013 (Pinewood-N. Doswell) Construct a new double circuit 230kV from Kraken to Allman.Construct a new 230kV circuit from Kraken to Elmont for approx. 31mi using double circuit monopoles. One circuit will be installed initially.Pinewood station should be converted to 230kV four-breaker ring station. Cut the Converted 230kV line near St. Johns and extend a double-circuit 230kV to Ruther Glen Sub. Necessary changes to the customer delivery points will be considered. | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3732.2 | Cut the existing 230kV Line from Fredericksburg to New Post and extend double-circuit 230kV lines for approx. 0.1 miles to Lee's Hill Switching Station. | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 6 |  |  | New Upgrade
PJM SOUTH | s3732.1 | Construct Lee's Hill 230 kV switching station with 4-breaker ring bus configuration. | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 10 |  |  | New Upgrade
PJM SOUTH | s3731.7 | convert Possum Point 230kV yard to GIS rated with 80kA breakers | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 0 |  |  | New Upgrade
PJM SOUTH | s3731.6 | uprate Ladysmith breakers from 40 to 63kA | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 0 |  |  | New Upgrade
PJM SOUTH | s3731.5 | Uprate Fredericksburg breakers from 40 to 63kA | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 0 |  |  | New Upgrade
PJM SOUTH | s3731.4 | Proposed Solution - Phase1 (01/2028): Rebuild approximately 6.5 miles of the existing 230kV Line #2090 between Summit DP and Fredericksburg Sub with double-circuit structures using a higher capacity conductor and associated substation equipment to achieve a minimum normal summer rating of 1573 MVA. Reconductor the first circuit of the Line #2089 from Ladysmith to Ladysmith CT for approximately 4 miles to achieve a minimum normal summer rating of 1573 MVA. Reconductor the second circuit of the Line #2089 from Ladysmith to Structure #2089/19 for approximately 3.3 miles to achieve a minimum normal summer rating of 1573 MVA. The rest of the Line #2089 on one side of the structures remains idle from Structure #2089/19 to Ladysmith CT Station. Construct a new 230kV Line from Structure #2089/19 to Structure #2090/106 for approx. 4.5 miles using double-circuit structures.Install the second circuit between existing Structure #2090/107, New Post Sub, Lee's Hill Sub, and Fredericksburg Sub by utilizing the vacant arms positions on the double-circuit structures in the corridor. The termination points of the new line will be Ladysmith, New Post, Lee's Hill, and Allman. Install two 500kV, 150 MVAr Capacitor Banks At Ladysmith Sub. Proposed Solution - Phase2 (07/2029): Expand Kraken 500kV Switching Station by cutting the existing 230kV Lines #2090 and #256, and future 230kV Line from Ladysmith to Allman constructed in Phase1. Rebuild Line #256 from St. Johns to Four Rivers for approx. 14.9 miles using double circuit monopoles. One circuit will be installed initially. Rebuild Line #2032 from Four Rivers to Elmont for approx. 9 miles using double circuit monopoles. One circuit will be installed initially. Wreck the 115kV Lines #47 (Fredericksburg-Four Rivers), #1008 (Pinewood-Four Rivers), #73 (Four Rivers-Elmont), 1013 (Pinewood-N. Doswell) Construct a new double circuit 230kV from Kraken to Allman.Construct a new 230kV circuit from Kraken to Elmont for approx. 31mi using double circuit monopoles. One circuit will be installed initially.Pinewood station should be converted to 230kV four-breaker ring station. Cut the Converted 230kV line near St. Johns and extend a double-circuit 230kV to Ruther Glen Sub. Necessary changes to the customer delivery points will be considered. | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 150 |  |  | New Upgrade
PJM SOUTH | s3731.3 | Proposed Solution - Phase1 (01/2028): Rebuild approximately 6.5 miles of the existing 230kV Line #2090 between Summit DP and Fredericksburg Sub with double-circuit structures using a higher capacity conductor and associated substation equipment to achieve a minimum normal summer rating of 1573 MVA. Reconductor the first circuit of the Line #2089 from Ladysmith to Ladysmith CT for approximately 4 miles to achieve a minimum normal summer rating of 1573 MVA. Reconductor the second circuit of the Line #2089 from Ladysmith to Structure #2089/19 for approximately 3.3 miles to achieve a minimum normal summer rating of 1573 MVA. The rest of the Line #2089 on one side of the structures remains idle from Structure #2089/19 to Ladysmith CT Station. Construct a new 230kV Line from Structure #2089/19 to Structure #2090/106 for approx. 4.5 miles using double-circuit structures.Install the second circuit between existing Structure #2090/107, New Post Sub, Lee's Hill Sub, and Fredericksburg Sub by utilizing the vacant arms positions on the double-circuit structures in the corridor. The termination points of the new line will be Ladysmith, New Post, Lee's Hill, and Allman. Install two 500kV, 150 MVAr Capacitor Banks At Ladysmith Sub. Proposed Solution - Phase2 (07/2029): Expand Kraken 500kV Switching Station by cutting the existing 230kV Lines #2090 and #256, and future 230kV Line from Ladysmith to Allman constructed in Phase1. Rebuild Line #256 from St. Johns to Four Rivers for approx. 14.9 miles using double circuit monopoles. One circuit will be installed initially. Rebuild Line #2032 from Four Rivers to Elmont for approx. 9 miles using double circuit monopoles. One circuit will be installed initially. Wreck the 115kV Lines #47 (Fredericksburg-Four Rivers), #1008 (Pinewood-Four Rivers), #73 (Four Rivers-Elmont), 1013 (Pinewood-N. Doswell) Construct a new double circuit 230kV from Kraken to Allman.Construct a new 230kV circuit from Kraken to Elmont for approx. 31mi using double circuit monopoles. One circuit will be installed initially.Pinewood station should be converted to 230kV four-breaker ring station. Cut the Converted 230kV line near St. Johns and extend a double-circuit 230kV to Ruther Glen Sub. Necessary changes to the customer delivery points will be considered. | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 300 |  |  | New Upgrade
PJM SOUTH | s3731.2 | Cut Line #2090 (Fredericksburg - Ladysmith CT) and extend double-circuit 230kV lines for approx. 0.3 miles to New Post Switching Station. | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 9 |  |  | New Upgrade
PJM SOUTH | s3731.1 | Construct New Post 230 kV switching station with 4-breaker ring bus configuration. | Dominion |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 18 |  |  | New Upgrade
PJM WEST | s3691.1 | Due to new delivery point of Clay Village #2, a new 69 kV box structure and associated bus/switches will be added to reconfigure existing distribution and protection scheme. New 69-13.2 12/16/20 Clay Village #2 distribution station will be built. | EKPC |  |  | Customer Service |  |  | Cancelled | 12/13/2024 | 12/13/2024 |  |  |  | Cancelled
PJM WEST | n9702.0 | Revise relay settings at Campbell substation as required. | ATSI | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | n9700.0 | Revise relay settings at Cedar substation as required. | ATSI | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | n9694.0 | Revise relay settings at Volant substation as required. | ATSI | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | s4063.1 | Replace the 450MVA-345/138 kV Transformer T5 at Jug St station with a 675MVA-345/138 kV transformer with associated protection equipment to address N-1-1 thermal violations associated with the customer load increase at Badger station. | AEP |  |  | Customer Service |  |  | EP | 6/13/2025 | 6/13/2025 | 0 |  |  | New Upgrade
PJM WEST | s4034.1 | Construct a new 138/25 kV distribution substation near the Spurlock - Renaker 138 kV line. Tap the new substation in and out and install a new three-way switch at the tap point. | EKPC |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 1.5 |  |  | New Upgrade
PJM WEST | s4027.2 | Construct a three breaker 69kV switching station to accommodate three 69kV exits and allow for the Renaker-Williamstown 69kV line to be operated normally closed and not create a three-terminal line. Cut-in the existing 69kV lines into the new Munk Jct 69kV switching station. | EKPC |  |  | Operational Flexibility and Efficiency |  |  | EP | 11/14/2025 | 11/14/2025 | 7.2 |  |  | New Upgrade
PJM WEST | s4027.1 | Rebuild a total of 18.46 miles of 69kV transmission line between Renaker and Williamstown. Replacing 16.94 miles of 1/0 conductor and 1.52 miles of 4/0 conductor with 556.5 ACSR conductor. | EKPC |  |  | Operational Flexibility and Efficiency |  |  | EP | 11/14/2025 | 11/14/2025 | 14.815 |  |  | New Upgrade
PJM WEST | s4026.1 | Build new 69 kV switching station called Thunder Ridge to split up existing Magoffin Co-Thelma 69 kV circuit and be able to connect the new AEP tie line to. | EKPC |  |  | Operational Flexibility and Efficiency |  |  | EP | 11/14/2025 | 11/14/2025 | 6.29 |  |  | New Upgrade
PJM SOUTH | s3996.4 | Rebuild 230 kV Line #2027: Midlothian-Bremo to current 230 kV standards to achieve a minimum normal summer rating of 1573 MVA. Upgrade substation equipment to 4000 A. Double-circuit 230 kV structures will be used. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 212 |  |  | New Upgrade
PJM SOUTH | s3996.3 | Replace Carson 500/230 kV TX #2 with new 1440 MVA TX and replace low-side equipment limiting TX rating. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 17.5 |  |  | New Upgrade
PJM SOUTH | s3996.2 | Cut and extend 230 kV Line #2003 (Chesterfield - Poe) approximately 1.0 miles in and out of James Hill substation on double-circuit structures. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 6 |  |  | New Upgrade
PJM SOUTH | s3996.1 | Construct James Hill 230 kV substation with a four-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 20 |  |  | New Upgrade
PJM MA | s4020.1 | Johnstown - Seward 230 kV Line Rebuild: Rebuild 6.7 miles of 230 kV transmission line on steel structures and install new conductor. Transmission Line Ratings: Before Proposed Solution: 546 / 666 / 619 / 790 MVA (SN/SE/WN/WE) After Proposed Solution: 627 / 775 / 729 / 939 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/4/2025 | 11/4/2025 | 30.01 |  |  | New Upgrade
PJM MA | s4019.1 | East Pike - Glory 115 kV Line Rebuild: Rebuild 13.04 miles on the East Pike - Glory 115 kV Line and install new conductor At East Pike Substation, adjust relay settings as necessary. At Glory Substation, adjust relay settings as necessary. Transmission Line Ratings: Before Proposed Solution: 137 / 177 / 188 / 245 MVA (SN/SE/WN/WE) After Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/16/2026 | 6/16/2026 | 47.73 |  |  | New Upgrade
PJM MA | s4018.1 | Forest - Glade 230 kV Line Rebuild approximately 34.1 miles of 230 kV line from Forest Substation to structure 288 Glade Substation Replace the 1033 ACSR bus conductor Transmission Line Ratings: Forest - Glade 230 kV Line Before Proposed Solution: 541 / 659 / 612 / 781 MVA (SN/SE/WN/WE) After Proposed Solution: 546 / 666 / 619 / 790 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/8/2025 | 10/8/2025 | 156.72 |  |  | New Upgrade
PJM MA | s4017.1 | Lincoln-Orrtanna 115 kV Customer Connection: Tap the Lincoln - Orrtanna 115 kV Line and install 2 network SCADA controlled switches and 1 radial SCADA controlled switch Construct 1-2 spans of transmission line conductor from tap location to new Customer substation Install 115 kV revenue metering Adjust relay settings at Lincoln Substation and Orrtanna Substation Transmission Line Ratings: Orrtanna - West Gettysburg 115 kV Line and Lincoln - West Gettysburg 115 kV Line Before Proposed Solution: 133 / 160 / 150 / 190 MVA (SN/SE/WN/WE) After Proposed Solution: 133 / 160 / 150 / 190 MVA (SN/SE/WN/WE) | ME |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 3.06 |  |  | New Upgrade
PJM WEST | n8089.1 | Expand Huntington Jct Switching Station into a 4 Breaker Ring Bus | AEP |  |  |  | 6/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 4.2344 |  | 2/26/2025 | Cancelled
PJM MA | s4016.1 | North Hanover 115 kV Breaker and a Half Substation: Convert the 115 kV yard at North Hanover Substation into an 11 breaker, breaker-and-a-half configuration. Revise relay settings at Gitts Run, Hunterstown, and Jackson substations. Modify the 115 kV N. Hanover 960 Line terminal at Hunterstown Substation for fiber installation. Transmission Line Ratings: Jackson - North Hanover 115 kV 968 Line: Before Proposed Solution: 133 / 160 / 150 / 190 MVA (SN/SE/WN/WE) After Proposed Solution: 133 / 160 / 150 / 190 MVA (SN/SE/WN/WE) Hunterstown - North Hanover 115 kV 960 Line: Before Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) After Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) Gitts Run - North Hanover No. 1 115 kV Line: Before Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) After Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) Gitts Run - North Hanover No. 2 115 kV Line: Before Proposed Solution: 221 / 263 / 263 / 301 MVA (SN/SE/WN/WE) After Proposed Solution: 221 / 263 / 263 / 301 MVA (SN/SE/WN/WE) | ME |  |  | Operational Flexibility and Efficiency |  |  | EP | 6/16/2026 | 6/16/2026 | 36.79 |  |  | New Upgrade
PJM WEST | n8089.2 | Sorenson - Delaware 138 kV Re-Route, Sorenson and Hummel Creek 138 kV line Re-Terminations | AEP |  |  |  | 6/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.3849 |  | 2/26/2025 | Cancelled
PJM WEST | n8089.3 | Install Transition Fiber Cable at Huntington Jct 138 kV substation | AEP |  |  |  | 6/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.1526 |  | 2/26/2025 | Cancelled
PJM MA | s4015.1 | Foxhill Substation 230 kV Ring Bus: Convert Foxhill Substation into a four-breaker 230 kV ring bus. At Shawnee Substation: Revise relay settings. At Monroe Substation: Revise relay settings. Transmission Line Ratings: Foxhill - Shawnee 230 kV Line: Before Proposed Solution: 494 / 630 / 545 / 685 MVA (SN/SE/WN/WE) After Proposed Solution: 494 / 630 / 545 / 685 MVA (SN/SE/WN/WE) Foxhill - Monroe 230 kV Line: Before Proposed Solution: 634 / 796 / 734 / 906 MVA (SN/SE/WN/WE) After Proposed Solution: 634 / 796 / 734 / 906 MVA (SN/SE/WN/WE) | ME |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/7/2026 | 7/7/2026 | 11.8 |  |  | New Upgrade
PJM WEST | n8089.4 | Sorenson and Hummel Creek 138 kV Remote End Work | AEP |  |  |  | 6/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.0471 |  | 2/26/2025 | Cancelled
PJM MA | s3987.1 | Rebuild the Grand Point - Roxbury 138 kV Line (14 miles total) with steel H-frame structures and new conductor. -5.5 miles per PN-2024-012 -8.5 miles per APS-2024-028 At Roxbury Substation: -Replace limiting substation conductor and revise relay settings. At Greene Substation (APS): -Revise relay settings. At Letterkenny Substation (APS): -Replace line switch and revise relay settings. At Grand Point Substation (APS): -Replace substation conductor, circuit breaker, install surge arrestors and ground switch, and revise relay settings. Transmission Line Ratings: Roxbury - AD2-062 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Greene - AD2-062 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Letterkenny - Greene 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Grand Point - Letterkenny 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/11/2025 | 12/11/2025 | 17.94 |  |  | New Upgrade
PJM MA | s3986.1 | Shawville and Lewistown 230 kV Terminal Upgrades: At Shawville Substation (PN-2023-022): Replace substation conductor and revise relay settings. At Lewistown Substation (PN-2023-022): Replace line trap and revise relay settings. Transmission Line Ratings: Lewistown - Shingletown 230 kV Line: Before Proposed Solution: 512 / 612 / 619 / 700 MVA (SN/SE/WN/WE) After Proposed Solution: 546 / 666 / 619 / 790 MVA (SN/SE/WN/WE) Shawville - Shingletown 230 kV Line: Before Proposed Solution: 442 / 582 / 619 / 700 MVA (SN/SE/WN/WE) After Proposed Solution: 546 / 666 / 619 / 790 MVA (SN/SE/WN/WE) Dale Summit - Shingletown 230 kV Line: Before Proposed Solution: 486 / 523 / 542 / 571 MVA (SN/SE/WN/WE) After Proposed Solution: 617 / 754 / 699 / 894 MVA (SN/SE/WN/WE) This project is concurrent with APS-2023-059. | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/7/2026 | 7/7/2026 | 4.97 |  |  | New Upgrade
PJM WEST | n8094.1 | 5.3.1 ComEd will be responsible to perform design, procurement, and construction to upgrade remote terminal TSS 61 Streator. | ComEd |  |  |  | 11/15/2019 | 12/31/2025 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8094.2 | L6101 Cut-in Tap into TSS 919 Peru Township | ComEd |  |  |  | 11/15/2019 | 12/31/2025 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | s3985.1 | Reeds Gap Switching Station – Blain 115 kV Line Rebuild: Rebuild and reconductor 9.9 miles of 115 kV line from Reeds Gap Switching Station to Blain Switching Station on the Lewiston - Shade Gap 115 kV Line. Upgrade all substation equipment at the line terminal stations. Replace CT's and Substation Conductor at Reed's Gap Switching Station on line terminal to Shade Gap Substation. Replace substation conductor at Reed's Gap Switching on line terminal to Reeds Gap Substation. Replace substation conductor at Reeds Gap Substation on line terminal to Blain Substation. Transmission Line Ratings: Reeds Gap Switching Station - Reeds Gap 115 kV Line: Before Proposed Solution: 95 / 99 / 121 /121 MVA (SN/SE/WN/WE) After Proposed: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) Reeds Gap - Blain 115 kV Line: Before Proposed Solution: 86 / 110 / 122 / 137 MVA (SN/SE/WN/WE) After Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 36.8 |  |  | New Upgrade
PJM MA | s3984.1 | Lewistown Area 46 kV Network: - Build a new two-mile 46 kV line from the Molly Ring Bus (b3754) and tap the 1LK2 46 kV line southwest of the existing Lewistown - Logan 46 kV 1LK Tap. - Cut the 46 kV Line between the existing 1LK Tap and the new Molly - 1LK2 Tap 46 kV Line. - Install a fourth 46 kV circuit breaker in the ring bus at Molly Substation. - Eliminate normally open and three terminal lines on the 1LK 46 kV circuit between Yeagertown and Lewistown substations. - Revise relay settings at Lewistown, Logan, Mount Union, Riverside, Warrior Ridge, and Yeagerstown Substations Transmission Line Ratings: New Molly - 1LK2 Tap 46 kV Line: Before Proposed Solution: N/A After Proposed Solution: 32 / 32 / 35 / 35 MVA (SN/SE/WN/WE) Molly- 1LK Tap 46 kV Line: Before Proposed Solution: 32 / 32 / 35 / 35 MVA (SN/SE/WN/WE) After Proposed Solution: 32 / 32 / 35 / 35 MVA (SN/SE/WN/WE) Yeagertown - Molly 46 kV Line: Before Proposed Solution: N/A MVA (SN/SE/WN/WE) After Proposed Solution: 36 / 43 / 40 / 51 MVA (SN/SE/WN/WE) Lewistown - First Quality 46 kV Line: Before Proposed Solution: 93 / 113 / 105 / 134 MVA (SN/SE/WN/WE) After Proposed Solution: 93 / 113 / 105 / 134 MVA (SN/SE/WN/WE) | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | EP | 3/18/2026 | 3/18/2026 | 6.61 |  |  | New Upgrade
PJM MA | s3983.1 | Corry East-Four Mile Junction 115 kV Line Rebuild: Rebuild the Corry East-Four Mile Junction 115 kV (24.3 miles total) with new conductor. Replace SCCIR at Corry East Substation Transmission Line Ratings: Corry East - Four Mile Junction 115 kV Line Before Proposed Solution: 202 / 245 / 228 / 290 MVA (SN/SE/WN/WE) After Proposed Solution: 232 / 282 / 263 / 334 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/18/2026 | 3/18/2026 | 68.82 |  |  | New Upgrade
PJM MA | s3982.1 | Bethlehem Mine 33 - Nanty Glo 46 kV SGR Line: Reroute the existing 46 kV Line overbuilding an existing distribution ROW to eliminate the clearance concern: - Raise span #332 to #333, span #350 to #351, and span #370 to #371 due to clearance concerns Transmission Line Ratings: Ebensburg - Revloc 46 kV Line Before Proposed Solution: 30 / 31 / 35 / 35 MVA (SN/SE/WN/WE) After Proposed Solution: 32 / 32 / 35 / 35 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 2/12/2026 | 2/12/2026 | 1.67 |  |  | New Upgrade
PJM MA | s3981.1 | Bobik Lane 46 kV Substation: - Construct a new 46 kV four breaker ring bus station At Glory Substation: - Replace line relaying At Spangler Substation: - Replace line relaying At Nanty Glo Substation: - Replace line relaying At Strongstown Substation: - Replace disconnect switches and install SCADA control Transmission Line Ratings: Bobik Lane - Glory 46 kV Line Before Proposed Solution: N/A After Proposed Solution: 67 / 81 / 75 / 95 MVA (SN/SE/WN/WE) Bobik Lane - Teakettle 46 kV Line Before Proposed Solution: N/A After Proposed Solution: 67 / 81 / 75 / 95 MVA (SN/SE/WN/WE) Bobik Lane - Moss Creek 46 kV Line Before Proposed Solution: N/A After Proposed Solution: 67 / 81 / 75 / 95 MVA (SN/SE/WN/WE) Bobik Lane - Nicktown 46 kV Line Before Proposed Solution: N/A After Proposed Solution: 67 / 81 / 75 / 95 MVA (SN/SE/WN/WE) | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | EP | 12/11/2025 | 12/11/2025 | 13.81 |  |  | New Upgrade
PJM MA | s3979.1 | Cooper and Prospect Substation 115 kV Terminal Upgrades: At Cooper Substation, replace circuit breaker, breaker leads, and associated disconnect switches, install new CCVTs and connect to existing relaying. At Prospect Substation, replace two circuit breakers, breaker leads, and associated disconnect switches, replaces substation conductor and transmission line drop. Transmission Line Ratings: Prospect - Rosedale Junction 115 kV Line: Before Proposed Solution: 147 / 191 / 214 / 237 MVA (SN/SE/WN/WE) After Proposed Solution: 202 / 245 / 228 / 290 MVA (SN/SE/WN/WE) Cooper - Rosedale Junction 115 kV Line: Before Proposed Solution: 249 / 300 / 282 / 351 MVA (SN/SE/WN/WE) After Proposed Solution: 273 / 333 / 309 / 395 MVA (SN/SE/WN/WE) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2025 | 11/13/2025 | 3.25 |  |  | New Upgrade
PJM MA | s3978.1 | Shelocta 230/115 kV Substation: Replace the limiting substation conductor on the Shelocta No. 2 230/115 kV Transformer. Shelocta No. 2 230/115 kV Transformer Before Proposed Solution: 146 / 190 / 209 / 236 MVA (SN/SE/WN/WE) After Proposed Solution: 221 / 228 / 274 / 283 MVA (SN/SE/WN/WE) | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | EP | 10/8/2025 | 10/8/2025 | 0.25 |  |  | New Upgrade
PJM MA | s3977.1 | Frystown – South Lebanon 69 kV Line Rebuild: Rebuild 10.85 miles of the Frystown - South Lebanon 69 kV 83 Line and install new conductor At South Lebanon Substation: - Reterminate new line conductor into substation At Frystown Substation: - Reterminate new line conductor into substation Transmission Line Ratings: Frystown - Rehrersburg 69 kV Line Before Proposed Solution: 55 / 56 / 62 / 62 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Rehrersburg - South Lebanon 69 kV Line Before Proposed Solution: 55 / 56 / 62 / 62 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) | ME |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/14/2026 | 5/14/2026 | 32.59 |  |  | New Upgrade
PJM MA | s3976.1 | Muhlenberg 69 kV Substation: Convert Muhlenberg Substation into a nine-breaker 69 kV Breaker-and-a-Half substation. Install nine (9) new 69 kV circuit breakers, associated disconnect switches and relaying at Muhlenberg Substation. Replace three (3) existing transformer high-side breakers with new 69 kV circuit breakers Install one (1) new package control enclosure (PCE) within the new substation fence. Revise relay settings at North Temple, Carpenter Technology, and Lucent substations. Re-terminate the existing Carpenter Technology - Muhlenberg, Lucent - Muhlenberg, and Muhlenberg - North Temple 69 kV Lines into substation. | ME |  |  | Operational Flexibility and Efficiency |  |  | EP | 3/18/2026 | 3/18/2026 | 29.29 |  |  | New Upgrade
PJM WEST | n8104.1 | a new three (3) circuit breaker 138 kV station, Snowhill, physically configured in a breaker and half bus arrangement but operated as a ring-bus | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 6.5353 |  |  | Cancelled
PJM WEST | n8104.2 | Connect Snowhill 138 kV Station to Existing Transmission Circuit, Update Remote End Protective Relay Settings | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.8126 |  |  | Cancelled
PJM MA | s3975.1 | South Reading - West Reading 69 kV Line Rebuild: Rebuild approximately 2.75 line miles of wood pole construction. South Reading - Replace relaying for 69 kV Circuit Breaker 2642. West Reading - Replace 69 kV Circuit Breaker 2602, Switches 2604 & 2605, and Relaying. Transmission Line Ratings: Existing Line ratings: 132 /158 / 158 / 180 MVA (SN/SE/WN/WE) New Line Ratings: 139 / 169 / 158 / 201 MVA (SN/SE/WN/WE) Transformer Ratings: N/A | ME |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 3/18/2026 | 3/18/2026 | 17.1 |  |  | New Upgrade
PJM WEST | n8104.3 | Replace Protective Relays at Strawton 138 kV Station | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.1987 |  |  | Cancelled
PJM WEST | n8104.4 | Install Two (2) Fiber-Optic Paths to facilitate relaying between Snowhill, Deer Creek, and Strawton 138 kV Stations | AEP |  |  |  | 12/1/2021 | 10/1/2023 | Cancelled | 1/9/2024 | 1/9/2024 | 0.2403 |  |  | Cancelled
PJM MA | s3974.1 | Carpenter Technology 69 kV Substation: Replace Carpenter Technology 69 kV breaker 83692 and associated disconnect switches. Transmission Line Ratings: Carpenter Technology - Riverview 69 kV 836 Line: Before Proposed Solution: 147 / 180 / 187 / 211 MVA (SN/SE/WN/WE) After Proposed Solution: 147 / 188 / 193 / 211 MVA (SN/SE/WN/WE) | ME |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/11/2025 | 12/11/2025 | 1.01 |  |  | New Upgrade
PJM MA | s3973.1 | Cleona – Campbelltown 69kV Line: Rebuild and convert Campbelltown - Cleona 69 kV Line from six-wired to double circuit (approximately 7.4 miles). At Campbelltown Substation: Install one 69 kV circuit breaker, associated disconnect switches and line relaying At Cleona Substation Install one 69 kV circuit breaker, associated disconnect switches and line relaying Transmission Line Ratings: Campbelltown - Hershey Beta Tap 69 kV Line Before Proposed Solution: 71 / 72 / 72 / 72 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Hershey Beta Tap - Millards Quarry 69 kV Line: Before Proposed Solution: 107 / 128 / 120 / 152 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Annville - Millards Quarry 69 kV Line: Before Proposed Solution: 82 / 103 / 108 / 124 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Annville - North Lebanon 69 kV Line: Before Proposed Solution: 71 / 89 / 101 / 108 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Campbelltown - Cleona 69 kV Line: Before Proposed Solution: NA After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) | ME |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 12/11/2025 | 12/11/2025 | 32.33 |  |  | New Upgrade
PJM SOUTH | n8105.1 | Build a three breaker AE2-190 115 kV switching station. The objective of this project is to build a 230kV, 3-breaker ring bus to support the new 70MW solar farm built by Alameda Solar I, LLC. The site is located along Dominion Energy's existing 230kV, 2114 Line from Remington C.T. Substation to Gainesville Substation. The cut line will consume two of the positions in the ring bus. The third position will be for the 230kV feed from Alameda Solar I, LLC collector station for the new 70MW solar farm. | Dominion |  |  |  | 11/30/2021 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n9635.0 | Expansion of existing 161 kV Summer Shade substation to include one (1) 161 kV A-Frame substation structure, one (1) 161 kV 2000 amp Circuit Breaker, four (4) 2000 amp switches (includes PCO switch), three (3) 161 kV metering CTs, and three (3) 108 kV station class surge arrestors. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 6.002 |  |  | New Upgrade
PJM SOUTH | n8105.3 | Re-arrange line #2114 to loop into and out of the new three breaker AE2-190 230kV switching station. The existing 230kV Line #2114 will be split into two (2) circuits in order to incorporate the new AE2-190 generation interconnect substation onto Dominion’s System. Line #2114 will be split between existing lattice tower structures 535/159 (2114/30) and 535/160 (2114/29) and dead-end on two (2) 3-pole steel single circuit double dead-end heavy angle structures. The two (2) new circuits will transition from the double dead-end 3-pole structures and terminate into the AE2-190 generation interconnect substation via two (2) standard backbone structures. | Dominion |  |  |  | 11/30/2021 |  | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n8105.2 | Remote protection and communication work | Dominion |  |  |  | 11/30/2021 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n9611.0 | West Flemingsburg Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 12.618 |  |  | New Upgrade
PJM WEST | n9610.0 | Revise Relay Settings at Goddard Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.134 |  |  | New Upgrade
PJM WEST | n9609.0 | Revise Relay Settings at Spurlock Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.134 |  |  | New Upgrade
PJM WEST | n9608.0 | Fiber Installation in Existing ROW: Install overhead optical ground wire (OPGW) on the Spurlock-Flemmingsburg-Goddard line section (32.1 miles). | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 4.1064 |  |  | New Upgrade
PJM WEST | n9607.0 | Interconnection Substation Tie-In: Cut and loop Spurlock - Flemingsburg 138 kV line into new interconnection substation with two (2) total new guyed steel 3-pole dead-end structures. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.847 |  |  | New Upgrade
PJM WEST | n9606.0 | Grounding Study at Flemingsburg Dist. Sub. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.085 |  |  | New Upgrade
PJM WEST | n7179 | EKPC to install OPGW on the Fawkes-Three Forks Tap 138kV line section (3.6 miles) | EKPC |  |  |  | 3/29/2019 | 12/1/2022 | EP | 11/3/2026 | 11/3/2026 | 0.635 |  |  | New Upgrade
PJM WEST | n7178 | EKPC to upgrade relays and modify relay settings at Fawkes substation for existing line to Three Forks Tap Switching substation | EKPC |  |  |  | 3/29/2019 | 12/1/2022 | EP | 11/3/2026 | 11/3/2026 | 0.09 |  |  | New Upgrade
PJM WEST | n7177 | EKPC to upgrade relays and modify relay settings at Dale substation for existing line to Three Forks Tap Switching substation | EKPC |  |  |  | 3/29/2019 | 12/1/2022 | EP | 11/3/2026 | 11/3/2026 | 0.09 |  |  | New Upgrade
PJM WEST | n7176 | EKPC to construct facilities (~125 feet) to loop the existing Dale-Fawkes 138kV line section into the new Three Forks Tap Switching substation and reroute the existing Three Forks Distribution 138kV Line (~900 feet) into the new Three Forks Tap Switching Station. | EKPC |  |  |  | 3/29/2019 | 12/1/2022 | EP | 11/3/2026 | 11/3/2026 | 0.82 |  |  | New Upgrade
PJM WEST | n7175 | EKPC to construct a new 138kV switching station (Three Forks Tap Switching) to facilitate connection of the Madison Solar generation project | EKPC |  |  |  | 3/29/2019 | 12/1/2022 | EP | 11/3/2026 | 11/3/2026 | 3.57 |  |  | New Upgrade
PJM WEST | s4062.2 | Install two 138 kV Circuit Breakers and a Meter at Progress Park station. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 7.128 |  |  | New Upgrade
PJM WEST | s4062.1 | Construct 0.2 miles of greenfield single circuit 138kV line from Progress Park to dead-end insulators on the customer's station steel structure. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 4.6309 |  |  | New Upgrade
PJM WEST | s4061.4 | Expand Torrey with the installation of (2) 138 kV 3000A 63 kA circuit breakers to allow the elimination of the Torrey Bypass; re-termination and remote end settings updates at Timken Richville & Timken Stations will be required to account for the new circuit breakers. Replace existing 138kV 40kA breaker AF with 63kA unit. Sub-conductor on the Torrey 138 kV Bus Tie Branch will be replaced with 2000 KCM AAC, 91-Str. (SE 449) to accommodate the additional load flow. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 5.662 |  |  | New Upgrade
PJM WEST | s4061.3 | Install (2) ~0.1 mile customer feeds from Vettel station utilizing 1272 ACSR 54/19 Pheasant (SE 963). | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 1.7119 |  |  | New Upgrade
PJM WEST | s4061.2 | Cut into the Southeast Canton - South Canton and Southeast Canton - Sunnyside 138 kV lines with (2) ~0.36 mile double circuit lines utilizing 1033.3 KCM ACSR 54/7 Curlew (SE 822 MVA), to accommodate the greenfield Vettel Station. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 9.2016 |  |  | New Upgrade
PJM WEST | s4061.1 | Construct a greenfield breaker and a half station operated as a ring bus with (6) 138 kV 3000A 63 kA circuit breakers. To accommodate the new station remote end work at South Canton, Southeast Canton, & Sunnyside will be required. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 16.4911 |  |  | New Upgrade
PJM WEST | n8121.2 | North Longview: Install a new 500kV terminal at North Longview substation. | APS |  |  |  | 6/1/2022 |  | EP | [5 empty] | Scope/Cost Change
PJM WEST | n8121.3 | Fort Martin: Modify relay settings. | APS |  |  |  | 6/1/2022 |  | EP | [5 empty] | Scope/Cost Change
PJM WEST | s4060.1 | In order to serve the customer's new delivery referred to as NBY-7, a new double circuit line extension will be constructed by tapping into the existing radial line to the customer's NBY6 station fed from AEP's Anguin station and extending it to the customer's new NBY-7 station on their site. This will involve about ~0.25 miles of double circuit line utilizing ACSS Drake 795 (26/7) conductor (SE 360 MV) that will terminate into the customer’s NBY-7 station. | AEP |  |  | Customer Service |  |  | EP | 1/17/2025 | 1/17/2025 | 0.6 |  |  | New Upgrade
PJM WEST | n8121.4 | 502 Junction: Modify relay settings. | APS |  |  |  | 6/1/2022 |  | EP | [5 empty] | Scope/Cost Change
PJM WEST | s4058.3 | At Hannibal substation to provide service to the customer, expand station yard and both 138kV main bus runs to accommodate new CB strings. A new 138 kV breaker string will be required due to lack of open positions at Hannibal station. Three new 138 kV 63 kA breakers will be necessary allow for customer interconnection. Two 138kV breakers will be relocated to allow for line relocations. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 4.4617 |  |  | New Upgrade
PJM WEST | s4058.2 | Relocate Kammer - Ormet No.1 double circuit 138kV line (Hannibal - Kammer 138kV circuits) to enter the Hannibal substation from North Side. This will allow for the Hannibal substation expansion to the West side and which in turn will allow the new customer lines to exit from the South of Hannibal substation. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 0.91731 |  |  | New Upgrade
PJM WEST | s4058.1 | Hannibal – Customer 138kV radial Feed: A new radial feed of about 0.2 miles to feed the customer directly from Hannibal station. | AEP |  |  | Customer Service |  |  | EP | 3/14/2025 | 3/14/2025 | 3.2115 |  |  | New Upgrade
PJM MA | s4014.1 | Traynor No. 14 230-34.5kV Transformer: Replace the Traynor No 14 230-34.5 kV Transformer. Replace 230 kV circuit switcher on No. 14 transformer with a SCADA controlled full load-break MOAB Switch Replace two 34.5 kV circuit breakers on No. 14 transformer. Replace transformer disconnect switches and substation conductor. Remove LB30 Load breaker switch and install one 230 kV circuit breaker on the Traynor - Whippany No. 1 230 kV Y1039 Line terminal. Traynor No. 14 230-34.5 kV Transformer Ratings: Before Proposed Solution: 137 / 168 / 171 / 201 MVA (SN/STLE/WN/WLTE) After Proposed Solution: 168 / 176 / 202 / 218 MVA (SN/STLE/WN/WLTE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/7/2026 | 7/7/2026 | 12.35 |  |  | New Upgrade
PJM SOUTH | n8129.1 | PJM Network Upgrade #nXXXX - Build a three breaker AF1-075 230 kV switching station. Project AF1-075 provides for the initial construction of a new 230kV three breaker ring substation between transmission structures 2134/46 and 2134/47 located in Rockingham County, Virginia. | Dominion |  |  |  | 12/31/2021 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM SOUTH | n8129.2 | Remote protection and communication work | Dominion |  |  |  | 12/31/2021 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | s4013.1 | Traynor No. 13 230-34.5kV Transformer: Replace the Traynor No. 13 230-34.5 kV Transformer. Replace 230 kV circuit switcher on No. 13 transformer with a SCADA controlled full load-break MOAB Switch Replace two 34.5 kV circuit breakers on No. 13 transformer. Replace transformer disconnect switches and substation conductor. Remove LB16 Load breaker switch and install one 230 kV circuit breaker on the Traynor - Whippany No. 2 230 kV Z1040 Line terminal. Traynor No. 13 230-34.5 kV Transformer Ratings: Before Proposed Solution: 82 / 103 / 108 / 124 MVA (SN/STLE/WN/WLTE) After Proposed Solution: 168 / 176 / 202 / 218 MVA (SN/STLE/WN/WLTE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/7/2026 | 7/7/2026 | 16.73 |  |  | New Upgrade
PJM SOUTH | n8129.3 | PJM Network Upgrade #nXXXX - Split line #2134 This project serves to install a new 73 MW solar generating facility interconnected to Line 2134 between Harrisonburg and Endless Caverns substation, thus splitting line 2134. | Dominion |  |  |  | 12/31/2021 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | s4012.1 | Leisure Valley 230 kV Substation: Rebuild the 230 kV station as a breaker and a half configuration utilizing nine new 230 kV breakers. Install a third 230-34.5 kV transformer with two new 34.5 kV breakers on the low side. Install high side breakers on the two 230-13.2 kV transformers. At Manitou Substation: Replace switches, line trap and line relaying. At Lakewood Substation: Replace circuit breakers, switches, surge arresters, line traps and relaying. Adjust line relaying at South Lakewood, Silverton, Drum Point, Cedar Bridge substations. Transmission Line Ratings: Lakewood-Leisure Village D2030 230 kV Line Before Proposed Solution: 678 / 813 / 833 / 929 MVA (SN/SE/WN/WE) After Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN/SE/WN/WE) Lakewood-Leisure Village U2021 230 kV Line Before Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN/SE/WN/WE) After Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN/SE/WN/WE) Leisure Village - Manitou A2027 230 kV Line Before Proposed Solution: 678 / 813 / 833 / 929 MVA (SN/SE/WN/WE) After Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN/SE/WN/WE) Leisure Village - Manitou C2029 230 kV Line Before Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN/SE/WN/WE) After Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN/SE/WN/WE) Leisure Village No. 5 230-34.5 kV Transformer Before Proposed Solution: N/A After Proposed Solution: 150 / 195 / 188 / 234 MVA (SN/SE/WN/WE) Leisure Village No. 3 230-34.5 kV Transformer Before Proposed Solution: 144 / 157 / 163 / 198 MVA (SN/SE/WN/WE) After Proposed Solution: 157 / 157 / 198 / 200 MVA (SN/SE/WN/WE) Leisure Village No. 4 230-34.5 kV Transformer Before Proposed Solution: 144 / 155 / 163 / 193 MVA (SN/SE/WN/WE) After Proposed Solution: 152 / 155 / 191 / 194 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | EP | 10/8/2025 | 10/8/2025 | 50.23 |  |  | New Upgrade
PJM SOUTH | s3997.4 | Expand North Anna substation to terminate the new 230 kV line from Frances by adding a new 230kV string of breakers in a breaker-and-a-half arrangement. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 2 |  |  | New Upgrade
PJM SOUTH | s3997.3 | Rebuild 230 kV line #255 (Southall-North Anna) approximately 1.1 miles as 230 kV double-circuit lines from Frances to North Anna. Expand North Anna substation to terminate the new 230 kV line from Frances by adding a new 230kV string of breakers in a breaker-and-a-half arrangement. Install associated 230 kV terminal equipment at Frances and North Anna to terminate both lines (existing Line #255 and new 230 kV line), creating two Frances to North Anna lines | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 10 |  |  | New Upgrade
PJM SOUTH | s3997.2 | Connect a new Frances substation by extending a new double circuit 230kV feed from Southall substation. Lines will terminate in a 230kV six-breaker ring arrangement between Southall and Frances. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 1 |  |  | New Upgrade
PJM SOUTH | s3997.1 | Construct Frances 230kV substation with 6 breaker ring bus configuration. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 20 |  |  | New Upgrade
PJM MA | s3972.1 | Replace the under-bridge cables on the Manitou-Ocean Beach-Seaside Park 34.5 kV D212 Line and Manitou-Ortley Beach 34.5 kV V126 Line with new submarine cables (1-mile). Utilize submarine EPR cable with health monitoring capability as the new transmission line conductor. Island Heights Tap-Ortley Beach 34.5 kV: Before Proposed Solution: 35 / 44 / 35 / 44 MVA (SN/SE/WN/WE) After Proposed Solution: 44 / 53 / 50 / 63 MVA (SN/SE/WN/WE) Toms River Tap-Seaside Park 1 Tap 34.5 kV: Before Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 10 |  |  | New Upgrade
PJM MA | s3971.1 | EH Werner - Keyport 34.5 kV V48 Line Rebuild: Rebuild approximately 7.6 miles of the EH Werner - Keyport 34.5 kV V48 Line using new conductor and upgrade relays at EH Werner and Keyport substations. A portion of the line between Str. 168 to Str. 206 (1.3-miles) will not be rebuilt as it will be rebuilt per b3130.6. Replace substation conductor at Clifford Solar Substation. Transmission Line Ratings: Keyport - Clifford Solar 34.5 kV Line Before Proposed Solution: 41 / 50 / 48 / 60 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Clifford Solar - EH Werner 34.5 kV Line: Before Proposed Solution: 41 / 50 / 48 / 60 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 42.1 |  |  | New Upgrade
PJM MA | s3970.1 | Bernardsville - Gillette 34.5 kV B730 Line: Rebuild approximately 5.0 miles of Gillette - Stirling - Lyons 34.5 kV B730 Line with new conductor. Rebuild approximately 1.7 miles Gillette - Martinsville 34.5 kV I737 Line from Structure #39 to #16 that are shared with Gillette - Stirling 34.5 kV B370 Line with new conductor. Replace in-line switch LB21-I737 on Gillette - Martinsville 34.5 kV I737 Line with 34.5 kV load break SCADA switch. At Gillette Substation: Upgrade relay settings. At Stirling Substation: Replace disconnect switches. Transmission Line Ratings: Gillette - Stirling Tap 34.5 kV B730 Line Section: Before Proposed Solution: 41 / 50 / 48 / 60 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Stirling Tap - Lyons 34.5 kV B730 Line Section: Before Proposed Solution: 37 / 38 / 42 / 42 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Stirling Tap - Stirling 34.5 kV B730 Line Section: Before Proposed Solution: 39 / 48 / 51 / 57 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Gillette - Stirling Tap 34.5 kV I737 Line Section: Before Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 7/17/2026 | 7/17/2026 | 20.51 |  |  | New Upgrade
PJM MA | s3969.1 | Allenhurst 34.5 kV Substation Breaker Replacements: At Allenhurst Substation, replace 34.5 kV circuit breakers H216 and V-74 and associated disconnect switches, substation conductor, and relaying. Transmission Line Ratings: Allenhurst - Oceanview H216 34.5 kV Line Before Proposed Solution: 44 / 48 / 48 / 48 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/16/2026 | 6/16/2026 | 3.31 |  |  | New Upgrade
PJM MA | s3968.1 | Highlands-Long Branch 34.5 kV K89 Line Rebuild: Rebuild 7.8 miles of the Highlands - Long Branch 34.5 kV K89 Line with new conductor. Rebuild the taps to the existing customers at Sandy Hook and Sea Bright substations. At Highlands Substation: Replace one disconnect switch and upgrade substation conductor. At Long Branch Substation: Replace one disconnect switch and upgrade substation conductor. At Sandy Hook Substation: Replace one disconnect switch. Transmission Line Ratings: Highlands - Sandy Hook SW 34.5 kV Line: Before Proposed Solution: 37 / 38 / 42 / 42 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Sandy Hook SW - Sandy Hook 34.5 kV Line: Before Proposed Solution: 26 / 33 / 37 / 41 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Sandy Hook SW - Sea Bright SW 34.5 kV Line: Before Proposed Solution: 37 / 38 / 42 / 42 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Sea Bright SW - Monmouth Beach 34.5 kV Line: Before Proposed Solution: 35 / 38 / 35 / 42 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Monmouth Beach - Long Branch 34.5kV Line: Before Proposed Solution: 34 / 38 / 34 / 42 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Sea Bright SW - Sea Bright 34.5 kV Line: Before Proposed Solution: 37 / 38 / 42 / 42 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/16/2026 | 6/16/2026 | 28.27 |  |  | New Upgrade
PJM MA | s3967.1 | Deep Run - Englishtown 115 kV DRE1 Line Rebuild: Rebuild the Englishtown - Deep Run 115 kV DRE1 Line using new conductor. At Englishtown Substation, replace relays and substation conductor. At Deep Run Substation, replace relays substation conductor. Before Proposed Solution: 176 / 223 / 227 / 279 MVA (SN/SE/WN/WE) After Proposed Solution: 373 / 430 / 374 / 452 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/14/2026 | 5/14/2026 | 38.88 |  |  | New Upgrade
PJM MA | s3966.1 | Deep Run - Englishtown 115 kV DRE2 Line Rebuild: Rebuild the Englishtown - Deep Run 115 kV DRE2 Line using new conductor. At Englishtown Substation, replace relays and substation conductor. At Deep Run Substation, replace relays substation conductor. Before Proposed Solution: 176 / 223 / 227 / 286 MVA (SN/SE/WN/WE) After Proposed Solution: 373 / 430 / 374 / 452 MA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/14/2026 | 5/14/2026 | 36.34 |  |  | New Upgrade
PJM MA | s3965.1 | EH Werner- Freneau- Keyport 34.5 kV E31 Line Rebuild: Rebuild the EH Werner- Freneau- Keyport 34.5 kV E31 Line (6.9 miles total) with new conductor. Replace limiting sub conductor at Freneau and Keyport substations. Transmission Line Ratings: Clark St - Keyport E31 34.5 kV Line Before Proposed Solution: 44 / 53 / 50 / 63 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Clark St - Clark St Tap E31 34.5 kV Line Before Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Clark St Tap - Freneau E31 34.5 kV Line Before Proposed Solution: 53 / 62 / 63 / 71 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Clark St Tap - Laurence E31 34.5 kV Line Before Proposed Solution: 35 / 44 / 35 / 44 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Feltus St - Laurence E31 34.5 kV Line Before Proposed Solution: 35 / 44 / 35 / 44 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) Feltus St - Werner E31 34.5 kV Line Before Proposed Solution: 44 / 53 / 50 / 62 MVA (SN/SE/WN/WE) After Proposed Solution: 55 / 67 / 63 / 79 MVA (SN/SE/WN/WE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/18/2026 | 3/18/2026 | 22.5 |  |  | New Upgrade
PJM MA | s3964.1 | Morris Court 34.5 kV Substation - Customer Interconnection: - Provide connection for a second transformer at Morris Court Substation - Upgrade remote terminal end relay settings at Briant Park and Traynor substations - Install wholesale revenue metering | JCPL |  |  | Customer Service |  |  | EP | 1/15/2026 | 1/15/2026 | 0.11 |  |  | New Upgrade
PJM MA | s3963.1 | Martinsville - Readington 34.5 kV X778 Line - Customer Interconnection: - Construct approximately 0.01 miles 34.5 kV extension line from the Martinsville - Readington 34.5 kV X778 Line to the customer substation. - Install three switches equipped with SCADA control, - Adjust relay settings at Martinsville and Readington substations - Install revenue metering | JCPL |  |  | Customer Service^Other |  |  | EP | 12/11/2025 | 12/11/2025 | 1.08 |  |  | New Upgrade
PJM MA | s3962.1 | Englishtown No. 6 230-34.5 kV Transformer: Replace limiting substation equipment of transformer leads to exceed the Englishtown No. 6 230-34.5 kV Transformer rating. Englishtown 230-34.5 kV Bank 6 Transformer Ratings: Before Proposed Solution: Single Breaker Outage #1: 72 / 94 / 72 / 94 MVA (SN/SSTE/WN/WSTE) Single Breaker Outage #2: 125 / 150 / 156 / 176 MVA (SN/SSTE/WN/WSTE) After Proposed Solution: 151 / 151 / 194 / 194 MVA (SN/SSTE/WN/WSTE) | JCPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 12/8/2025 | 12/8/2025 | 2.06 |  |  | New Upgrade
PJM MA | s3961.1 | Glen Gardner No. 8 230-34.5 kV Transformer: -Replace the Glen Gardner No. 8 230-34.5 kV Transformer with a 168 MVA unit -Replace 230 kV MOAB switch with one full load break MOAB switch with SCADA control -Replace the limiting terminal equipment and relays Glen Gardner No. 8 230-34.5 kV Transformer rating: Before Proposed Solution: 108 / 136 / 137 / 152 MVA (SN/STE/WN/WTE) After Proposed Solution 168 / 176 / 202 / 218 MVA (SN/STE/WN/WTE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/8/2025 | 12/8/2025 | 7.35 |  |  | New Upgrade
PJM MA | s3960.1 | Glen Gardner No. 1 230-34.5 kV Transformer: - Replace the Glen Gardner No. 1 230-34.5 kV Transformer with a 168 MVA unit - Replace one 230 kV circuit switcher with one 230 kV full-load break MOAB Switch with SCADA control - Replace one 34.5 kV circuit breaker - Replace the limiting terminal equipment and relays Glen Gardner No. 1 230-34.5 kV Transformer Ratings: Before Proposed Solution: 93 / 116 / 118 / 129 MVA (SN/STE/WN/WTE) After Proposed Solution: 168 / 176 / 202 / 218 MVA (SN/STE/WN/WTE) | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/8/2025 | 12/8/2025 | 7.35 |  |  | New Upgrade
PJM SOUTH | s3990.2 | Replace Elmont 500/230 kV TX #2 with new 1440 MVA TX and replace low-side equipment limiting TX rating. | Dominion |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 17.5 |  |  | New Upgrade
PJM SOUTH | s3990.1 | 230kV switching station with at least five strings of breaker and a half configuration. Both 230kV lines #2090 (Ladysmith CT - Fredericksburg) and #256 (Ladysmith CT - Four Rivers) should be cut and terminated at Matta switching station. Six 230kV 4000A breakers will be installed initially to accommodate four 230kV transmission lines. | Dominion |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 25.5 |  |  | New Upgrade
PJM SOUTH | s3989.3 | Wreck and rebuild the existing transmission lines #2088 (Gordonsville - Louisa CT), #2074 (Louisa CT - South Anna), #2202 (South Anna- Desper), #2298 (Desper - Foxbrook Lane) for approximately 19 miles with a double circuit 230kV structures. The new second circuit will be connected between Gordonsville and Wesbey Drive substations. This new line will share the double circuit structures with lines #2088, #2074, #2202, and #2298. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 115 |  |  | New Upgrade
PJM SOUTH | s3989.2 | Connect a new Wesbey Drive substation by extending a new double circuit 230kV feed from Foxbrook Lane substation. Lines to terminate in a 230kV six-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 20 |  |  | New Upgrade
PJM SOUTH | s3989.1 | Connect the new Wesbey Drive substation to the Foxbrook Lane substation with a double circuit 230kV lines for approximately 0.5 miles. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 1 |  |  | New Upgrade
PJM SOUTH | s3988.3 | Install a 150 MVAr Capacitor Bank at Shaw substation | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 4 |  |  | New Upgrade
PJM SOUTH | s3988.2 | Cut and extend Line #2276 (Kyser-Remington) line approximately 0.6 miles on double-circuit 230 kV structures to the new Shaw substation. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 9 |  |  | New Upgrade
PJM SOUTH | s3988.1 | Cut and extend Line #2276 (Kyser-Remington) line approximately 0.6 miles on double-circuit 230 kV structures to the new Shaw substation. The lines will terminate in a 230 kV ring bus configured for an ultimate arrangement of six breakers, with four breakers installed initially. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 23 |  |  | New Upgrade
PJM SOUTH | s3992.2 | West Creek Substation will be constructed with a 230 kV ring-bus, configured for an ultimate arrangement of six breakers, with four breakers installed initially. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 15 |  |  | New Upgrade
PJM SOUTH | s3992.1 | Cut existing 230kV Line 2009 between Short Pump and Rockville and extend a new 230kV double circuit loop, approximately 6.5 miles, in and out of West Creek Substation. | Dominion |  |  | Customer Service |  |  | EP | 1/6/2026 | 1/6/2026 | 20 |  |  | New Upgrade
PJM WEST | s3948.1 | Reconductor the Black River-Shinrock 69 kV Line from Str. 113=39 to Str. 244=41 (~22.56 miles). Rebuild the section from Shinrock Substation to Str. 113=39 with double circuit structures, this will rebuild a section of the Shinrock-Greenfield 69 kV Line as well (~1 mile). The section from Str. 244=41 to Black River Substation will not be reconductored due to being reconductored recently. Also reconductor the taps to Baumhart (~0.1 miles), Elyria City Pumping (~0.2 miles), and Washington (~0.4 miles). Transmission Line Ratings: Black River Tap-Washington Tap 69 kV Line - Before Proposed Solution: 100 / 121 / 113 / 143 MVA (SN/SE/WN/WE) - After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Elyria Waterworks Tap-Washington Tap 69 kV Line - Before Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) - After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Baumhart-Elyria Waterworks Tap 69 kV Line Before Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Axtel-Baumhart 69 kV Line Before Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Axtel-Shinrock 69 kV Line Before Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Washington-Washington Tap 69 kV Line Before Proposed Solution: 45 / 54 / 51 / 65 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 67.65 |  |  | New Upgrade
PJM SOUTH | s3903.1 | Replace existing 115-13.2 kV 5 MVA TX #1 with 9.375 MVA at Disputanta Substation | Dominion |  |  | Customer Service |  |  | EP | 9/18/2025 | 9/18/2025 | 0.67 |  |  | New Upgrade
PJM SOUTH | s3913.1 | Modification of the existing EMC-EMC Mayo-Dunbar delivery point. The newly constructed DP will be adjacent to the existing Mayo-Dunbar DP. Would like to move the tap location one span over on the Dominion 80 Line to alleviate interference with new station exit feeders. Build a T-tap on the 115kV Line #80 (Beech Branch - Cool Springs) near structures #80/71 and #80/72. Install a switch on the Mayo Dunbar tap. The existing switches 8026 and 8029 are sufficient and remain unchanged. Customer is responsible for the cost associated with moving the tap. | Dominion |  |  | Customer Service |  |  | EP | 5/14/2026 | 5/14/2026 | 1.9 |  |  | New Upgrade
PJM SOUTH | s3911.1 | Rebuild approximately 6.36 miles single circuit of line#26 between Rockbridge to Buena Vista substation to current 115kV standards with a minimum summer rating of 393 MVA. Replace the line Switch with 2000A switch and associated equipment to current 115kV standards. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/14/2026 | 5/14/2026 | 15 |  |  | New Upgrade
PJM MA | s3822.1 | Burches Hill 230kV Breaker 2A, 2C, 3C, 4C | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/8/2025 | 12/8/2025 | 3.6 |  |  | New Upgrade
PJM MA | s3821.1 | Replace Riverside circuit breaker B53 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/4/2025 | 11/4/2025 | 0.8 |  |  | New Upgrade
PJM MA | s3820.1 | Replace Riverside circuit breaker B52 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/4/2025 | 11/4/2025 | 0.8 |  |  | New Upgrade
PJM MA | s3791.1 | Replacement of CB875 with SF6 circuit breaker, replacement of disconnect switches and associated CTs. The breaker short circuit ratings have been increased from 50 kA to 63 kA. | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/4/2025 | 11/4/2025 | 0.6 |  |  | New Upgrade
PJM MA | s3789.1 | Reconductor approximately 5 miles of 110541/110542 double circuit 115 kV tower line from High Ridge to Dorsey Run Tap on existing towers and 1.3 miles from Dorsey Run Tap to Crystal Springs Tap on existing poles with HTLS conductor. | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2025 | 11/13/2025 | 12.4 |  |  | New Upgrade
PJM WEST | n8169.1 | Construct Millikan 138 kV Station. associated line protection and control equipment, line risers, switches, jumpers, and SCADA at the Millikan 138 kV Station | AEP |  |  |  | 12/31/2022 | 11/22/2025 | Cancelled | 1/9/2024 | 1/9/2024 | 6.4897 |  |  | Cancelled
PJM WEST | n8169.2 | Install Two (2) Structures, Two (2) Spans of Conductor, Connect Millikan 138 kV Station to Existing Transmission Circuit, Update Remote End Protective Relay Settings | AEP |  |  |  | 12/31/2022 | 11/22/2025 | Cancelled | 1/9/2024 | 1/9/2024 | 0.7569 |  |  | Cancelled
PJM MA | s3787.1 | Replacement of CB785 and CB875 with SF6 circuit breakers, replacement of bus tie cable, and breaker disconnect switches. The breaker short circuit ratings have been increased from 42 kA to 63 kA. | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/18/2025 | 9/18/2025 | 0.9 |  |  | New Upgrade
PJM WEST | n8169.3 | Install Two (2) Fiber-Optic Paths to facilitate relaying between Millikan, Kenzie Creek, and Colby Tap 138 kV Stations | AEP |  |  |  | 12/31/2022 | 11/22/2025 | Cancelled | 1/9/2024 | 1/9/2024 | 0.2049 |  |  | Cancelled
PJM MA | s3786.1 | Replace obsolete electromechanical protective relays on the 220-17 Whitpain-Whitemarsh-Jenkintown 230 kV line with new microprocessor-based relays. New relays increase winter load dump ratings from 1036 MVA to 1092 MVA. | PECO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/9/2025 | 9/9/2025 | 3.6 |  |  | New Upgrade
PJM MA | s3784.1 | Install a new 8-position 230 kV breaker and a half substation by cutting into the existing Betzwood – Barbadoes 230 kV line. | PECO |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 27 |  |  | New Upgrade
PJM MA | s3807.1 | Phase 1: Install 2 temporary radial 230kV lines to the customer location by tapping into the existing 230kV 220-90 and 220-91 Emilie – Ford Mill lines to serve the initial 240 MW of customer load. Temporary feeds will be re-used in phase 2. Upgrade relays at Emilie substation. Install 7.5 miles of new OPGW static wire along length of existing structures. | PECO |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 3.9 |  |  | New Upgrade
PJM MA | s3730.2 | Phase 2: Install two new radial 230 kV feeds from the Planebrook #7 bus and #9 bus to the customers location. Reconductor approximately 1000ft of the 230-31 Bradford-Planebrook line. Install a breaker on the high side of transformer #9 at Planebrook substation. | PECO |  |  | Customer Service |  |  | EP | 3/4/2025 | 3/4/2025 | 7 |  |  | New Upgrade
PJM MA | s3730.1 | Phase 1: Install a temporary radial 230kV line from a tap off the Planebrook-Upper Merion-Tredyffrin line to the customers location. | PECO |  |  | Customer Service |  |  | EP | 3/4/2025 | 3/4/2025 | 0 | 0 |  | New Upgrade
PJM WEST | n8178.1 | Install new 138 kV three-breaker ring bus station along the Axton - Danville #1 138 kV line. Install a Drop-In Control Module (DICM) and other associated line protection and control equipment, line risers, switches, jumpers, and supervisory control and data acquisition (SCADA) equipment. | AEP |  |  |  | 5/31/2022 |  | Cancelled | 1/9/2024 | 1/9/2024 | 4.7008 |  |  | Cancelled
PJM WEST | n8178.2 | Perform final connection of the Axton - Danville #1 138 kV line to the Lendlease 138 kV Station, update remote end protective relay settings. | AEP |  |  |  | 12/31/2021 |  | Cancelled | 1/9/2024 | 1/9/2024 | 1.2555 |  |  | Cancelled
PJM WEST | n8178.3 | Install one (1) Fiber-Optic path to facilitate relaying between Lendlease and Axton 138 kV Stations | AEP |  |  |  | 12/31/2021 |  | Cancelled | 1/9/2024 | 1/9/2024 | 0.7635 |  |  | Cancelled
PJM SOUTH | s3883.1 | Construct 230kV Azalea Lane Substation, by cutting line 2210 | Dominion |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 56.5 |  |  | New Upgrade
PJM WEST | n8178.4 | Replace protective relays. | AEP |  |  |  | 12/31/2021 |  | Cancelled | 1/9/2024 | 1/9/2024 | 0.2433 |  |  | Cancelled
PJM WEST | n8178.5 | extend two (2) new fiber-optic connections from the AE2-140 proposed Lendlease 138 kV Station into AEP's existing fiber-optic network to facilitate SCADA network connectivity | AEP |  |  |  | 12/31/2021 |  | Cancelled | 1/9/2024 | 1/9/2024 | 0.1838 |  |  | Cancelled
PJM SOUTH | s4033.1 | Install one (1) 1200 Amp, 25kAIC circuit switcher and associated equipment to facilitate installation of a second 56 MVA, 115/34.5 kV transformer. | Dominion |  |  | Customer Service |  |  | EP | 7/7/2026 | 7/7/2026 | 1.3 |  |  | New Upgrade
PJM SOUTH | s4032.1 | Approved baseline projects PJM b4000.344 and b4000.345 will build a 500kV line from North Anna - Thornburg and Thornburg - Bristers. The new 500kV line will be constructed using 5/2 monopoles. Install 230kV conductor rated at 1573 MVA from North Anna to Bristers, bypassing Thornburg. The 230 kV line will be utilized to serve approximately 3 GW of requested load in the immediate transmission corridor, and the termination points will be presented with the associated requests. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 6/2/2026 | 6/2/2026 | 33.75 |  |  | New Upgrade
PJM SOUTH | s4031.2 | Cut and extend existing Line #2207 (Paragon - Beco) and terminate into the new substation. | Dominion |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 23.6 |  |  | New Upgrade
PJM SOUTH | s4031.1 | New Firehouse Substation to accommodate a 230kV ring bus with an ultimate configuration of four (4) breakers, with all breakers initially installed. | Dominion |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 40.7 |  |  | New Upgrade
PJM SOUTH | s4030.2 | Interconnect the new substation by cutting and extending Lines #2081 and #2150 (Paragon Park - Golden - Sterling Park) into the proposed Auto World 230kV Substation. | Dominion |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 8.3 |  |  | New Upgrade
PJM SOUTH | s4030.1 | New Auto World Substation to accommodate a GIS six-breaker ring bus arrangement. | Dominion |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 23.5 |  |  | New Upgrade
PJM SOUTH | s4029.2 | Construct two new New Post - Emy 230 kV transmission lines. Reconfigure both 230 kV lines passing by Emy and New Post so that both are looped through the campus. These will be future lines #2404 (Tributary - New Post) and #2372 (Thornburg - New Post). | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 6 |  |  | New Upgrade
PJM SOUTH | s4029.1 | Construct Emy 230 kV substation with a 6-breaker ring bus configuration. Add two new 230 kV breakers at New Post substation to accommodate New Post - Emy lines. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 20 |  |  | New Upgrade
PJM WEST | s4025.4 | Add a new 138 kV circuit breaker to Polaris station to improve sectionalizing towards Maliszewski and the existing Distribution equipment. The breaker addition also drives the need for a new control house. | AEP |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 4.0123 |  |  | New Upgrade
PJM WEST | s4025.3 | Install five new 138 kV, 63 kA circuit breakers to accommodate the new distribution transformer at Maliszewski station. | AEP |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 7.0085 |  |  | New Upgrade
PJM WEST | s4025.2 | Remote end relay settings work to allow work at Maliszewski 138 kV | AEP |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 0.66691 |  |  | New Upgrade
PJM WEST | s4025.1 | Re-terminate the Polaris - Maliszewski 138 kV circuit between Breaker P1 and New Breaker P at Maliszewski station. | AEP |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 0.8818 |  |  | New Upgrade
PJM WEST | s4024.2 | Install ~0.35 miles of 138kV line from Muskingum to customer station | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 2.6971 |  |  | New Upgrade
PJM WEST | s4024.1 | Install a new 138kV breaker at Muskingum River 138kV on bus #1 to facilitate extension to customer site | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 3.0848 |  |  | New Upgrade
PJM WEST | s4023.5 | To support this customers anticipated load ~0.30 miles of 138 kV line on the South Canton - Timken Richville circuit will be reconductored utilizing 1033.5 ACSS 54/7 Curlew (SE 557). | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 1.5 |  |  | New Upgrade
PJM WEST | s4023.4 | To support this customers anticipated load ~1.42 miles of double circuit 138 kV line on the South Canton - Timken Richville & Timken Richville - Torrey circuits will be rebuilt utilizing 1033.5 ACSS 54/7 Curlew (SE 557). | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 13.49 |  |  | New Upgrade
PJM WEST | s4023.3 | Install (2) ~0.1 mile customer feeds from Petros station utilizing 795 kcmil 26/7 "Drake" ACSS (SE 492). | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 0.50165 |  |  | New Upgrade
PJM WEST | s4023.2 | Cut into the South Canton - Torrey 138 kV line with a ~2.00 mile double circuit line utilizing 795 kcmil 26/7 "Drake" ACSS (SE 492), to accommodate the greenfield Petros Station. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 19.5996 |  |  | New Upgrade
PJM WEST | s4023.1 | Construct a greenfield breaker and a half station operated as a ring bus with (4) 138 kV 3000A 63 kA circuit breakers. | AEP |  |  | Customer Service |  |  | EP | 5/15/2026 | 5/15/2026 | 14.0326 |  |  | New Upgrade
PJM WEST | s4022.5 | Install (1) ~0.02-mile customer feed from Triton station utilizing 1272 ACSR 54/19 Pheasant (SE 481 MVA) | AEP |  |  | Customer Service |  |  | EP | 4/15/2026 | 4/15/2026 | 0.073634 |  |  | New Upgrade
PJM WEST | s4022.4 | Install (1) ~0.02-mile customer feed from Triton station utilizing 1272 ACSR 54/19 Pheasant (SE 481 MVA) | AEP |  |  | Customer Service |  |  | EP | 4/15/2026 | 4/15/2026 | 0.073634 |  |  | New Upgrade
PJM WEST | s4022.3 | Construct a greenfield ~0.81-mile double circuit 138 kV line between Canton Central and the greenfield Triton station utilizing 1272 ACSR 54/19 Pheasant (SE 481 MVA). To accommodate this greenfield line the Canton Central - Wagenhals and Tidd - Wagenhals 138 kV lines will be raised. | AEP |  |  | Customer Service |  |  | EP | 4/15/2026 | 4/15/2026 | 7.715 |  |  | New Upgrade
PJM MA | n8193.1 | Install fiber from AE2-344 to Edinboro South for communication transport. | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.3961 |  | 2/26/2025 | Cancelled
PJM MA | n8193.10 | Morgan Street Substation: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.5863 |  | 2/26/2025 | Cancelled
PJM WEST | s4022.2 | Construct a greenfield breaker and a half station operated as a ring bus with (4) 138 kV 4000A 63 kA circuit breakers. | AEP |  |  | Customer Service |  |  | EP | 4/15/2026 | 4/15/2026 | 11.0667 |  |  | New Upgrade
PJM MA | n8193.2 | Design, install, and test/commission MPLS Equipment for SCADA transport. | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.1927 |  | 2/26/2025 | Cancelled
PJM MA | n8193.3 | Edinboro South-Morgan Street-Springboro 115kV Line Loop: Loop from the MF1/MFS (Edinboro South-Morgan Street-Springboro) 115kV line to the new AE2-344 interconnection substation. | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.9651 |  | 2/26/2025 | Cancelled
PJM WEST | s4022.1 | Expand Canton Central with the installation of (3) 138 kV 4000A 63kA circuit breakers. | AEP |  |  | Customer Service |  |  | EP | 4/15/2026 | 4/15/2026 | 3.0321 |  |  | New Upgrade
PJM MA | n8193.4 | Edinboro South: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.5471 |  | 2/26/2025 | Cancelled
PJM MA | n8193.5 | Wayne Substation: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.0332 |  | 2/26/2025 | Cancelled
PJM WEST | s4021.2 | Install ~0.25 miles of 1590 KCM 54/19 FALCON ACSS conductor on the open side of the double circuit structures which will be installed with AEP-2024-OH040. | AEP |  |  | Customer Service |  |  | EP | 1/16/2026 | 1/16/2026 | 0.53192 |  |  | New Upgrade
PJM MA | n8193.6 | GenevaSubstation: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.5264 |  | 2/26/2025 | Cancelled
PJM MA | n8193.7 | Erie West Substation: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.2069 |  | 2/26/2025 | Cancelled
PJM WEST | s4021.1 | Install 1 - 138 kV 3000A 63 kA circuit breaker in addition to the 3 being installed with AEP-2024-OH040, to accommodate the additional customer feed. | AEP |  |  | Customer Service |  |  | EP | 1/16/2026 | 1/16/2026 | 1.3436 |  |  | New Upgrade
PJM MA | n8193.8 | Erie South Substation: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.2069 |  | 2/26/2025 | Cancelled
PJM MA | n8193.9 | Springboro Substation: Line Terminal Upgrade | PENELEC |  |  |  |  | 3/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.5183 |  | 2/26/2025 | Cancelled
PJM WEST | s4011.1 | Replace Cherry Valley 138 kV 1-2 circuit breaker. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 2.6 |  |  | New Upgrade
PJM WEST | s4010.1 | Replace existing 345 kV oil BT 5-6 circuit breaker at Plano with a new 345 kV gas circuit breaker, and replace 3 motor operated disconnects. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/4/2025 | 11/4/2025 | 3.9 |  |  | New Upgrade
PJM WEST | s4008.1 | Replace existing 345 kV oil BT 1-2 circuit breaker with a new gas circuit breaker at Lockport. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/8/2025 | 10/8/2025 | 2.2 |  |  | New Upgrade
PJM WEST | s4007.1 | Replace 138 kV line L1205 circuit switcher from Mazon to ESS J375 tap. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 0.4 |  |  | New Upgrade
PJM WEST | n8196.2 | * Scope replaced by B3851* Replace an additional existing double circuit towers with steel double circuit single pole structures on the Allen - RPMone 345kV line. New rating is 1301 MVA Rate B. Scope is from the Facility Study results of the N6740 Sag Study for AE1-113. | AEP | [5 empty] | Cancelled | [5 empty] | Scope/Cost Change
PJM MA | n8198.1 | Install (3) 34.5 kV load-break air switches with SCADA control on the Cookstown – New Lisbon (W75) 34.5 kV line approximately 0.3 miles from the Fort Dix W75 Tap and 3.1 miles from the Hanover Solar Tap (at structures 116 & 117). | JCPL |  |  |  |  | 6/1/2025 | Cancelled | 10/3/2023 | 10/3/2023 | 0.3643 |  | 11/18/2025 | Cancelled
PJM MA | n8198.2 | Review Cookstown line relay settings as required for AF2-254 tap. @ New Lisbon | JCPL |  |  |  |  | 6/1/2025 | Cancelled | 10/3/2023 | 10/3/2023 | 0.041 |  | 11/18/2025 | Cancelled
PJM MA | n8198.3 | Review New Lisbon line relay settings as required for AF2-254 tap. @ Cookstown | JCPL |  |  |  |  | 6/1/2025 | Cancelled | 10/3/2023 | 10/3/2023 | 0.041 |  | 11/18/2025 | Cancelled
PJM WEST | s4006.1 | Replace existing 138 kV line L1206 circuit switcher from Channahon to ESS J375 tap. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 0.4 |  |  | New Upgrade
PJM SOUTH | s4005.1 | Extend two new 230 kV lines from New Post to Emy. Add two new 230 kV breakers at New Post substation to accommodate the new lines. Cut two 230 kV lines into Emy from the South. The lines cut will be future Lines #2404 (Tributary – New Post) and #2372 (Kraken – New Post). | Dominion |  |  | Customer Service |  |  | Cancelled | 2/3/2026 | 2/3/2026 | 26 |  |  | Cancelled
PJM SOUTH | s4004.1 | Construct new Firehouse Substation to accommodate a 230kV ring bus with an ultimate configuration of four (4) breakers, with all breakers initially installed. Cut and extend existing Line #2207 (Paragon - Beco) and terminate into the new substation | Dominion |  |  | Customer Service |  |  | Cancelled | 4/7/2026 | 4/7/2026 | 64.3 |  |  | Cancelled
PJM SOUTH | s4003.1 | Interconnect the new substation by cutting and extending Lines #2081 and #2150 (Paragon Park – Golden – Sterling Park) into the proposed Auto World 230kV Substation. The lines will terminate in a 230kV GIS six-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | Cancelled | 4/7/2026 | 4/7/2026 | 31.8 |  |  | Cancelled
PJM SOUTH | s4002.1 | Approved baseline projects PJM b4000.344 and b4000.345 will build a 500kV line from North Anna - Thornburg and Thornburg - Bristers. The new 500kV line will be constructed using 5/2 monopoles. Install 230kV conductor rated at 1573 MVA from North Anna to Bristers, bypassing Thornburg. The 230 kV line will be utilized to serve approximately 3 GW of requested load in the immediate transmission corridor, and the termination points will be presented with the associated requests. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | Cancelled | 6/2/2026 | 6/2/2026 | 33.75 |  |  | Cancelled
PJM SOUTH | n8205.1 | Build a three breaker AF2-222 115 kV switching station. | Dominion |  |  |  | 5/31/2023 | 2/1/2025 | EP | 11/3/2026 | 11/3/2026 | 7.972 |  |  | New Upgrade
PJM SOUTH | n8205.2 | Re-arrange line #154 to loop into and out of the new three breaker AF2-222 115 kV switching station | Dominion |  |  |  | 5/31/2023 | 2/2/2025 | EP | 11/3/2026 | 11/3/2026 | 3.98 |  |  | New Upgrade
PJM SOUTH | s4001.1 | Install one (1) 1200 Amp, 63kAIC circuit switcher and associated equipment to facilitate installation of a second 84 MVA, 230/34.5 kV transformer. | Dominion |  |  | Customer Service |  |  | EP | 7/7/2026 | 7/7/2026 | 1.6 |  |  | New Upgrade
PJM SOUTH | n8205.3 | Remote protection and communication work. | Dominion |  |  |  | 5/31/2023 | 2/3/2025 | Cancelled | [5 empty] | Scope/Cost Change
PJM SOUTH | s4000.2 | Tap Line #71 (Brodnax - Clubhouse) near structure 71/44 and extend a 115kV tap to Lewis Drive DP. | Dominion |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 5.3 |  |  | New Upgrade
PJM SOUTH | s4000.1 | Construct a 115kV Substation at the proposed site for Lewis Drive to be served by the Line #71 extension. | Dominion |  |  | Customer Service |  |  | EP | 7/17/2026 | 7/17/2026 | 0 |  |  | New Upgrade
PJM SOUTH | s3999.6 | Terminal Equipment Upgrades at Chickahominy associated with new 230 kV Terminations | Dominion |  |  | Operational Flexibility and Efficiency |  |  | Deactivated | 5/5/2026 | 5/5/2026 | 6.665 |  |  | New Upgrade
PJM SOUTH | s3999.5 | Terminal Equipment Upgrades at Elmont associated with new 230 kV Terminations | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 6.665 |  |  | New Upgrade
PJM SOUTH | s3999.4 | Terminal Equipment Upgrades at Thornburg associated with new 230 kV Terminations | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 6.67 |  |  | New Upgrade
PJM SOUTH | s3999.3 | Terminate one 230kV conductor rated at 1573 MVA at Thornburg and Chickahominy. Conductor is being installed on 500kV Line #557 5/2 structures being rebuild under 2021 Open Window End of Life project b3692. Note: 2025 Open Window Project b3692 will rebuild 500kV Line #557 as 5/2 structures, and the 230kV conductor is being strung but not terminated in that baseline project. Terminate the 230kV circuit under this supplemental project at Chickahominy. Final configuration will be two 230kV circuits from Thornburg to Elmont, one 230kV circuit from Thornburg to Chickahominy, one 230kV circuit from Elmont to Chickahominy. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 55 |  |  | New Upgrade
PJM SOUTH | s3999.2 | Install one 230kV conductor rated at 1573 MVA on open arms of existing 230kV Line #2075 from Elmont to Chickahominy. Note: This is the 2nd 230 kV circuit on each tower. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 55 |  |  | New Upgrade
PJM SOUTH | s3999.1 | Install one 230kV conductor rated at 1573 MVA on the both 5/2 double circuit structures from Thornburg to Elmont. Note: this is the 2nd 230 kV circuit on each tower. Previously presented Do No Harm supplemental project DOM-2023-0016, 0053, 0055, 2024-0012 will wreck and rebuild 230kV line 256/2032 (Thornburg-Elmont) with double circuit structures and 115kV line #47 (Fredericksburg-Four Rivers) and line #73 (Four Rivers-Elmont) with double circuit structures. Update - 115kV Line 47/73 from Thornburg to Elmont will be constructed as 5/2 structures instead of 2/2 structures per approved 2025 Open Window project b4053.8, 9, 10. The 500kV cost will be allocated to the PJM Zone while the 230kV cost will be allocated to the DOM Zone. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 55 |  |  | New Upgrade
PJM SOUTH | s3998.1 | - DP Request (upgrade distribution TX#2) triggers transmission project to meet current substation engineering standards for high-side protection of distribution TXs - Replace existing 1200A high-side switch H234 to 2000A MOAB switch | Dominion |  |  | Customer Service |  |  | EP | 5/14/2026 | 5/14/2026 | 0.33 |  |  | New Upgrade
PJM SOUTH | s3995.2 | Proposed Stockholm Substation will cut future Line 2075 and Line 2294. | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 6 |  |  | New Upgrade
PJM SOUTH | s3995.1 | Proposed Stockholm Substation will tap future Line 2075 and Line 2294, and lines will terminate in a 230kV six breaker ring bus arrangement. Proposed Stockholm Substation will have a 75 MVAR cap bank. | Dominion |  |  | Customer Service |  |  | EP | 5/5/2026 | 5/5/2026 | 20 |  |  | New Upgrade
PJM SOUTH | s3994.2 | Cut existing 230kV Line 2032 between Hanover and Four Rivers and extend a new 230kV double circuit loop, approximately .5 miles, in and out of Slayden Creek Substation. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 6 |  |  | New Upgrade
PJM SOUTH | s3994.1 | Slayden Creek Substation will be constructed with a 230 kV ring-bus, configured for an ultimate arrangement of six breakers, with four breakers installed initially. | Dominion |  |  | Customer Service |  |  | EP | 3/10/2026 | 3/10/2026 | 20 |  |  | New Upgrade
PJM SOUTH | s3993.2 | Cut double-circuit New Post to Lee's Hill lines south of Cosner and Lee's Hill and terminate at Cosner, removing the existing line terminations at Lee's Hill. Extend two new 230 kV lines from Lee's Hill to Cosner. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 6 |  |  | New Upgrade
PJM SOUTH | n8213.1 | Re-arrange line #65 to loop into and out of the new three breaker AG1-135 115 kV switching station | Dominion |  |  |  | 12/1/2024 | 3/1/2026 | IS | 11/3/2026 | 11/3/2026 | 2.825 |  |  | New Upgrade
PJM SOUTH | n8213.2 | Build a three breaker AG1-135 115 kV switching station. | Dominion |  |  |  | 12/1/2024 | 3/2/2026 | IS | 11/3/2026 | 11/3/2026 | 7.995 |  |  | New Upgrade
PJM SOUTH | n8213.3 | Remote protection and communication work. | Dominion |  |  |  | 12/1/2024 | 3/3/2026 | IS | 11/3/2026 | 11/3/2026 | 0.305 |  |  | New Upgrade
PJM SOUTH | s3993.1 | Construct new Cosner 230 kV substation with a 6-breaker ring bus configuration. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 20 |  |  | New Upgrade
PJM SOUTH | s3991.2 | Extend two 230 kV lines approximately one mile from Orrock (Matta) to Mudd Tavern. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 7 |  |  | New Upgrade
PJM SOUTH | s3991.1 | Mudd Tavern Substation will be constructed with a 230 kV ring-bus, configured for an ultimate arrangement of six breakers, with four breakers installed initially. | Dominion |  |  | Customer Service |  |  | EP | 2/3/2026 | 2/3/2026 | 15 |  |  | New Upgrade
PJM WEST | s3980.1 | Construct a new four-breaker (future five-breaker) 138 kV station, cut into the Bredenville - Kilgo 138 kV Line and loop the line in and out of the new ring bus station. Construct two 138 kV spans from the new ring bus station to the POI with the Customer. Transmission Line Ratings: 287 / 287 / 287 / 287 MVA (SN/SSTE/WN/WSTE) Transformer Ratings: N/A | APS |  |  | Customer Service |  |  | EP | 3/19/2026 | 3/19/2026 | 22.75 |  |  | New Upgrade
PJM WEST | s3959.3 | Remote end relaying work to accommodate new breaker at Timken Mercy | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/17/2026 | 7/17/2026 | 0.221 |  |  | New Upgrade
PJM WEST | s3959.2 | Retermination of t-line into the rebuilt station ~0.05 miles of line work utilizing 1033.5 KCM ACSR 54/7 Curlew (SE 206) | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/17/2026 | 7/17/2026 | 1.4737 |  |  | New Upgrade
PJM WEST | s3959.1 | Rebuild the existing station in the clear as a In-Out Box Bay with (2) 2000A switches on the line exits and a (1) 69 kV 3000A 40 kA bus tie circuit breaker | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/17/2026 | 7/17/2026 | 5.5001 |  |  | New Upgrade
PJM MA | n8220.1 | Complete FRAC-FISH 69 kV line modifications to tie in the new AF2-445A Attachment Facilities. Intersperse a new custom foundation steel tap structure at the POI. Reframe/modify existing structures on each side of the new tap structure if required. | PPL |  |  |  | 6/1/2021 | 7/25/2024 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | n8220.2 | Relay Modifications Scope of Work at Frackville Substation | PPL |  |  |  | 6/1/2021 | 7/25/2024 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | s3958.8 | Retire the ~7.6 mile Gavin - Addison 69 kV line. | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 6.4066 |  |  | New Upgrade
PJM WEST | n8221.1 | Construct a new 69 kV 3 breaker ring bus on the Cardington-Tangy 69 kV line. | ATSI |  |  |  | 11/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 5.7771 |  | 2/26/2025 | Cancelled
PJM WEST | n8221.2 | Design, install, and test/commission MPLS Equipment for SCADA transport. | ATSI |  |  |  | 11/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.2616 |  | 2/26/2025 | Cancelled
PJM WEST | s3958.7 | Extend double circuit 138kV line (0.2 miles) from Gavin-North Proctorville 138kV line into Chickamauga to establish new path to Haners/Addison | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 4.6274 |  |  | New Upgrade
PJM WEST | n8221.3 | Loop the Cardington-Tangy 69kV line to create the interconnection for the new AF1-122 3-breaker ring bus, approximately 1.1 miles from the Cardington substation. Install fiber from the new AF1-122 3-breaker ring bus to the Cardington substation. | ATSI |  |  |  | 11/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 1.1442 |  | 2/26/2025 | Cancelled
PJM WEST | n8221.4 | Relay Settings Changes, Drawing Updates, and Nameplates. | ATSI |  |  |  | 11/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.0628 |  | 2/26/2025 | Cancelled
PJM WEST | n8221.5 | Upgrade line relaying. | ATSI |  |  |  | 11/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.5597 |  | 2/26/2025 | Cancelled
PJM WEST | s3958.6 | Build a greenfield Chickamauga station a 138 kV 3-breaker ring bus. | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 11.9026 |  |  | New Upgrade
PJM WEST | s3958.5 | Install 3-way switch on the new Addison - Chickamauga 138kV line to feed Haners station. Replace the Distribution 69/13.09 kV 25MVA transformer at Haners with a 138/13.08 kV 25 MVA non-LTC transformer fed from the 3-way switch on the new Addison - Chickamauga 138kV line. | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 2.3749 |  |  | New Upgrade
PJM WEST | s3958.4 | Remove the ~4.18 mile Addison - Haners 138kV line and rebuild as the Addison - Chickamauga 138 kV ~4.72 mile line. | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 22.3805 |  |  | New Upgrade
PJM WEST | s3958.3 | Rebuild the 138kV side of Addison Station as a 3-breaker ring bus. The new Addison station will be constructed on existing property in the clear. The 69 kV side will be removed. Rebuild the 12kV side and add a 4th distribution feeder | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 11.8225 |  |  | New Upgrade
PJM WEST | n8240.2 | Install two (2) Dead End Structures, two (2) Spans of Conductor, Connect ITO 138 kV Station to existing Columbia (AEP) - Northeast (NIPSCO) 138kV Circuit | AEP |  |  |  | 7/31/2021 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | s3958.2 | Rebuild Rio as a 5 breaker ring bus to accommodate the new circuit going to Sporn 138kV | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 10.5067 |  |  | New Upgrade
PJM WEST | n8240.3 | Install One (1) New Fiber-Optic Cable Path to Facilitate MUX based relaying between the Proposed ITO 138 kV Station and Columbia 138 kV Station. | AEP |  |  |  | 7/31/2021 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8240.4 | Upgrade Protective Relays, Install SFP Transceiver, Remove existing Wavetrap at the Columbia 138 kV Station | AEP |  |  |  | 7/31/2021 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | s3958.1 | Rebuild 29.02 miles of the 138kV Lick-Addison line | AEP |  |  | Customer Service^Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 95.7052 |  |  | New Upgrade
PJM WEST | s3957.1 | Install a 69 kV 40 kA circuit breaker on the low side of the 138/69 kV transformer #8 at Kenova Substation. | AEP |  |  | Customer Service |  |  | EP | 6/17/2026 | 6/17/2026 | 0.6 |  |  | New Upgrade
PJM WEST | s3956.1 | Rebuild ~73.9 miles of the existing Tanners Creek-Junction Tower 345kV line asset as 345 kV single circuit utilizing 2-bundle 954 ACSR 54/7 Cardinal conductor. Rebuild ~5.65 miles of the existing Hanna-Junction Tower 345 kV line asset as double circuit line with the conductor size 2-bundle 954 ACSR 54/7 Cardinal. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/2/2026 | 6/2/2026 | 520 |  |  | New Upgrade
PJM WEST | s3955.6 | Replace the bus conductor on bus #1 and #2. Replace the station fence and update relay settings. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 0.205 |  |  | New Upgrade
PJM WEST | s3955.5 | Setting updates to support the 69kV line rebuild | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 0.05 |  |  | New Upgrade
PJM WEST | s3955.4 | Raising four 138kV line structures due to two crossings of the 69kV double circuit rebuild. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 1.1 |  |  | New Upgrade
PJM WEST | s3955.3 | Replace the existing Memorial Drive phase over phase switching structure. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 0.697 |  |  | New Upgrade
PJM WEST | s3955.2 | Retire 3.0 miles of 69kV line from West Lancaster to Memorial Drive station. Build 1.4 miles of greenfield single circuit 69kV line from where the West Lancaster - Anchor Hocking and West Lancaster - Memorial Drive lines were double circuit. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 11.1 |  |  | New Upgrade
PJM WEST | s3955.1 | Retire 1.3 miles of 69kV line from West Lancaster to Anchor Hocking station. Rebuild 3.2 miles of 69kV line from West Lancaster to Anchor Hocking stations. 2 miles of the rebuild will be double circuit that includes the West Lancaster - Memorial Drive 69kV line. The remaining 1.2 miles will be single circuit line before entering Anchor Hocking station. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 20.7 |  |  | New Upgrade
PJM WEST | s3954.4 | Replacing jumpers on Big Sandy Line. Big Sandy Line Trap, CCVT, and Tuner will be replaced. Replacement of associated control cables. Update relay settings at Thelma substation. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 1.1 |  |  | New Upgrade
PJM WEST | s3954.3 | Relay settings update at Big Sandy Substation | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 0.055 |  |  | New Upgrade
PJM WEST | s3954.2 | Rebuild the 7 mile long section of Big Sandy - Busseyville 138 kV line. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 48.4 |  |  | New Upgrade
PJM WEST | s3954.1 | Rebuild the 19 mile long 138 kV line from Thelma - Busseyville. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 120 |  |  | New Upgrade
PJM WEST | s3953.2 | Replace the Lincolnway 3 way POP switch with a new 3 way pop switch called Conrail SW | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 1.7432 |  |  | New Upgrade
PJM WEST | s3953.1 | Rebuilding 12.39 miles of the Illinois Rd - Gateway 69kV transmission line with steel poles and 556 ACSR conductor. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 53.8847 |  |  | New Upgrade
PJM WEST | s3952.3 | Rebuild 11.01 mile single circuit 138kV line to replace the existing single circuit 138kV line between East Lynn - Lavalette. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 60.6 |  |  | New Upgrade
PJM WEST | s3952.2 | Rebuild 4.7 mile single circuit 138kV line to replace the existing single circuit 138kV line between Structure 160-16 and Lavalette station. Structure 160-16 is a newer tower installed in 2009 and will not be replaced as part of this project. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 25.3 |  |  | New Upgrade
PJM WEST | s3952.1 | Rebuild 2.26 mile single circuit 138kV line to replace the existing single circuit 138kV line between Tri-State and existing structure 160-16 located in WV. Structure 160-16 is a newer tower installed in 2009 and will not be replaced as part of this project. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 12.9 |  |  | New Upgrade
PJM WEST | s3947.1 | Phase I: Medina-Medina Industries-Seville 69 kV Line Upgrade Project -Build a new ~7.5 miles 69 kV line with new conductor to extend the Medina industries 69 kV line from/at Carlisle Brake & Friction to Seville Substation and terminate the line at Seville Substation. Line will be built in a separate ROW from Ryan-Seville 138 kV Line. This phase will create the Medina-Seville 69 kV Line. The new line construction will be from Seville Substation to Carlisle Brake & Friction Tap. -Rebuild the existing Medina Industries radial 69 kV line (~3.3 miles) from str# 373 to 17D with new conductor. The rebuild construction will be from Carlisle Brake & Friction Tap to just east of Plastipak Tap. -Convert the 69 kV yard at Seville Substation into a five-breaker ring bus. -Add switches at all Medina-Seville 69 kV Line main line tap points. Phase II: West Medina Substation Project -Convert 138 kV yard at West Medina Substation into a five-breaker ring bus. -Add a new 69 kV four-breaker ring bus at West Medina Substation. -Add a 138/69 kV Transformer at West Medina Substation. -Add high side distribution transformer breaker at West Medina Substation. -Loop the Abbe - Medina 69 kV Line into the 69 kV ring bus at West Medina Substation, creating the Abbe-West Medina 69 kV Line and Medina-West Medina 69 kV Line. -Rebuild the Abbe-Medina 69 kV Line from str# 373 to str# 369/368 (~0.2 miles) as a double circuit 69 kV line with new conductor, to reroute the Medina - Seville 69 kV Line into the 69 kV yard at the West Medina Substation. This will create the Seville-West Medina 69 kV Line. (The Medina-Seville 69 kV line will be operated normally open at str#373A/374). -Reroute the Medina-Seville 69 kV Line from the Medina Substation into the 69 kV ring bus into the West Medina Substation using the newly built line from str# 373 to str# 369/368. -Add a 1200A switch at str# 373/372 on the Seville-West Medina 69 kV Line. -Add a 1200A normally open switch at str# 373A/374 on the Medina-Seville 69 kV Line. Phase III: Medina 69 kV Breaker-and-a-Half Project - Convert the 69 kV yard at West Medina Substation into a breaker-and-a-half configuration. Transmission Line Rating Changes: Medina-Seville 69 kV Line: Industry Tap-Medina 69 kV Branch: Before Proposed Solution: 45 / 46 / 51 / 51 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Industry Tap-Plastipk Tap 69 kV Branch: Before Proposed Solution: 45 / 54 / 51 / 65 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Plastipk Tap - TLT Babck Tap 69 kV Branch: Before Proposed Solution: 45 / 54 / 51 / 65 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Par-Pkg Spec Tap-TLT Babck Tap 69 kV Branch: Before Proposed Solution: 45 / 54 / 51 / 65 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Par-Pkg Spec Tap - Ravago Tap 69 kV Branch: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Heritage Tap-Ravago Tap 69 kV Branch: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Carlisle Brake & Friction Tap-Heritage Tap 69 kV Branch: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Carlisle Brake & Friction Tap - Seville 69 kV Branch: Before Proposed Solution: N/A After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) West Medina 138/69 kV Transformer Circuit: Before Proposed Solution: N/A After Proposed Solution: 175 / 184 / 210 / 228 MVA (SN/SE/WN/WE) Industry Tap-West Medina 69 kV Branch: Before Proposed Solution: N/A After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Sun Oil Tap-West Medina 69 kV Branch: Before Proposed Solution: N/A After Proposed Solution: 100 / 121 / 113 / 143 MVA (SN/SE/WN/WE) Medina Tap-West Medina 69 kV Branch: Before Proposed Solution: N/A After Proposed Solution: 100 / 121 / 113 / 143 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 7/17/2026 | 7/17/2026 | 97.83 |  |  | New Upgrade
PJM WEST | s3946.1 | At Dixie Substation, replace three 69 kV breakers (B6903, B6904, and B6923), seven disconnect switches, 69 kV bus PTs, station conductor, strain bus and brown insulators, and relays for the line towards Jeep. Transmission Line Ratings: Dixie-Perstorp 69 kV Line Before Proposed Solution: 107 / 134 / 139 / 154 MVA (SN/SE/WN/WE) After Proposed Solution: 139 / 171 / 164 / 210 MVA (SN/SE/WN/WE) Dixie-Teledyne 69 kV Line Before Proposed Solution: 107 / 136 / 129 / 164 MVA (SN/SE/WN/WE) After Proposed Solution: 111 / 136 / 129 / 164 MVA (SN/SE/WN/WE) Dixie-Omni 69 kV Line Before Proposed Solution: 107 / 138 / 140 / 166 MVA (SN/SE/WN/WE) After Proposed Solution: 121 / 148 / 140 / 179 MVA (SN/SE/WN/WE) Transformer Ratings: Dixie No. 6 138/69 kV Transformer Before Proposed Solution: 187 / 241 / 267 / 298 MVA (SN/SSTE/WN/WSTE) After Proposed Solution: 305 / 305 / 383 / 383 MVA (SN/SSTE/WN/WSTE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 3.43 |  |  | New Upgrade
PJM MA | n8313.1 | Install Tap Pole | PENELEC |  |  |  | 3/17/2020 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.0236 |  | 2/26/2025 | Cancelled
PJM MA | n8313.2 | Haynie: Revise Relay Settings | PENELEC |  |  |  | 3/17/2020 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.2727 |  | 2/26/2025 | Cancelled
PJM WEST | s3945.1 | Replace 138 kV breaker B-4 and three switches at Bulk Mail Facility Station. Transmission Line Ratings: Bulk Mail Facility-Pine 138 kV Line Before Proposed Solution: 232 / 287 / 287 / 287 MVA (SN/SE/WN/WE) After Proposed Solution: 265 / 316 / 326 / 361 MVA (SN/SE/WN/WE) Bulk Mail Facility-Fernway 138 kV Line Before Proposed Solution: 232 / 287 / 287 / 287 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 1.69 |  |  | New Upgrade
PJM MA | n8313.3 | Emlenton: Revise Relay Settings | PENELEC |  |  |  | 3/17/2020 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.2727 |  | 2/26/2025 | Cancelled
PJM WEST | s3944.1 | At Pemberville Station, replace two 69 kV breakers (7286 and 7287), four disconnect switches, and line relays. Transmission Line Ratings: Pemberville-Maclean 69 kV Line Before Proposed Solution: 116 / 143 / 143 / 143 MVA (SN/SE/WN/WE) After Proposed Solution: 139 / 169 / 158 / 201 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/17/2026 | 4/17/2026 | 3.46 |  |  | New Upgrade
PJM WEST | s3943.1 | Retire the capacitor bank, breaker B65, switch D65, and associated relays at Crestline Station. | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/17/2026 | 4/17/2026 | 0.44 |  |  | New Upgrade
PJM WEST | s3942.1 | At Chrysler Station, replace three 138 kV breakers (B13290, B13291 and B13292), eight 138 kV disconnect switches, two CCVT's, and wavetraps/tuners. Transmission Line Ratings: Chrysler-Shelby 138 kV Line Before Proposed Solution: 278 / 343 / 327 / 396 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 343 / 327 / 420 MVA (SN/SE/WN/WE) Chrysler-First Solar 138 kV Line Before Proposed Solution: 288 / 346 / 333 / 396 MVA (SN/SE/WN/WE) After Proposed Solution: 288 / 353 / 333 / 427 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/17/2026 | 4/17/2026 | 2.76 |  |  | New Upgrade
PJM WEST | s3941.1 | Replace breakers B-20, B-21 and B-22 and associated disconnect switches at Rockaway Substation. Transmission Line Ratings Rockaway - OS Kelly 69 kV Line: Before Proposed Solution: 62 / 62 / 62 / 62 MVA (SN/SE/WN/WE) After Proposed Solution: 76 / 92 / 87 / 111 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/17/2026 | 4/17/2026 | 3.43 |  |  | New Upgrade
PJM WEST | s3940.1 | Convert Nursery Substation 138 kV yard to breaker-and-a-half configuration. Reterminate the existing 138-36 kV transformers and Queen 138-13.2 kV transformer into the new 138 kV bus. Loop the existing Grand River - Leroy Center 138 kV No. 1 Line into the Nursery Substation 138 kV yard. Cut the Grand River - Leroy Center 138 kV No. 1 Line between structures 1172-W and 1172-C and cut the Grand River - Leroy Center 138 kV No. 2 Line extension on structure 1172-W and reterminate it on structure 1172-C. This will create Grand River - Nursery 138 kV and Nursery - Leroy Center 138 kV. Transmission Line Ratings Before Proposed Solution: Existing Painesville Muni Tap-Nursery Tap 138 kV Q15 Transmission Line and Conductor Ratings: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Existing Nursery Tap-Nursery 138 kV Q15 Transmission Line and Conductor Ratings: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Existing Nursery Tap-Painesville Muni 2 Tap 138 kV Q15 Transmission Line and Conductor Ratings: 273 / 332 / 309 / 393 MVA (SN/SE/WN/WE) Existing Painesville Muni Tap-Nursery Tap 138 kV Q16 Transmission Line and Conductor Ratings: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Existing Nursery Tap-Nursery 138 kV Q16 Transmission Line and Conductor Ratings: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Existing Nursery Tap-Painesville Muni 2 Tap 138 kV Q16 Transmission Line and Conductor Ratings: 273 / 332 / 309 / 393 MVA (SN/SE/WN/WE) Transmission Line Ratings After Proposed Solution: Proposed Painesville Muni Tap-Painesville Muni Tap 2 138 kV Q16 Transmission Line and Conductor Ratings: 273 / 332 / 309 / 393 MVA (SN/SE/WN/WE) Proposed Painesville Muni Tap-Nursery 138 kV Q15 Transmission Line and Conductor Ratings: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Proposed Nursery-Painesville Muni 2 Tap 138 kV Q15 Transmission Line and Conductor Ratings: 273 / 332 / 309 / 393 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | EP | 4/17/2026 | 4/17/2026 | 25.58 |  |  | New Upgrade
PJM WEST | s3939.1 | Rebuild the 7.6 miles of the wood section of Gordon - Nyswaner 138 kV Line from Nyswaner Substation south to Gordon Substation. This includes structures 1-48 and excludes the eastern steel pole section of the line. Upgrade terminal equipment and relaying at remote end substations. Gordon - Perryman 138 kV section ratings: Before Proposed Solution: 169 / 213 / 217 / 280 MVA (SN/SE/WN/WE) After Proposed Solution: 211 / 268 / 250 / 317 MVA (SN/SE/WN/WE) Perryman - Manifold 138 kV section ratings: Before Proposed Solution: 169 / 213 / 217 / 280 MVA (SN/SE/WN/WE) After Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) Manifold - Nyswaner138 kV section ratings: Before Proposed Solution: 300 / 358 / 349 / 410 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 30.12 |  |  | New Upgrade
PJM WEST | s3938.1 | Rebuild approximately 47.2 miles of the Loughs Lane - Pickens 138 kV Line and install OPGW. At the Durbin Tap: Replace transmission line disconnect switches. At Loughs Lane Substation: Remove wave trap, replace disconnect switch, substation conductor, and relaying. At Durbin Substation: Remove wave trap, replace substation conductor, CVT's, and upgrade relaying. At Beverly Substation: Remove wave trap, replace disconnect switches, CVT's substation conductor, and relaying. At Pickens Substation: Remove wave trap, replace substation conductor, and relaying. Pickens - Durbin Tap 138 kV Line Ratings: Before Proposed Solution: 169 / 213 / 217 / 280 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Durbin - Durbin Tap 138 kV Line Ratings: Before Proposed Solution: 94 / 105 / 105 / 114 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Beverly Tap - Durbin Tap 138 kV Line Ratings: Before Proposed Solution: 164 / 206 / 216 / 248 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Beverly Tap - Loughs Lane 138 kV Line Ratings: Before Proposed Solution: 169 / 213 / 217 / 280 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 182.84 |  |  | New Upgrade
PJM WEST | s3937.1 | - At North Shenandoah Substation, replace 138 kV substation conductor, CVT, circuit breaker and associated disconnect switches and relaying. - At Page Substation, replace 138 kV wave trap, line turner and coax, CVT and relaying. North Shenandoah - Page 138 kV Line Before Proposed Solution: 292 / 306 / 306 / 306 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/15/2026 | 4/15/2026 | 4.06 |  |  | New Upgrade
PJM WEST | s3935.1 | - At Shepherdstown Substation: Replace relaying, circuit switcher, disconnect switches, PT, and CCVT. - At Sleepy Hollow Substation: Replace relaying, circuit breaker, disconnect switches, PT, CCVT, and line trap. Shepherdstown - Sleepy Hollow 138 kV Line Ratings: Before Proposed Solution: 221 / 268 / 250 / 306 MVA (SN/SE/WN/WE) After Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 2.6 |  |  | New Upgrade
PJM WEST | s3934.1 | - At Parr Run Substation: Replace substation conductor, circuit breaker, disconnect switches, line trap, PT, CCVT, and relaying. - At Junction Substation: Replace disconnect switches, circuit breaker, CCVT, substation conductor, line trap, and relaying. Parr Run - Junction 138 kV Line Ratings: Before Proposed Solution: 164 / 206 / 216 / 229 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/17/2026 | 7/17/2026 | 4.67 |  |  | New Upgrade
PJM WEST | s3933.1 | Relocate approximately 0.5 miles of the existing Charleroi - Mitchell - Yukon (Shepler Hill Jct) 138 kV Line. At Mitchell Substation: Re-terminate the Charleroi - Mitchell - Yukon (Shepler Hill Jct) 138 kV Line to isolate the transmission line from the power plant. Install new CCVT, CCVT junction box and stand foundation, grounding connectors, bus support adapters, switch stands, wave trap and line turner, surge arrester and dead-end tower. Replace disconnect switches. Revise relay settings. Transmission Line Ratings: Mitchell - Shepler Hill Jct 138 kV Line Segment: Before Proposed Solution: 295 / 375 / 349 / 441 MVA (SN/SE/WN/SE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/SE) | APS |  |  | Other |  |  | EP | 7/17/2026 | 7/17/2026 | 11.01 |  |  | New Upgrade
PJM WEST | s3932.1 | Convert Shingletown Substation into a six-breaker 230 kV ring bus. (APS-2023-059) At Shawville Substation (PN-2023-022): Replace substation conductor and revise relay settings. At Lewistown Substation (PN-2023-022): Replace line trap and revise relay settings. Transmission Line Ratings: Lewistown - Shingletown 230 kV Line: Before Proposed Solution: 512 / 612 / 619 / 700 MVA (SN/SE/WN/WE) After Proposed Solution: 546 / 666 / 619 / 790 MVA (SN/SE/WN/WE) Shawville - Shingletown 230 kV Line: Before Proposed Solution: 442 / 582 / 619 / 700 MVA (SN/SE/WN/WE) After Proposed Solution: 546 / 666 / 619 / 790 MVA (SN/SE/WN/WE) Dale Summit - Shingletown 230 kV Line: Before Proposed Solution: 486 / 523 / 542 / 571 MVA (SN/SE/WN/WE) After Proposed Solution: 617 / 754 / 699 / 894 MVA (SN/SE/WN/WE) This project is concurrent with PN-2023-022. | APS |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/7/2026 | 7/7/2026 | 19.11 |  |  | New Upgrade
PJM WEST | s3931.1 | At Yukon Substation: Replace 500 kV breakers, disconnect switches, substation conductors, and wave trap. At Rhodes Lane Substation: Replace 500 kV breakers, disconnect switches, substation conductors, and wave trap. Rhodes Lane - Yukon 500 kV Line Ratings: Before Proposed Solution: 3526 / 3792 / 3928 / 4140 MVA (SN/SE/WN/WE) After Proposed Solution: 3573 / 4378 / 4050 / 5175 MVA (SN/SE/WN/WE) | APS |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/7/2026 | 7/7/2026 | 5.45 |  |  | New Upgrade
PJM WEST | s3930.1 | Rebuild 12.5 miles of the Dutch Fork - Enon 138 kV Line with Light Duty (LD) steel horizontal structures and install OPGW. At Dutch Fork Substation: Remove wave trap, replace circuit breaker, disconnect switches, substation conductor and relaying. At Enon Substation: Remove wave trap. Dutch Fork - Enon 138 kV Line Ratings: Existing Line Ratings: 229 / 229 / 229 / 229 MVA (SN/SE/WN/WE) New Line Ratings: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/17/2026 | 6/17/2026 | 41.7 |  |  | New Upgrade
PJM WEST | s3929.1 | Replace one aged 138 kV breaker with a modern breaker. | DL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2026 | 5/15/2026 | 0.825 |  |  | New Upgrade
PJM MA | s3928.3 | Install mechanical refrigeration on the existing Brunot Island – Carson 345 kV HPFF transmission circuit to mitigate a violation of DLC’s local planning criteria. | DL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 19.8 |  |  | New Upgrade
PJM MA | s3928.2 | FirstEnergy work to support the establishment of McGinley Substation. Scope of work includes looping the Huntingdon – Springdale and Cheswick – Yukon 138 kV Lines into McGinley Substation, replacement of a 138 kV breaker at Huntingdon Substation, and upgrading and coordinating relaying at remote FE substations. | DL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 5.2 |  |  | New Upgrade
PJM MA | s3928.1 | Establish a new breaker-and-a-half substation, McGinley Substation, to serve the requested customer load. Establishing this substation requires the looping of the Cheswick (DLC) – Yukon (FE) 138 kV transmission line and the Springdale (FE) – Huntingdon (FE) 138 kV transmission line. McGinley Substation is to be comprised of twelve 138 kV breakers and a 50 MVAR capacitor bank. | DL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 21.3 |  |  | New Upgrade
PJM MA | s3926.1 | Rebuild ~22.1 miles of Renovo Tap 69kV line as Double Circuit. Rebuild ~2.1 miles of Lock Haven - Renovo 69kV line to Flemington Tap. Reconductor ~0.9 miles of the Flemington taps on the Lock Haven - Flemington and Lock Haven - Renovo 69kV lines. Utilize 556 ACSR. | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 6/16/2026 | 6/16/2026 | 59.9 |  |  | New Upgrade
PJM MA | s3925.1 | Rebuild 0.5 miles of the Quarry-Sands 1 & 2 lines. Utilize 556 ACSR. | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/14/2026 | 5/14/2026 | 1.3 |  |  | New Upgrade
PJM MA | s3924.1 | Tap the existing Hosensack-Quarry #2 line and extend 0.5 miles to the Hosensack 2 South Allentown Tap. Utilize 556 ACSR. | PPL |  |  | Customer Service |  |  | EP | 5/14/2026 | 5/14/2026 | 3.6 |  |  | New Upgrade
PJM MA | s3923.1 | Upgrade the Steel City 500kV Switchyard to a BAAH configuration. Install two 3000A circuit breakers | PPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 3 |  |  | New Upgrade
PJM MA | s3922.1 | Upgrade the Hosensack 500kV Switchyard to a BAAH configuration. Install three 3000A circuit breakers and five 3000A MODs | PPL |  |  | Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | EP | 5/5/2026 | 5/5/2026 | 4.9 |  |  | New Upgrade
PJM MA | s3921.1 | Install a new 170MVA, 230-69kV transformer as an in-kind replacement of the existing 230-69kV Jenkins Transformer 4 | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/5/2026 | 5/5/2026 | 7.1 |  |  | New Upgrade
PJM MA | s3920.1 | Install a new 170MVA, 230-69kV transformer as an in-kind replacement of the existing 230-69kV Hummelstown Transformer 1 | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/5/2026 | 5/5/2026 | 7.1 |  |  | New Upgrade
PJM WEST | n8358.1 | OVECI0024b: Replace 4 Dearborn 1600 A switches. | OVEC | [5 empty] | EP | [5 empty] | New Upgrade
PJM MA | s3919.1 | Extend the existing Port Carbon Tap 2 ~2.5 miles from Frackville - Orwigsburg 2 69kV line to Port Carbon Substation transformer bay 2 position. Utilize 556 ACSR. | PPL |  |  | Customer Service |  |  | EP | 5/14/2026 | 5/14/2026 | 7.2 |  |  | New Upgrade
PJM MA | s3918.1 | Upgrade the Hosensack 69kV yard to complete Double breaker-double bus design. Install 5 new 2000A breakers. | PPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 5/14/2026 | 5/14/2026 | 3.4 |  |  | New Upgrade
PJM MA | s3917.1 | Tap the existing Jenkins - Scranton #2 69kV line and extend ~0.1 miles to Dupont Substation transformer bay 2 position. Utilize 556 ACSR. | PPL |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 5/14/2026 | 5/14/2026 | 0.9 |  |  | New Upgrade
PJM MA | s3916.1 | Tap the existing Lycoming - Lock Haven #4 69kV line and extend ~0.9 miles to Woolrich Substation transformer bay 2 position. Utilize 556 ACSR | PPL |  |  | Customer Service |  |  | EP | 5/14/2026 | 5/14/2026 | 2.1 |  |  | New Upgrade
PJM MA | s3914.1 | Tap existing Stanton - Avoca 2 69kV line. Extend circuit 0.2 miles into to Sullivan Trail 69kV Substation transformer bay 2 (L) position. Utilize 556 ACSR | PPL |  |  | Customer Service |  |  | EP | 4/14/2026 | 4/14/2026 | 1 |  |  | New Upgrade
PJM WEST | s3910.3 | Install two 138 kV CCVT's, two relays, and necessary conduits to create ATO scheme on Mapleknoll - Mt. Healthy and Mapleknoll - Willey circuits. | DEOK |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 5/15/2026 | 5/15/2026 | 1.05 |  |  | New Upgrade
PJM WEST | s3910.2 | Install two 138 kV CCVT's, two relays, and necessary conduits to create ATO scheme on Finneytown - Mt. Healthy and Finneytown - Terminal circuits. | DEOK |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 5/15/2026 | 5/15/2026 | 1.05 |  |  | New Upgrade
PJM WEST | s3910.1 | Replace necessary existing foundations, structures and devices to accommodate installation of a new four-position ring bus configuration. This includes the installation of: four 138 kV, 2000 A, 40 kA circuit breakers; two 138 kV, 2000 A wave traps; eight 138 kV CCVT's; six 138 kV lightning arresters; two 138 kV 2000 A motor operated line disconnect switches; and six 138 kV 2000 A breaker disconnect switches. | DEOK |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 5/15/2026 | 5/15/2026 | 6.5 |  |  | New Upgrade
PJM WEST | s3909.6 | Install two 138 kV, 3000 A, 63 kA interrupt circuit breakers in Beckjord 138 kV substation to connect | DEOK |  |  | Customer Service |  |  | EP | 8/4/2026 | 8/4/2026 | 0 |  |  | New Upgrade
PJM WEST | s3909.5 | Install one new 345 kV, 3000 A, 50 kA interrupt circuit breaker in the 345 kV Pierce Substation. | DEOK |  |  | Customer Service |  |  | EP | 8/4/2026 | 8/4/2026 | 0 |  |  | New Upgrade
PJM WEST | s3909.4 | Install two new 345 kV, 4000 A, 50 kA interrupt circuit breakers in Woodsdale substation to connect a new circuit. | DEOK |  |  | Customer Service |  |  | EP | 8/4/2026 | 8/4/2026 | 0 |  |  | New Upgrade
PJM WEST | s3909.3 | Install a new 400 MVA 345/138 kV transformer. | DEOK |  |  | Customer Service |  |  | EP | 8/4/2026 | 8/4/2026 | 15 |  |  | New Upgrade
PJM WEST | s3909.2 | Install approximately 0.3 miles of new 954 ACSR 45x7 bundled conductor. This conductor will be used to connect the low side of the new Pierce 345/138 kV transformer to the 138 kV Beckjord substation. This line will be rated 618/618 MVA summer and 757/757 MVA winter. | DEOK |  |  | Customer Service |  |  | EP | 8/4/2026 | 8/4/2026 | 3.7 |  |  | New Upgrade
PJM WEST | s3909.1 | Install approximately 1.0 mile of bundled 954 ACSR, from Woodsdale to the customer site. The new line will be rated 1509/1509 MVA Summer, 1894/1894 MVA Winter. | DEOK |  |  | Customer Service |  |  | EP | 8/4/2026 | 8/4/2026 | 14.1 |  |  | New Upgrade
PJM WEST | s3908.1 | Rebuild 7.99 miles of the Kossuth - West Moulton 69kV line with 556 ACSR conductor. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 4/15/2026 | 4/15/2026 | 23.3959 |  |  | New Upgrade
PJM WEST | s3907.3 | One of the double circuit connections on the Hartman Farms 138kV Extension No. 3 will be reconfigured to feed a different Customer delivery position to meet the Customer's reliability and redundancy requirements. | AEP |  |  | Customer Service |  |  | EP | 3/19/2026 | 3/19/2026 | 0.123 |  |  | New Upgrade
PJM WEST | s3907.2 | Build one 138 kV double circuit line, ~0.65 miles, using ACSR Drake 795 (26/7) conductor to connect Cyprus station to the Customer's delivery points. | AEP |  |  | Customer Service |  |  | EP | 3/19/2026 | 3/19/2026 | 0.29321 |  |  | New Upgrade
PJM WEST | s3907.1 | At Cyprus station, build out the 9th partial string in the breaker and half bus, installing 3-138kV circuit breakers to terminate the two new customer feeds. Install 2-138kV customer meters and required fiber cables which will require a control house expansion. | AEP |  |  | Customer Service |  |  | EP | 3/19/2026 | 3/19/2026 | 4.802 |  |  | New Upgrade
PJM WEST | s3906.9 | Convert the Elkhart Hydro - Osolo line to 69kV operation. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 1.329 |  |  | New Upgrade
PJM WEST | s3906.8 | Convert the Elkhart Hydro - Dunlap line to 69kV operation. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.79861 |  |  | New Upgrade
PJM WEST | s3906.7 | Convert the East Elkhart - Elkhart Hydro line to 69kV operation. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 2.0476 |  |  | New Upgrade
PJM WEST | s3906.6 | Convert 34.5kV equipment to 69kV operation. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.46604 |  |  | New Upgrade
PJM WEST | s3906.5 | Convert 34.5kV equipment to 69kV operation. Install the relocated CB C from Osolo to the low side of Transformer #2 | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 1.4347 |  |  | New Upgrade
PJM WEST | s3906.4 | Install 69kV bus and convert CB B to 69kV operation. Relocate CB C to Dunlap station. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 1.0295 |  |  | New Upgrade
PJM WEST | s3906.3 | Convert 34.5kV equipment to 69kV operation. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.7855 |  |  | New Upgrade
PJM WEST | s3906.2 | Rebuild the station as an in/out station and operate at 69kV. Install 2 69/12kV distribution transformers and associated distribution equipment. Install a 69kV bus tie breaker. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 4.6422 |  |  | New Upgrade
PJM WEST | s3906.13 | Remove Parkway Tap 34.5kV | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.68945 |  |  | New Upgrade
PJM WEST | s3906.12 | Removal Middlebury Tap 34.5kV | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.37804 |  |  | New Upgrade
PJM WEST | s3906.11 | Remove Middleton Run SS 34.5kV | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 1.0549 |  |  | New Upgrade
PJM WEST | s3906.10 | Remove Wyland SS 34.5kV | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.41433 |  |  | New Upgrade
PJM WEST | s3906.1 | Rebuild the station as an in/out station and operate at 69kV. Install 2 69/12kV distribution transformers and associated distribution equipment. Install a 69kV bus tie breaker. Install a 28.7 MVAR capacitor bank. | AEP |  |  | Other |  |  | EP | 2/13/2026 | 2/13/2026 | 5.5775 |  |  | New Upgrade
PJM WEST | s3905.1 | Install a 69 kV 2000A three-way phase over phase MOAB switch with automatic reclosing and SCADA control capability to replace the hard tap. | AEP |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 1/16/2026 | 1/16/2026 | 4.4403 |  |  | New Upgrade
PJM WEST | s3904.1 | At North Haverhill station, replace breakers 'M' and 'P' with 3000A 40 kA 69 kV breakers. Add bus tie breaker. Replace 69 kV capacitor switcher 'AA' with new 2000 A/40 kA interrupting device. Replace Relays. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 1/16/2026 | 1/16/2026 | 12.9847 |  |  | New Upgrade
PJM MA | s3902.1 | Tap the existing COOP-BING tie and extend the new transformer position at Bingen substation. Utilize 556 ACSR | PPL |  |  | Customer Service |  |  | EP | 4/14/2026 | 4/14/2026 | 0.6 |  |  | New Upgrade
PJM MA | n8446.1 | Modify relays at Dauphin 69kV Substation | PPL |  |  |  | 12/31/2027 | 12/31/2027 | Cancelled | 10/8/2024 | 10/8/2024 | 0.137 |  | 2/26/2025 | Cancelled
PJM MA | n8446.2 | Modify relays at Sunbury 69kV Substation | PPL |  |  |  | 12/31/2027 | 12/31/2027 | Cancelled | 10/8/2024 | 10/8/2024 | 0.137 |  | 2/26/2025 | Cancelled
PJM MA | s3901.1 | Rebuild 14.2 miles and reconductor 5.3 miles of the Berks-South Akron 2 69kV line. Utilize 556 ACSR conductor. | PPL |  |  | Infrastructure Resilience |  |  | EP | 3/18/2026 | 3/18/2026 | 38.3 |  |  | New Upgrade
PJM MA | n8446.3 | Relay Modifications Scope of Work at Dauphin Substation | PPL |  |  |  | 12/1/2022 | 10/15/2025 | Cancelled | [5 empty] | Cancelled
PJM MA | s3900.1 | Rebuild 4.11 miles of the Cumberland West Shore 1 & 2 69kV lines - from Wertzville substation to Enola Tap. Utilize 795 ACSR. | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/18/2026 | 3/18/2026 | 20.3 |  |  | New Upgrade
PJM SOUTH | s3897.1 | Replace the fuse and the switch on the high side of TX#1, with a 1200 A circuit switcher and 2000 A switch at the Craigsville substation. | Dominion |  |  | Customer Service |  |  | EP | 3/18/2026 | 3/18/2026 | 0.84 |  |  | New Upgrade
PJM SOUTH | s3896.1 | Install a 1200 Amp, 25 kAIC circuit switcher and associated equipment (center break switch, bus work, relaying, etc) on the 115kV high side of the new transformer at Glasgow Substation. | Dominion |  |  | Customer Service |  |  | EP | 3/18/2026 | 3/18/2026 | 0.55 |  |  | New Upgrade
PJM SOUTH | s3895.2 | Replace the ground switch with a 2000A switch, and circuit switcher with a 1200A switcher. Substation expansion will be required. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/18/2026 | 3/18/2026 | 3 |  |  | New Upgrade
PJM SOUTH | s3895.1 | Wreck and rebuild the structures 1012/909A, 1012/910A, 1012/910B, 1012/910 and switch structure 1012/909 to current 115 kV standards and replace the conductor using a minimum summer normal rating of 175.9 MVA. Replace the ground switch with a 2000A switch, and circuit switcher with a 1200A switcher. Substation expansion will be required. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/18/2026 | 3/18/2026 | 1 |  |  | New Upgrade
PJM WEST | n8448.2 | Install Two (2) Fiber-Optic Paths to facilitate relaying between ITO, Haviland, and South Van Wert 69 kV Stations | AEP |  |  |  | 12/31/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.2632 |  | 2/26/2025 | Cancelled
PJM WEST | n8448.1 | Install two (2) Structures, two (2) Spans of Conductor, Connect ITO 69 Station to Existing Transmission Circuit | AEP |  |  |  | 12/31/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.68 |  | 2/26/2025 | Cancelled
PJM SOUTH | s3894.1 | Dominion Energy Distribution has submitted a Delivery Point (DP) Request for the installation of 2nd 115/36.5kV, 22.4MVA Delta-Wye connected TX at Dominion substation with a target energization date of 12/31/2026. | Dominion |  |  | Customer Service |  |  | EP | 3/18/2026 | 3/18/2026 | 0.5 |  |  | New Upgrade
PJM WEST | n8448.3 | Replace Protective Relays, Other Equipment at Haviland and South Van Wert 69 kV Stations | AEP |  |  |  | 12/31/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.7422 |  | 2/26/2025 | Cancelled
PJM WEST | n8448.4 | Review/Update Protective Relay Settings at the Proposed AE2-298 69 kV Station. | AEP |  |  |  | 12/31/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 0.4533 |  | 2/26/2025 | Cancelled
PJM SOUTH | s3893.1 | Dominion Energy Distribution has submitted a Delivery Point (DP) Request for the installation of one three-phase 9 MVA, 115/12.5kV transformer to feed Circuit 730 and replacing the existing transformer with a 9 MVA, 115/4.16kV transformer to feed Circuit 831 at Trego Substation with a target energization date in 04/30/2026. | Dominion |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 0.7 |  |  | New Upgrade
PJM SOUTH | s3892.1 | New 84 MVA 230-34.5 TX at Hanover Substation | Dominion |  |  | Customer Service |  |  | EP | 1/15/2026 | 1/15/2026 | 1.38 |  |  | New Upgrade
PJM MA | s3849.1 | Extend a new circuit 69kV tap from the existing Milton-Muncy 69kV line to interconnect the new Washingtonville 69-12kV. Build 0.1 miles of new 69kV single circuit line using 556 ACSR conductor. | PPL |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 1.25 |  |  | New Upgrade
PJM WEST | s3847.1 | Rebuild East Casstown to St Paris and reconductor the 8.5-mile section of 4/0 conductor with 1351 ACSR to improve capacity in the area. | Dayton |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 2/13/2026 | 2/13/2026 | 8 |  |  | New Upgrade
PJM WEST | n8450.1 | Bruceton Mills Interconnection Sub: Construct 3-breaker ring-bus substation for new generation interconnection | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 8.3782 |  | 2/26/2025 | Cancelled
PJM WEST | n8450.2 | AE1-106 Sub: Design, install, and test/commission multi-protocol label switching (MPLS) equipment for SCADA transport | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.7437 |  | 2/26/2025 | Cancelled
PJM WEST | s3846.4 | AES will refurbish the protection and controls at Crystal and Hutchings substations. | Dayton |  |  | Operational Flexibility and Efficiency |  |  | EP | 2/13/2026 | 2/13/2026 | 1 |  |  | New Upgrade
PJM WEST | n8450.3 | Design, install, and test/commission microwave equipment for Supervisory Control and Data Acquisition (SCADA) transport between AE1-106 Customer Facility and Bruceton Mills Substation. | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.2271 |  | 2/26/2025 | Cancelled
PJM WEST | n8450.4 | Brandonville Junction (Albright-Hazelton-Lake Lynn) 138kV: Loop the existing Brandonville Junction (Albright-Hazelton-Lake Lynn) 138kV line into the new Bruceton Mills Substation. | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 1.6741 |  | 2/26/2025 | Cancelled
PJM WEST | s3846.3 | AES will install one new 69kV circuit breakers to establish a bus-tie breaker | Dayton |  |  | Operational Flexibility and Efficiency |  |  | EP | 2/13/2026 | 2/13/2026 | 1.3 |  |  | New Upgrade
PJM WEST | n8450.5 | Lake Lynn Substation: Replace Panel No. 4 existing line relaying with new breaker control panel with (1) SEL451 and (1) SATEC meter. | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.3316 |  | 2/26/2025 | Cancelled
PJM WEST | s3846.2 | AES will install two new 69kV circuit breakers to establish two line-breakers | Dayton |  |  | Operational Flexibility and Efficiency |  |  | EP | 2/13/2026 | 2/13/2026 | 2.6 |  |  | New Upgrade
PJM WEST | n8450.6 | Hazelton Substation: Provide remote end equipment required for AE1-106. | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.925 |  | 2/26/2025 | Cancelled
PJM WEST | n8450.7 | Albright Substation: Provide remote end equipment required for AE1-106. | APS |  |  |  | 9/30/2021 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 1.7172 |  | 2/26/2025 | Cancelled
PJM WEST | s3846.1 | AES will install one new 69kV circuit breaker to establish a bus-tie breaker | Dayton |  |  | Operational Flexibility and Efficiency |  |  | EP | 2/13/2026 | 2/13/2026 | 1.3 |  |  | New Upgrade
PJM SOUTH | s3862.4 | Upgrade 230kV breakers 212432, 219732, 204632, 204132, 26832, and 2046T2197 at Hopewell Substation from 40kA to 63kA. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 6.6 |  |  | New Upgrade
PJM SOUTH | s3862.3 | Rebuild 230 kV Line #2370 (Allied - Shand Creek) to current 230 kV standards to achieve a minimum normal summer rating of 1573 MVA. Upgrade substation equipment to 4000 A. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 7 |  |  | New Upgrade
PJM SOUTH | s3862.2 | Rebuild 230 kV Line #2368 (Bermuda Hundred - Allied) to current 230 kV standards to achieve a minimum normal summer rating of 1573 MVA. Upgrade substation equipment to 4000 A. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 5.4 |  |  | New Upgrade
PJM SOUTH | s3862.1 | Cut existing 230kV Lines #286 and #2091 in and out of proposed Tropical substation. Lines to terminate in a breaker and a half scheme of twelve breakers. Customer has asked for redundant feeds. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 33.5 |  |  | New Upgrade
PJM MA | s3860.1 | Install new Mausdale 69-12kV substation with two 0.8 mile tap lines utilizing 556 ACSR along the Sunbury-Columbia 1&2 lines. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 3.6 |  |  | New Upgrade
PJM MA | s3859.1 | Extend The Clinton-Milton 1 69kV Watson Tap 0.1 miles utilizing 556 ACSR and bring into the Watson 69-12kV Substation, into transformer 1 bay position. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 0.5 |  |  | New Upgrade
PJM MA | s3858.1 | Extend The Columbia-Glen Brook 2 69kV West Berwick Tap 0.1 miles utilizing 556 ACSR and bring into the West Berwick 69-12kV Substation, into transformer 2 bay position. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 0.1 |  |  | New Upgrade
PJM MA | s3857.1 | Extend Parrish Tap from Harwood-Palooka-Hanover 1 69kV 0.1 miles and bring into the Parrish 69-12kV Substation, into transformer 2 bay position. Utilizing 556 ACSR. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 0.3 |  |  | New Upgrade
PJM MA | s3856.1 | Extend The Lycoming 2 - Muncy-Tie 69kV Fairfield Tap 0.1 miles utilizing 556 ACSR and bring into the Fairfield 69-12kV Substation, into transformer 2 bay position. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 0.2 |  |  | New Upgrade
PJM WEST | n8452.1 | Replace Sullivan 345 kV Relays, Install Trenching and Conduit for Fiber Cable, Install Two (2) Fiber Cable Transitions, Remove Wave Trap & Line Tuner | AEP | [5 empty] | IS | [5 empty] | New Upgrade
PJM WEST | n8452.2 | Install Two (2) 2.3 mile OPGW Fiber Cable Runs, Reinforce Five (5) Existing Structures | AEP | [5 empty] | IS | [5 empty] | New Upgrade
PJM MA | s3855.1 | Extend The Frackville - Mowry 69kV line 0.1 miles and bring into the Fountain springs Creek 69-12kV Substation, into transformer 1 bay position. Utilizing 556 ACSR. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 1.6 |  |  | New Upgrade
PJM MA | s3854.1 | Extend The Palooka-Jenkins 2 69kV Bear Creek Tap 2.3 miles and bring into the Bear Creek 69-12kV Substation, into transformer 2 bay position. Utilizing 556 ACSR. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 8 |  |  | New Upgrade
PJM WEST | n8455.2 | Midway Substation: Carrier equipment for anti-islanding | ATSI |  |  |  | 3/31/2022 | 4/30/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.5046 |  | 2/26/2025 | Scope/Cost Change
PJM WEST | n8455.3 | Bowling Green No.2: Carrier equipment for anti-islanding | APS |  |  |  | 3/31/2022 | 4/30/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.4706 |  | 2/26/2025 | Scope/Cost Change
PJM MA | s3853.1 | Extend Harwood - East Hazleton 2 0.1 miles from first structure outside of station, into transformer 2 bay position. Utilizing 556 ACSR. | PPL |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 0.3 |  |  | New Upgrade
PJM MA | s3852.1 | Extend new circuit from Tap Pole into West Damascus Substation transformer 2. | PPL |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 0.5 |  |  | New Upgrade
PJM MA | s3851.1 | Tap existing 69kV line to feed new 69-12kV Substation | PPL |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 1.85 |  |  | New Upgrade
PJM SOUTH | s3834.1 | - Construct new 230 kV substation Hibie St with an installed 84 MVA 230/24.5 kV TX and standard high-side protection (MOAB, circuit switcher, wave trap) - Tap Line #279 Reeves Ave <> Thrasher between structures 279/86 and 279/87 to extend a single circuit 230 kV source to the site. | Dominion |  |  | Customer Service |  |  | EP | 12/8/2025 | 12/8/2025 | 3.56 |  |  | New Upgrade
PJM SOUTH | s3833.1 | Install a 1200 Amp, 25 kAIC circuit switcher and associated equipment (center break switch, bus work, relaying, etc) on the high side of the new transformer at Jarratt Substation. | Dominion |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 0.4 |  |  | New Upgrade
PJM SOUTH | s3816.1 | Install a 1200 Amp, 50 kAIC circuit switcher and associated equipment (center break switch, bus work, relaying, etc) on the high side of the new transformer at Harmony Village. | Dominion |  |  | Customer Service |  |  | EP | 12/11/2025 | 12/11/2025 | 1.21 |  |  | New Upgrade
PJM SOUTH | s3815.1 | - Rebuild approximately 12.7 miles of Line #27 between Burton <> Bayside <> Long Creek <> Bains Store <> VA Beach to current 115kV standards. - Upgrade substation equipment to support the new conductor rating. - The Summer normal rating in the four-segment line will be 393 MVA. - The construction sequence for this project is unusually complex due to the requirements to avoid outages to distribution service costumers. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2025 | 11/13/2025 | 64 |  |  | New Upgrade
PJM SOUTH | s3814.1 | Tap Line #1037 (Skippers - Ivory Lane) near Ivory Lane Sub and extend a 115kV tap to Fontaine Creek DP | Dominion |  |  | Customer Service |  |  | EP | 2/12/2026 | 2/12/2026 | 4 |  |  | New Upgrade
PJM MA | n8468.1 | Install 2 new circuit breakers at Montour 230 kV Bay 5 as BAAH and install associated equipment to accept new AE2-271 Attachment Facilities | PPL |  |  |  | 10/1/2021 | 3/6/2026 | Cancelled | [5 empty] | Scope/Cost Change
PJM SOUTH | s3813.2 | Cut and extend Line #2104 (Spartan - Centreport) and Line #2305 (Aquia Harbor - Allman) approx. 0.3 miles to interconnect the proposed Alto Substation. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 1.5 |  |  | New Upgrade
PJM SOUTH | s3813.1 | Construct Alto Switching Station. Lines to terminate into a 230 kV six-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 15 |  |  | New Upgrade
PJM SOUTH | s3812.2 | Cut Line #2030 (Loudoun – Gainesville) to interconnect the proposed Aphrodite Substation. | Dominion |  |  | Customer Service |  |  | Cancelled | 10/8/2025 | 10/8/2025 |  |  |  | Cancelled
PJM SOUTH | s3812.1 | Lines to terminate into a 230 kV four-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | Cancelled | 10/8/2025 | 10/8/2025 |  |  |  | Cancelled
PJM SOUTH | s3811.1 | Cut existing 230kV Line 2103 (Elmont to Short Pump) in and out of proposed Flamingo substation. Lines to terminate initially in a 230kV four-breaker ring arrangement, with an ultimate six-breaker configuration. | Dominion |  |  | Customer Service |  |  | Cancelled | 10/8/2025 | 10/8/2025 |  |  |  | Cancelled
PJM SOUTH | s3810.2 | Cut and extend Line #2104 (Alto - Centreport) and #9575 (Alto - Allman) to interconnect the proposed Baritone Substation. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 0.5 |  |  | New Upgrade
PJM SOUTH | s3810.1 | Construct Baritone 230 kV Switching Station. Lines to terminate into a 230 kV six-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 15 |  |  | New Upgrade
PJM WEST | s3824.2 | Remove tertiary 34 kV capacitor bank on 345/138 kV autotransformer 82 at Skokie. Replace 345/138 kV autotransformer 82 with a new 420 MVA 345/138 kV transformer. Replace 138 kV TR 82 oil circuit breaker with a 3000 A, 63kA SF6 circuit breaker. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/5/2025 | 8/5/2025 | 15.36 |  |  | New Upgrade
PJM WEST | s3824.1 | Install a new 138 kV, 115.2 MVAR capacitor bank on 138 kV bus 1 at Skokie. | ComEd |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/5/2025 | 8/5/2025 | 9.04 |  |  | New Upgrade
PJM WEST | s3823.1 | Install 2 new 50 MVA, 138/12 kV transformers and install 4 new 138 kV bus tie CBs to complete double ring bus configuration at station Y764-2. | ComEd |  |  | Customer Service |  |  | EP | 6/13/2025 | 6/13/2025 | 0 |  |  | New Upgrade
PJM MA | s3819.9 | Install the second circuit on the existing single circuit, future double circuit, Big Bass - Pocono 230kV line between Big Bass and Pocono (7.25 miles) | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 9.1 |  |  | New Upgrade
PJM MA | s3819.8 | Install the second circuit on the existing single circuit, future double circuit, Acahela - Big Bass 230kV line between Acahela and Big Bass (12.9 miles) | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 16.125 |  |  | New Upgrade
PJM MA | s3819.7 | Bifurcate Acahela - Pocono 230kV line into the new Big Bass 230kV switchyard (~0.25 miles) | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 3 |  |  | New Upgrade
PJM MA | s3819.6 | Install a new DBDB (BAAH ultimate) bay at Acahela 230kV yard. Install two breakers, one dead-end, and ancillary equipment. Build out bay #3 and install one new 230kV breaker, two MODs, and ancillary equipment | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 3.75 |  |  | New Upgrade
PJM MA | s3819.5 | Install the second circuit on the existing single circuit, future double circuit, sections of Jenkins - Palooka and Palooka - Acahela 230kV lines between Jenkins and Acahela (15 miles) | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 18.75 |  |  | New Upgrade
PJM MA | s3819.4 | Re-terminate the JENK-PALO 230kV line from bay 3 to bay 2 at Jenkins 230kV yard | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 1 |  |  | New Upgrade
PJM MA | s3819.3 | Build out bay #2 at Jenkins 230kV yard and install one new 230kV breaker, two MODs, and ancillary equipment | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 1.25 |  |  | New Upgrade
PJM MA | s3819.2 | Install three 230kV lead lines for approximately 0.2 miles from Big Bass 230kV switchyard to each of the customer's two substations (six lines total) | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 8 |  |  | New Upgrade
PJM MA | s3819.15 | Add two subconductors to each phase in the 500kV designed section of the Callender Gap - Paupack 230kV Line for ~ 17.1 miles. Reconductor the existing ~0.9 mile 230kV designed section of Callender Gap - Paupack 230kV line | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 31.1 |  |  | New Upgrade
PJM MA | s3819.14 | Replace two 230kV breakers and four MODs in Bay #3 at Lackawanna 230kV | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 2.9 |  |  | New Upgrade
PJM MA | s3819.13 | Add two subconductors to each phase in the 500kV designed section of the Lackawanna - Callender Gap 230kV line for ~ 3 miles. Rebuild the existing ~0.5 mile 230kV designed section of Lackawanna - Callender Gap 230kV line | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 7.75 |  |  | New Upgrade
PJM MA | s3819.12 | Build out bay #2 at Paupack 230kV yard and install one new 230kV breaker, one dead-end, and ancillary equipment. Replace four MODs in Bay 3 at Paupack 230kV | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 2.9 |  |  | New Upgrade
PJM MA | s3819.11 | Install the second circuit on the existing single circuit, future double circuit, Paupack - Pocono 230kV line between Paupack and Pocono (21.75 miles) | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 27.5 |  |  | New Upgrade
PJM MA | s3819.10 | Install a new DBDB (BAAH ultimate) bay at Pocono 230kV yard. Install two breakers, one dead-end, and ancillary equipment. Build out bay #3 and install one new 230kV breaker, two MODs, and ancillary equipment | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 3.75 |  |  | New Upgrade
PJM MA | s3819.1 | Install a six bay BAAH 230kV switchyard with two 125MVAR Capacitor banks | PPL |  |  | Customer Service |  |  | EP | 9/9/2025 | 9/9/2025 | 50 |  |  | New Upgrade
PJM MA | s3781.1 | Rebuild 9.6 miles of the Lycoming 2-Muncy line as single circuit-future double 69kV line. Rebuild 0.4 miles of the Atlantic Refining Tap. Utilize 556 kcmil ACSR Conductor. | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/16/2025 | 10/16/2025 | 31 | 31 |  | New Upgrade
PJM MA | s3805.9 | Install three 230kV lead lines for approximately 0.1 miles from Gordon 230kV switchyard to the customer facility | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 4 |  |  | New Upgrade
PJM MA | s3805.8 | Rebuild the existing Eldred - Frackville 230kV Line to double circuit 230kV from Gordon to Frackville (4.4 miles) | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 19.8 |  |  | New Upgrade
PJM MA | s3805.7 | Rebuild the existing Eldred - Frackville 230kV Line to double circuit 230kV from Eldred to Gordon (7.3 miles) | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 32.85 |  |  | New Upgrade
PJM MA | s3805.6 | Rebuild the existing Sunbury - Eldred 230kV Line to double circuit 230kV from Sunbury to Eldred (24.8 miles) | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 112.5 |  |  | New Upgrade
PJM MA | s3805.5 | Install one new 230kV breaker, 230kV dead-end, and ancillary equipment in bay #3 at Frackville 230kV Yard | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 2 |  |  | New Upgrade
PJM MA | s3805.4 | Install two new terminals at Eldred Substation by building out two bays in DBDB future BAAH arrangement. Install total of four 230kV breakers. | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 4.5 |  |  | New Upgrade
PJM MA | s3805.3 | Build out bay #2 in the 230kV GIS with two new breakers and associated equipment. Re-terminate the SUNB-SUSQ #1 230kV line from Bay #3 to Bay #2. | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 7 |  |  | New Upgrade
PJM MA | s3805.2 | Bifurcate the Eldred - Frackville 230kV Line and terminate at the new Gordon 230kV switchyard. Extend lines approximately 0.4 miles into the new Gordon 230kV switchyard | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 4 |  |  | New Upgrade
PJM MA | s3805.1 | Install a four bay BAAH 230kV switchyard with an 80MVAR Capacitor bank | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 45 |  |  | New Upgrade
PJM MA | s3804.6 | Install two 230kV lead lines for approximately 0.2 miles from Sturges 230kV switchyard to customer sub #1 and install four 230kV lead lines for approximately 0.6 miles from Sturges 230kV switchyard to customer sub #2. (six circuits total) | PPL |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 8 |  |  | New Upgrade
PJM MA | s3804.5 | Replace one 230kV breaker and two MODs in Bay #3 at Lackawanna 230kV | PPL |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 1.5 |  |  | New Upgrade
PJM MA | s3804.4 | Terminate the Lackawanna - Callender Gap #2 line (from PPL-2025-0005) at Sturgis instead of Lackawanna | PPL |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 2.5 |  |  | New Upgrade
PJM MA | s3804.3 | Bifurcate Lackawanna - Callender Gap #1 230kV line into the new Sturges 230kV switchyard (~0.1 miles) | PPL |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 3 |  |  | New Upgrade
PJM MA | s3804.2 | Bifurcate Summit - Lackawanna #1 & #2 230kV lines into the new Sturges 230kV switchyard (~0.9 miles). Rebuild the ~0.2 mile section of SUMT-LACK #1 & #2 from bifurcation point to Lackawanna 230kV yard | PPL |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 9.9 |  |  | New Upgrade
PJM MA | s3804.1 | Install an eight bay BAAH 230kV switchyard with a 125MVAR Capacitor banks | PPL |  |  | Customer Service |  |  | EP | 10/8/2025 | 10/8/2025 | 50 |  |  | New Upgrade
PJM MA | s3803.2 | Install three 230kV lead lines for approximately 0.7 miles from Tomhicken 230kV switchyard to the customer facility | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 5.5 |  |  | New Upgrade
PJM MA | s3803.1 | Expand Tomhicken 230kV Yard and install three new line terminals by building out one bay BAAH and one bay in DBDB future BAAH arrangement. Install total of five 230kV breakers | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 8 |  |  | New Upgrade
PJM MA | s3802.6 | Rebuild the existing Hummelstown - Steelton 230kV Line to single circuit, future double circuit 230kV from Steelton to Highspire (1.5 miles) | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 6 |  |  | New Upgrade
PJM MA | s3802.5 | Rebuild the existing Hummelstown - Steelton 230kV Line to double circuit 230kV from Hummelstown to Highspire (5.1 miles) | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 23 |  |  | New Upgrade
PJM MA | s3802.4 | Install three 230kV lead lines for approximately 0.1 miles from Highspire 230kV switchyard to the customer facility | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 4 |  |  | New Upgrade
PJM MA | s3802.3 | Expand Hummelstown 230kV yard and install two new DBDB 230kV bays. Re-terminate the Steelton 230kV tap into a new bay position. Install one new breaker in Bay 6 to make HUMM-MIDD #2 DBDB | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 8 |  |  | New Upgrade
PJM MA | s3802.2 | Bifurcate the Hummelstown - Steelton 230kV line and terminate at the new Highspire 230kV switchyard. Extend lines approximately 0.2 miles into the new Highspire 230kV switchyard | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 3 |  |  | New Upgrade
PJM MA | s3802.1 | Install a four bay BAAH 230kV switchyard with an 80MVAR Capacitor bank | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 45 |  |  | New Upgrade
PJM MA | s3801.8 | Rebuild the 138kV yard at Wescosville in a BAAH configuration. Re-terminate the 138kV lines and transformer connections into the new yard | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 35 |  |  | New Upgrade
PJM MA | s3801.7 | Connect on-site spare 500-138kV Transformer at Wescosville substation. Terminate 500kV side into a new GIS bay and install 138kV breaker and tie to 138kV bus | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 5 |  |  | New Upgrade
PJM MA | s3801.6 | Install six 138kV lead lines for approximately 0.75 miles from Orefield 138kV yard to the customer facility | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 9 |  |  | New Upgrade
PJM MA | s3801.5 | Bifurcate the Wescosville - Allentown #1 & #2 138kV Lines and terminate at the new Orefield 500-138kV substation. Extend lines approximately 0.3 miles on separate double circuit pole lines to the Orefield 138kV yard | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 2.4 |  |  | New Upgrade
PJM MA | s3801.4 | Bifurcate the Siegfried - Wescosville #1 & #2 138kV Lines and terminate at the new Orefield 500-138kV substation. Extend lines approximately 1.8 miles on separate double circuit pole lines to the Orefield 138kV yard | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 14.4 |  |  | New Upgrade
PJM MA | s3801.3 | Bifurcate the Susquehanna - Wescosville 500kV line and terminate at the new Orefield 500-138kV substation. Extend lines approximately 1.2 miles on separate pole lines to the Orefield 500kV yard | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 17.2 |  |  | New Upgrade
PJM MA | s3801.2 | Install an eight bay BAAH 138kV yard with two 44MVAR capacitor banks | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 40 |  |  | New Upgrade
PJM MA | s3801.1 | Install a new three bay BAAH 500kV yard with two 500-138kV Transformers and one 144MVAR Capacitor Bank | PPL |  |  | Customer Service |  |  | EP | 11/4/2025 | 11/4/2025 | 71 |  |  | New Upgrade
PJM MA | s3800.5 | Install three 230kV lead lines for approximately 0.1 miles from Callender Gap 230kV switchyard to the customer facility | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 4 |  |  | New Upgrade
PJM MA | s3800.4 | Install a new single circuit, future double circuit, 230kV line from Lackawanna to Callender Gap (3.7 miles) | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 16.5 |  |  | New Upgrade
PJM MA | s3800.3 | Install one new 230kV breaker, 230kV dead-end, and ancillary equipment in Bay #1 at Lackawanna 230kV Yard | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 2 |  |  | New Upgrade
PJM MA | s3800.2 | Bifurcate the Lackawanna - Paupack 230kV line and terminate at the new Callender Gap 230kV switchyard. Extend lines approximately 0.2 miles into the new Callender Gap 230kV switchyard. | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 6 |  |  | New Upgrade
PJM MA | s3800.1 | Install a four bay BAAH 230kV switchyard with a 125MVAR Capacitor bank. | PPL |  |  | Customer Service |  |  | EP | 6/5/2025 | 6/5/2025 | 45 |  |  | New Upgrade
PJM WEST | s3752.3 | Construct a new 16-mile 69 kV single circuit line from St. Marys substation to Botkins substation. Constructing three 69 kV MOAB switches with supervisory control, two with auto-sectionalizing capability, approximately 6.3 miles from the St. Marys substation to facilitate the New Knoxville Delivery Point. Approximately 0.25 miles from Tap to Delivery Point. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 26.2 |  |  | New Upgrade
PJM WEST | s3752.2 | Reconfigure Botkins 69 kV substation into breaker-and-a-half arrangement to accommodate the new 69 kV line. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 13 |  |  | New Upgrade
PJM WEST | s3752.1 | Install 2 new 69 kV breakers at St. Marys substation to accommodate the new 69 kV line. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 4 |  |  | New Upgrade
PJM WEST | s3751.6 | Add a second 69kV bus to Indian Lake and convert to double breaker double bus configuration Retire 33kV system | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 10.1 |  |  | New Upgrade
PJM WEST | s3751.5 | Construct New 8 Miles Single Circuit T-Line using 795 ACSR from Wrestle Creek to Tap Point and Install 2 69kV Reclosers. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 20 |  |  | New Upgrade
PJM WEST | s3751.4 | Add 69kV, single straight bus substation “Wrestle Creek” with one 69kV/12kV 30MVA transformer. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 2.2 |  |  | New Upgrade
PJM WEST | s3751.3 | Add an additional 69kV breaker position at Indian Lake substation. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 2 |  |  | New Upgrade
PJM WEST | s3751.2 | Construct New 13 Miles Single Circuit T-Line using 795 ACSR from Chippewa to Indian Lake | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 25.1 |  |  | New Upgrade
PJM WEST | s3751.1 | Add 69kV, single straight bus substation “Chippewa” with one 69kV/12kV 30MVA transformer. | Dayton |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 1.9 |  |  | New Upgrade
PJM MA | s3741.1 | Extend a new circuit 69kV tap from the existing Frackville-Siegfried 2 69kV line to interconnect the new Customer substation. Build 0.1 miles of new 69kV single circuit line using 556 ACSR conductor. Initial loading of ~2MVA | PPL |  |  | Customer Service |  |  | EP | 9/18/2025 | 9/18/2025 | 0.7 |  |  | New Upgrade
PJM MA | s3740.1 | Rebuild 5 miles of the Frackville-Greenwood and Frackville-Orwigsburg 1 lines as double circuit 69kV. Rebuild 13 miles of the Frackville-Greenwood line as a single circuit 69kV. | PPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/18/2025 | 9/18/2025 | 45 |  |  | New Upgrade
PJM MA | s3739.1 | Install loops to tap the existing Copperstone-Harrisburg 2 69kV line to interconnect the spare transformer to Rutherford distribution substation. Build new loops using 556 ACSR conductor. | PPL |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/18/2025 | 9/18/2025 | 0.5 |  |  | New Upgrade
PJM MA | s3738.1 | Extend a new circuit 69kV tap from the existing Eldred - Cleveland 69kV line to interconnect the new Customer substation. Build 0.1 miles of new 69kV single circuit line using 556 ACSR conductor | PPL |  |  | Customer Service |  |  | EP | 7/17/2025 | 7/17/2025 | 0.9 |  |  | New Upgrade
PJM MA | s3737.9 | Install four 230kV lead lines for approximately 0.1 miles from Tomhicken 230kV switchyard to the customer facility. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 3.8 |  |  | New Upgrade
PJM MA | s3737.8 | Extend a double circuit 230kV (built for 500kV) for ~9 miles from Nescopeck to Tomhicken on existing PPL ROW. Extend single circuit 230kV (built for 500kV DlbCir) for 2.7 miles from Tomhicken to Harwood and terminate at Harwood. This will create the Nescopeck - Tomhicken 230kV and Nescopeck - Harwood 230kV lines. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 80.5 |  |  | New Upgrade
PJM MA | s3737.7 | Rebuild the Sunbury - Susquehanna # 1 230kV Line to double circuit 230kV for 3.9 miles from the Susquehanna 230kV yard to the new Nescopeck 230kV switchyard. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 17.2 |  |  | New Upgrade
PJM MA | s3737.6 | Bifurcate the Sunbury – Susquehanna #1 230kV into the new Nescopeck 230kV switchyard. Extend lines approximately 0.2 into the new Nescopeck 230kV switchyard. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 1.85 |  |  | New Upgrade
PJM MA | s3737.5 | Bifurcate the Susquehanna – Harwood #1 & #2 230kV and terminate at the new Tomhicken 230kV switchyard. Extend lines approximately 0.25 into the new Tomhicken 230kV switchyard. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 3.7 |  |  | New Upgrade
PJM MA | s3737.4 | Install new line terminal in the Harwood 230kV switchyard, install one dead-end, two breakers, and associated equipment. New bay to be DBDB initial and future BAAH. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 4 |  |  | New Upgrade
PJM MA | s3737.3 | Expand yard, extend busses, and install two new bays at Susquehanna 230kV yard. Install two dead-ends, four 230kV breakers, and associated equipment. Rebuild existing East and West bus to higher capacity. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 10 |  |  | New Upgrade
PJM MA | s3737.2 | Install a new three bay BAAH 230kV switchyard. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 29.5 |  |  | New Upgrade
PJM MA | s3737.1 | Install a six bay BAAH 230kV switchyard with a 125MVAR Capacitor bank. | PPL |  |  | Customer Service |  |  | EP | 8/6/2024 | 8/6/2024 | 45 |  |  | New Upgrade
PJM MA | s3736.4 | Extend two sets of double circuit 69kV lines (1113 ACSS) for approximately 0.6 miles to tie into customer substation #2 | PPL |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 3 |  |  | New Upgrade
PJM MA | s3736.3 | Extend two sets of double circuit 69kV lines (1113 ACSS) for approximately 7.1 miles to tie into the existing FRAC-SIEG #1 & #2 69kV lines. | PPL |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 43 |  |  | New Upgrade
PJM MA | s3736.2 | Expand the proposed Tresckow 230kV switchyard to include four 230-69kV transformers, a 4 bay BAAH 69kV yard (6 bay ultimate), and one 69kV capacitor bank. | PPL |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 53 |  |  | New Upgrade
PJM MA | s3736.1 | Tap the existing FRAC-SIEG #1 & #2 69kV lines and extend 69kV double circuit line (556ACSR) to the customer substation #1. Extend lines approximately 0.5 miles | PPL |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 2 |  |  | New Upgrade
PJM SOUTH | s3672.5 | Upgrade 230kV breakers 212432, 219732, 204632, 204132, 26832, and 2046T2197 at Hopewell Substation from 40kA to 63kA. | Dominion |  |  | Customer Service |  |  | EP | 7/7/2026 | 7/7/2026 |  | 6.6 |  | Scope/Cost Change
PJM WEST | n9713.0 | AEP Ohio Transmission Company Inc. will install one (1) new 8340 router at the Beverly 345 kV Station. | AEP | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | n9707.0 | OHTCO will tie the proposed AH1-719 345 kV project into the existing Beverly 345 kV station by completing the following construction tasks: - AEP Ohio Transmission Company Inc. will transition existing OPGW fiber-optic shield wire from the cut-in dead ends into the Beverly 345 kV Station. - AEP Ohio Transmission Company Inc. will install 1 mile of 144 count all dielectric self supporting (ADSS) fiber-optic cable. - AEP Ohio Transmission Company Inc. will install 1 mile of 144 count all dielectric loose tube (ADLT) underground fiber-optic cable. | AEP | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | n9614.0 | Corey 138 kV Station: Re-terminate Kenzie Creek - Corey 138 kV line. • Remove one (1) steel dead end structure and associated conductor and shield wire along the Kenzie Creek – Corey 138 kV Circuit. • Install one (1) new 100’ steel, single circuit, single pole dead end structure on a concrete foundation with an anchor bolt cage and two spans of aluminum conductor steel-reinforced 1033.5 (Curlew) transmission line conductor with 7#8 Alumoweld shield wire. | AEP |  |  |  | 2/28/2029 |  | EP | 11/3/2026 | 11/3/2026 | 0.59138 |  |  | New Upgrade
PJM WEST | n9612.0 | Corey 1385 kV Station: Re-terminate the Hydramatic - Corey 138 kV Circuit. • Remove two (2) steel tangent structures, one (1) steel dead end structure, and associated conductor and shield wire along the existing Corey – Hydramatic 138 kV Circuit. • Install one (1) new 90’ steel, single circuit, single pole, running corner direct embedded structure. • Install one (1) new 90’ steel, single circuit, single pole dead end structure on a concrete foundation with an anchor bolt cage. • Install two (2) spans of alumunim conductor steel-reinforced 1033.5 (Curlew) transmission line conductor with 7#8 Alumoweld shield wire. | AEP |  |  |  | 2/28/2029 |  | EP | 11/3/2026 | 11/3/2026 | 0.60101 |  |  | New Upgrade
PJM SOUTH | n9288.0 | Re-arrange line #2118 to loop into and out of the new 230 kV four breaker switching station, AE2-122 | Dominion |  |  |  | 12/31/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n10143.0 | Millville Substation: Replace OCB with (1) 138 kV 2000A SF6 circuit breaker. Replace existing line relaying with (1) new line relaying panel. Install (1) anti-islanding protection panel, GPS Clock and Satec PM174 meter. | APS |  |  |  | 10/14/2027 |  | EP | [5 empty] | New Upgrade
PJM MA | n10142.0 | Raritan River Substation: Install (1) in-sub fiber run to represent ADSS tail extension from Raritan River substation control house to last T-Line structure for OPGW build. | JCPL |  |  |  | 1/31/2031 |  | EP | [5 empty] | New Upgrade
PJM MA | n10141.1 | Duplicate of n10141.0: Deep Run Substation: Review and update relay settings. | JCPL |  |  |  | 1/31/2031 |  | Cancelled | [5 empty] | Scope/Cost Change
PJM MA | n10141.0 | Deep Run Substation: Review and update relay settings. | JCPL |  |  |  | 1/31/2031 |  | EP | [5 empty] | New Upgrade
PJM SOUTH | b4000.365 | Terminate line 568 Ladysmith to Possum Point from the line of demarcation into Thornburg substation (Possum Point - Thornburg portion). | Dominion |  | 2024-W1-967 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 10/6/2026 | 10/6/2026 | 2.5 | 2.5 |  | Scope/Cost Change
PJM SOUTH | b4000.364 | Terminate line 568 Ladysmith to Possum Point from the line of demarcation into Thornburg substation (Ladysmith - Thornburg portion). | Dominion |  | 2024-W1-967 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 10/6/2026 | 10/6/2026 | 2.5 | 2.5 |  | Scope/Cost Change
PJM WEST | s3898.9 | Relocating the existing Clinton - Greene 345 kV transmission Line. | Dayton |  |  | Customer Service |  |  | EP | 7/7/2026 | 7/7/2026 | 8.3 | 8.3 |  | New Upgrade
PJM WEST | s3898.8 | Relocating the existing Clinton - Lynchburg 345 kV transmission Line. | Dayton |  |  | Customer Service |  |  | EP | 7/7/2026 | 7/7/2026 | 3.2 | 3.2 |  | New Upgrade
PJM WEST | s3898.7 | Establish two ~2-mile 345 kV single circuit feeds to the customer substation from AES's Clinton substation. These lines will be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 20 | 20 |  | New Upgrade
PJM WEST | s3898.6 | Construct an ~ 27-mile 345 kV single circuit from Clinton substation to Fayette substation. These lines will be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 100 | 187 |  | New Upgrade
PJM WEST | s3898.5 | Expand the Clinton 345 kV substation to accommodate the additional 345 kV line, 2 customer feeds, one 300-MVAR capacitor (two steps of 150 MVAR) Projected ISD: 1/2028 12/31/2028 and a new one 150-MVAR STATCOM, Projected ISD: 12/1/2030 | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 75 | 65.4 |  | New Upgrade
PJM WEST | s3898.4 | Establish four ~0.5-mile 345 kV feed to the customer substations from AES's Fayette substation. These lines will be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 9 | 9 |  | New Upgrade
PJM WEST | s3898.3 | Construct an ~ 25-mile 345 kV double circuit line from Atlanta substation to Fayette substation. The line is projected to be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 192 | 220.7 |  | New Upgrade
PJM WEST | s3898.2 | Reconfigure the Atlanta 345kV substation into a breaker-and-a-half arrangement to accommodate the 2 additional 345 kV lines. | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 36 | 24.3 |  | New Upgrade
PJM WEST | s3898.1 | Expand the Fayette 345 kV substation to breaker-and-a-half arrangement to accommodate the additional 345 kV lines and the customer feeds. Projected ISD: 10/30/2026 and a 300-MVAR capacitor (two steps of 150 MVAR) Projected ISD: 1/1/2030 | Dayton |  |  | Customer Service |  |  | EP | 4/1/2025 | 7/7/2026 | 48 | 51.9 |  | New Upgrade
PJM WEST | n10140.1 | Remote end work at Lemoyne substation required for the Lulu 345 kV Switchyard build | ATSI |  |  |  | 5/1/2029 |  | Cancelled | [5 empty] | Cancelled
PJM MA | s0934.1 | Build a new Port Street 69 kV substation | PSEG |  |  | Operational Flexibility and Efficiency |  |  | IS | 7/29/2015 | 7/29/2015 | 67.5 |  |  | Scope/Cost Change
PJM WEST | s3889.2 | FE to update relay settings at Sand Ridge substation. | AMPT |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency^Other |  |  | EP | 2/13/2026 | 2/13/2026 | 0.076 |  |  | New Upgrade
PJM WEST | s3889.1 | AMPT to rebuild 2.75 miles of the AMPT owned portion of the Poe Road - Tontogany 69 kV line from the Poe Road substation to the AMPT/FE point of interconnection. | AMPT |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency^Other |  |  | EP | 2/13/2026 | 2/13/2026 | 6.06 |  |  | New Upgrade
PJM WEST | s3888.2 | Reroute the existing McDonald Steel - Niles Central 138 kV line to terminate in a new position in the Niles Central 138 kV ring bus. Upgrade remote end relays and/or relay settings. | AMPT |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 1/16/2026 | 1/16/2026 | 2.4 |  |  | New Upgrade
PJM WEST | s3888.1 | Reconfigure the existing Niles Central 138 kV station into a four (4) circuit breaker ring bus by installing one (1) new 138 kV circuit breaker and relocate the existing 138 kV CB "B-20" to create a new line terminal towards Niles (ATSI). Expand the two existing in-line bus configurations to create a ring bus configuration. Install five (5) new 138 kV circuit switchers on the high-side of the distribution transformers to ensure a transformer fault does not take out a portion of the 138 kV ring bus. Demolish switches, busses, and trenching due to age of these pieces of equipment. Upgrade the vintage protection systems (including new control house) to meet modern utility standards. | AMPT |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 1/16/2026 | 1/16/2026 | 11.7 |  |  | New Upgrade
PJM WEST | s3891.1 | Build a new substation (North Clayben) as a 138/69 kV substation adjacent to the Clayben Substation, a 138-12.4 kV substation. -Build a three breaker 69 kV ring bus. -Build a four breaker 138 kV ring bus. -Loop the Lakemore-South Akron (future Glenmount) 138 kV Line in/out of the new substation. -Loop the Gilchrist-Star 69 kV Line in/out of the new substation. Re-terminate the Clayben Substation distribution high side into the 138 kV breaker position in the new substation. Add automatic sectionalizing to McKnights Substation. The line project will separate the Gilchrist-Star 69 kV Line and Lakemore-South Akron (future Glenmount) 138 kV line, and create the following lines: -North Clayben-Gilchrist 69 kV Line ~9.8 miles -North Clayben-Star 69 kV Line ~14.8 miles -North Clayben-Lakemore 138 kV Line ~4.1 miles -North Clayben-South Akron (future Glenmount) 138 kV Line ~4.0 miles Transmission Line Ratings: North Clayben - Rochling Auto 69 kV Line Before Proposed Solution: N/A After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) North Clayben - MckNight 69 kV Line Before Proposed Solution: N/A After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) North Clayben - Lakemore 138 kV Line Before Proposed Solution: N/A After Proposed Solution: 157 / 196 / 198 / 255 MVA (SN/SE/WN/WE) North Clayben - South Akron (future Glenmount) 138 kV Line Before Proposed Solution: N/A After Proposed Solution: 157 / 196 / 198 / 255 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | EP | 3/19/2026 | 3/19/2026 | 36.49 |  |  | New Upgrade
PJM WEST | s3890.1 | Rebuild the Cedar St - Lowellville South 69 kV Line using new conductor (9.6-miles). Upgrade disconnect switches, station conductor, and relays at Cedar St and Lowellville stations. Transmission Line Ratings: - Before Proposed Solution: 65 / 68 / 72 / 72 MVA (SN/SE/WN/WE) - After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) Transmission Conductor Ratings: - Before Proposed Solution: 65 / 68 / 87 / 87 MVA (SN/SE/WN/WE) - After Proposed Solution: 111 / 134 / 125 / 159 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience |  |  | EP | 3/19/2026 | 3/19/2026 | 30.79 |  |  | New Upgrade
PJM WEST | s3886.1 | Replace the Line Switch 1007 on the Loughs Lane - Pickens 138 kV Line at the Durbin Tap. Beverly Tap - Durbin Tap 138 kV Line -Before Proposed Solution: 164 / 206 / 216 / 248 MVA (SN/SE/WN/WE) -After Proposed Solution: 169 / 213 / 217 / 280 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 1/16/2026 | 1/16/2026 | 1.05 |  |  | New Upgrade
PJM WEST | s3887.1 | Rebuild approximately 30.2 miles of Glenville - Weston 138 kV Line using steel structures and install new conductor. Replace one double circuit steel lattice structure #94-A with steel monopole structure. At Glenville Substation: Replace line trap, substation conductor, and revise relay settings. At Weston Substation: Replace substation conductor and revise relay settings. Glenville - Sand Fork Tap 138 kV Line Ratings: Before Proposed Solution: 195 / 209 / 217 / 229 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) Sand Fork Tap - Weston 138 kV Line Ratings: Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 1/16/2026 | 1/16/2026 | 89.52 |  |  | New Upgrade
PJM WEST | s3885.1 | At Yukon Substation, replace the limiting conductor on the No. 7 500/138 kV Transformer. Transformer Ratings: - Before Proposed Solution: 1096 / 1296 / 1309 / 1375 MVA (SN/SSTE/WN/WSTE) - After Proposed Solution: 1096 / 1365 / 1372 / 1558 MVA (SN/SSTE/WN/WSTE) | APS |  |  | Operational Flexibility and Efficiency |  |  | EP | 1/6/2026 | 1/6/2026 | 0.41 |  |  | New Upgrade
PJM MA | s3817.1 | Willis Road 115 kV Substation - Construct new 115 kV substation adjacent to Smith Street Substation. Willis Road will replace 115 kV equipment at Smith Street Substation. | ME |  |  | Operational Flexibility and Efficiency | 12/31/2027 |  | EP | 9/14/2023 | 9/14/2023 | 25 |  |  | New Upgrade
PJM WEST | s3879.1 | Replace manually operated switches A-66 and A-67 on the Black River - Willow Creek 69 kV Line. New switches will be equipped with SCADA controlled motor operators. Replace the existing structure with independent steel structures for the switches. Black River Tap - Willow Creek Tap 69 kV Line: -Before Proposed Solution: 82 / 103 / 108 / 124 MVA (SN/SE/WN/WE) -After Proposed Solution: 100 / 121 / 113 / 143 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | PL | 12/12/2025 | 12/12/2025 | 1.53 |  |  | New Upgrade
PJM WEST | s3872.1 | Reconfigure the feeds into the Ashtabula East and the ties to the Ashtabula - Zenith 138 kV line to allow for improved operational flexibility during maintenance. -Eliminate/Retire the existing tie and switches between the Ashtabula East and Zenith 138 kV lines. -Eliminate the existing tap located outside of the Ashtabula East Substation. -Construct approximately 0.1 miles of new 138 kV line. -Install two 138 kV switches; one switch will be operated normally opened. | ATSI |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | PL | 11/14/2025 | 11/14/2025 | 4.79 |  |  | New Upgrade
PJM WEST | s3873.1 | Rebuild the Maple - Pine 69 kV Line from Maple through structure 110 (~10 miles). Replace five disconnect switches (A-6041, A-6042, A-194, A-195, A-219). Maple - Evans City 69 kV Line: Before Proposed Solution: 141 / 171 / 160 / 203 MVA (SN/SE/WN/WE) After Proposed Solution: 154 / 188 / 175 / 223 MVA (SN/SE/WN/WE) Evans City - Callery 69 kV Line: Before Proposed Solution: 141 / 171 / 160 / 203 MVA (SN/SE/WN/WE) After Proposed Solution: 154 / 188 / 175 / 223 MVA (SN/SE/WN/WE) Callery - Kline 69 kV Line: Before Proposed Solution: 141 / 171 / 160 / 203 MVA (SN/SE/WN/WE) After Proposed Solution: 154 / 188 / 175 / 223 MVA (SN/SE/WN/WE) Kline - Concast Metals 69 kV Line: Before Proposed Solution: 141 / 171 / 160 / 203 MVA (SN/SE/WN/WE) After Proposed Solution: 154 / 188 / 175 / 223 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience |  |  | PL | 11/14/2025 | 11/14/2025 | 36.68 |  |  | New Upgrade
PJM WEST | s3878.1 | Rebuild the Sharon - McDowell 69 kV Line, including tap structures and lines up to customer facilities (19.2 miles total). Upgrade terminal equipment at Sharon and McDowell substations, including station conductor, relays, CCVTs, and disconnect switches. Replace line switches A-161 & A-179 (4 miles from McDowell Substation). Sharon - Mercer 69 kV Line (no ratings change): Before Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) Mercer - Reznor Thomas 69 kV Line: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) Reznor Thomas - Mercer Forge 69 kV Line: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) Mercer Forge - Department of Corrections 69 kV Line: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) Department of Corrections - McDowell 69 kV Line: Before Proposed Solution: 47 / 56 / 53 / 67 MVA (SN/SE/WN/WE) After Proposed Solution: 80 / 96 / 90 / 114 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | PL | 12/12/2025 | 12/12/2025 | 63.7 |  |  | New Upgrade
PJM WEST | s3877.1 | Convert Newton Falls Substation 138 kV yard into a six-breaker ring bus by installing three new 138 kV breakers. Build a new Whitman Station, a four-breaker 138 kV ring bus, near Reinforcements Systems of Ohio Cut into the Evergreen - Ivanhoe 138 kV Line 4.5 miles from Evergreen Substation and loop into the new Whitman Station four-breaker ring bus by constructing 0.6 miles of new transmission line. Construct five miles of new 138 kV line from Newton Falls Substation to the new four-breaker Whitman Station. Remote end upgrades at Bridge, Ohio Star Forge, Ivanhoe, Evergreen, and Franklin substations. Transmission Line Ratings: Before Proposed Solution: Evergreen - Ivanhoe 138 kV Line: 190 / 225 / 226 / 258 MVA (SN/SE/WN/WE) After Proposed Solution: Evergreen - Whitman 138 kV Line: 200 / 242 / 226 / 286 MVA (SN/SE/WN/WE) Whitman - Ivanhoe 138 kV Line: 200 / 242 / 226 / 286 MVA (SN/SE/WN/WE) Whitman - Newton Falls 138 kV Line: 278 / 339 / 315 / 401 MVA (SN/SE/WN/WE) | ATSI |  |  | Equipment Material Condition, Performance and Risk^Infrastructure Resilience^Operational Flexibility and Efficiency |  |  | PL | 12/12/2025 | 12/12/2025 | 51.52 |  |  | New Upgrade
PJM WEST | s3884.3 | Construct a 69kV Extension from the switch to the customer substation, ~0.11-miles. | AEP |  |  | Customer Service |  |  | EP | 12/12/2025 | 12/12/2025 | 0.75237 |  |  | New Upgrade
PJM WEST | s3884.2 | Cut into the Sharp Road - Commerce 69 kV circuit to allow new switch to serve customer. | AEP |  |  | Customer Service |  |  | EP | 12/12/2025 | 12/12/2025 | 0.52524 |  |  | New Upgrade
PJM WEST | s3884.1 | Add Phase over Phase switch with auto-sectionalizing named Jennings Road Switch cut-in to the Sharp Road - Commerce 69 kV circuit to feed new customer. | AEP |  |  | Customer Service |  |  | EP | 12/12/2025 | 12/12/2025 | 1.2977 |  |  | New Upgrade
PJM WEST | s3880.1 | Rebuild the Grand Point - Roxbury 138 kV Line (14 miles total) with steel H-frame structures and new conductor. -5.5 miles per PN-2024-012 -8.5 miles per APS-2024-028 At Roxbury Substation (PN): -Replace limiting substation conductor and revise relay settings. At Greene Substation: -Revise relay settings. At Letterkenny Substation: -Replace line switch and revise relay settings. At Grand Point Substation: -Replace substation conductor, circuit breaker, install surge arrestors and ground switch, and revise relay settings. Transmission Line Ratings: Roxbury - AD2-062 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Greene - AD2-062 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Letterkenny - Greene 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) Grand Point - Letterkenny 138 kV Line Before Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/12/2025 | 12/12/2025 | 28.34 |  |  | New Upgrade
PJM WEST | s3871.1 | Carroll – Mt. Airy 230 kV Line: - Remove and replace 93 wood structures with steel structures on concrete foundation and install 12.72 miles of new conductor - Adjust relaying at Carroll and Mt. Airy substations Carroll – Mount Airy 230 kV Line Ratings: Before Proposed Solution: 251 / 343 / 302 / 370 MVA (SN/SE/WN/WE) After Proposed Solution: 709 / 869 / 805 / 1031 MVA (SN / SE / WN / WE) | APS |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 11/4/2025 | 4/7/2026 | 50 |  |  | New Upgrade
PJM WEST | s3870.1 | At Wylie Ridge Substation: Replace the No. 3 345/138 kV Transformer Replace one 138 kV disconnect switch with a circuit breaker Replace 345 kV disconnect switches, substation conductor, and relaying Wylie Ridge No. 3 345/138 kV Transformer: Before Proposed Solution: 407 / 516 / 480 / 548 MVA (SN/SSTE/WN/WSTE) After Proposed Solution: 575 / 748 / 690 / 805 MVA (SN/SSTE/WN/WSTE) | APS |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 11/4/2025 | 11/4/2025 | 13.45 |  |  | New Upgrade
PJM WEST | s3869.1 | At Eaglehead Substation: Replace 230 kV circuit breaker, disconnect switches, substation conductor, CVT, CT, surge arresters, and relaying. At Monocacy Substation: Replace 230 kV disconnect switches, substation conductor, CVT, CT, surge arresters, and relaying. Monocacy - Eaglehead 230 kV Line Ratings: Before Proposed Solution: 548 / 688 / 699 / 797 MVA (SN/SE/WN/WE) After Proposed Solution: 617 / 754 / 699 / 894 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/4/2025 | 11/4/2025 | 3.88 |  |  | New Upgrade
PJM WEST | s3874.1 | At Elko Substation: Replace No. 1 230/138 kV transformer Replace 230 kV disconnect switch, limiting substation conductor and transformer relaying Elko No. 1 230/138 kV Transformer: Before Proposed Solution: 230 / 286 / 280 / 325 MVA (SN/SSTE/WN/WSTE) After Proposed Solution: 266 / 346 / 319 / 372 MVA (SN/SSTE/WN/WSTE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/8/2025 | 12/8/2025 | 6.69 |  |  | New Upgrade
PJM WEST | s3868.1 | Replace limiting substation conductor at Price Hill Substation on the South Morgantown terminal. Price Hill - South Morgantown 138 kV Line Ratings: Before Proposed Solution: 224 / 293 / 323 / 343 MVA (SN/SE/WN/WE) After Proposed Solution: 262 / 314 / 325 / 343 MVA (SN/SE/WN/WE) | APS |  |  | Operational Flexibility and Efficiency |  |  | EP | 10/17/2025 | 10/17/2025 | 0.1 |  |  | New Upgrade
PJM WEST | s3875.1 | Rebuild 12.1 miles of the Junction - Parr Run 138 kV Line. Structures 1-18 (~4.9 miles) are double circuited with the Kelso Gap - Parr Run 138 kV Line and this section does not require a rebuild at this time. Transmission Line Ratings: Junction - Parr Run 138 kV Line Before Proposed Solution: 164 / 206 / 216 / 229 MVA (SN/SE/WN/WE) After Proposed Solution: 164 / 206 / 216 / 229 MVA (SN/SE/WN/WE) Note - This line is currently limited by terminal equipment, which will be upgraded per APS-2024-086. Therefore, this project will not affect the ratings of the Junction - Parr Run 138 kV Line. | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/12/2025 | 12/12/2025 | 35 |  |  | New Upgrade
PJM WEST | s3867.1 | At Cecil Substation, replace substation conductor, line trap, line turner and coax, CVTs and relaying. At Enlow Substation, replace circuit breaker, disconnect switches, line trap, line turner and coax, CVT and relaying. Cecil – Enlow 138 kV Line Ratings: Before Proposed Solution: 292 / 314 / 325 / 343 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/17/2025 | 10/17/2025 | 4 |  |  | New Upgrade
PJM WEST | s3865.1 | At Armstrong Substation, replace disconnect switches, line trap, line turner and coax, CVT and relaying. At Kittanning Substation, replace circuit breaker, disconnect switches, line trap, line turner and coax, CVT and relaying. Armstrong - Kittanning 138 kV Line Ratings: Before Proposed Solution: 195 / 209 / 217 / 229 MVA (SN/SE/WN/WE) After Proposed Solution: 221 / 268 / 250 / 317 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/17/2025 | 10/17/2025 | 3.44 |  |  | New Upgrade
PJM WEST | s3866.1 | At Belmon Substation, replace line and disconnect switches, substation conductor, and relaying. At Charleroi Substation, replace substation conductor, and relaying. At Mitchell Substation, replace substation conductor, and relaying. At Smithton Substation, replace disconnect switches, and relaying. At Yukon, replace relaying Charleroi – Belmon 138 kV Line Ratings: Before Proposed Solution: 274 / 345 / 345 / 405 MVA (SN/SE/WN/WE) After Proposed Solution: 297 / 365 / 345 / 441 MVA (SN/SE/WN/WE) Belmon – Shepler Hill Jct 138 kV Line Ratings: Before Proposed Solution: 269 / 335 / 326 / 380 MVA (SN/SE/WN/WE) After Proposed Solution: 269 / 335 / 326 / 421 MVA (SN/SE/WN/WE) Shepler Hill Jct – Mitchell 138 kV Line Ratings: Before Proposed Solution: 295 / 375 / 349 / 441 MVA (SN/SE/WN/WE) After Proposed Solution: 308 / 376 / 349 / 445 MVA (SN/SE/WN/WE) | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/17/2025 | 10/17/2025 | 3.71 |  |  | New Upgrade
PJM WEST | s3864.6 | Construct a second 1.8 mile 345kV single circuit transmission line from Don Marquis to the new Monza Station | AEP |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 7.5 |  |  | New Upgrade
PJM WEST | s3864.5 | Install four (4) 63kA 5000A breakers for two (2) additional feeds to a new switching station Monza | AEP |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 9.1 |  |  | New Upgrade
PJM WEST | s3864.4 | Greenfield 0.2 mile 345kV transmission feed from Monza Station to customer site | AEP |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 0.5 |  |  | New Upgrade
PJM WEST | s3864.3 | Greenfield 345kV 0.2 mile transmission feed from Monza Station to customer site | AEP |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 0.5 |  |  | New Upgrade
PJM WEST | s3864.2 | Construct greenfield 345kV ring bus switching station, comprising of six (6) 345kV 63kA 5000A breakers and a 150 MVAR STATCOM | AEP |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 131.5 |  |  | New Upgrade
PJM WEST | s3864.1 | Construct 1.8 mile 345kV single circuit transmission line from Don Marquis to the new Monza Station | AEP |  |  | Customer Service |  |  | EP | 4/7/2026 | 4/7/2026 | 7.5 |  |  | New Upgrade
PJM WEST | s3845.1 | At Lallendorf Substation: - Replace line relaying Install new seven-mile ADSS fiber line from Lallendorf Substation to Toledo Edison regional services territory boundary | ATSI |  |  | Other |  |  | EP | 3/4/2025 | 3/4/2025 | 5.9 |  |  | New Upgrade
PJM WEST | s3844.1 | At Lemoyne Substation: - Replace line relaying Install new 20-mile ADSS fiber line from Lemoyne Substation to Toledo Edison regional services territory boundary. | ATSI |  |  | Other |  |  | EP | 3/4/2025 | 3/4/2025 | 15.6 |  |  | New Upgrade
PJM WEST | s3863.1 | Rebuild the 2.5-mile section 954ACSR conductor, 64 steel poles and two hybrid poles for a river and railroad crossing. The ratings for this section will increase to 150/150/150 MVA summer, 189/189/189 MVA winter. | DEOK |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 2/14/2025 | 2/14/2025 | 7.21 |  |  | New Upgrade
PJM WEST | s3843.9 | Remote end coordination work necessary to support the following: cut-in the existing Paris-Zion and Pleasant Prairie-Zion 345 kV transmission lines into Lakeview substation (MISO), cut-in the existing Olive-University Park and Olive-Green Acres 345 kV transmission lines into Babcock substation. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 0 |  |  | New Upgrade
PJM WEST | s3843.8 | Mitigate sag limit on 345 kV line from Zion-Paris (ATC) and replace line trap at Zion. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 3 |  |  | New Upgrade
PJM WEST | s3843.7 | Replace 345 kV BT 1-5, BT 2-5, BT 2-3, L4620, L4621, and L12006 oil CBs at Des Plaines from 40 kA to 63 kA. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 21 |  |  | New Upgrade
PJM WEST | s3843.6 | Replace 345 kV BT 5-6 and BT 17-18 oil CBs at Zion from 50 kA to 63 kA. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 7 |  |  | New Upgrade
PJM WEST | s3843.5 | Replace 345 kV BT 5-6 oil CB at Powerton from 40 kA to 63 kA. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 3.5 |  |  | New Upgrade
PJM WEST | s3843.4 | Cut-in existing ComEd 345 kV Powerton-Katydid and Powerton-Nevada transmission lines into a new Woodford County substation (MISO). | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 7 |  |  | New Upgrade
PJM WEST | s3843.3 | Construct a segment of a new 765 kV transmission line from the existing ComEd Collins 765 kV substation to a new 765 kV Woodford County substation. Interconnection point with MISO to be determined. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 272 |  |  | New Upgrade
PJM WEST | s3843.2 | Construct new 765 kV transmission line from the existing ComEd Collins 765 kV substation to an interconnection point with MISO near the Illinois/Wisconsin state border. | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 521.6 |  |  | New Upgrade
PJM WEST | s3843.1 | Expand and reconfigure the existing ComEd Collins 765 kV substation to install bus positions for two new 765 kV transmission lines, two new 300 MVAR line reactors with dedicated circuit breakers for each of the two new outgoing 765 kV lines and two single-phase spare 765 kV reactors (one for each new 765 kV transmission line). | ComEd |  |  | Other |  |  | EP | 11/4/2025 | 11/4/2025 | 73.6 |  |  | New Upgrade
PJM MA | s3850.1 | Extend a new circuit 69kV tap from the existing Clinton-Muncy 2 69kV line to independently interconnect the Hughesville Transformer 2. Customer substation. Build 3.1 miles of new 69kV single circuit line using 556 ACSR conductor. | PPL |  |  | Customer Service |  |  | PL | 12/11/2025 | 12/11/2025 | 7.3 | 7.3 |  | New Upgrade
PJM WEST | s3767.1 | Add one (1) new 69 kV bus tie-breaker and two (2) new 69 kV circuit switchers on the high-side of the distribution transformers and associated relaying. Upgrade all station equipment, including but not limited to, bus conductor, breaker leads, and switches so all series elements on the 69 kV are greater than or equal to 1200 A. Addition of bus-tiebreaker and circuit switchers will add new zones of protection to limit the overall tripping footprint of bus and transformer faults. | AMPT |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 8/15/2025 | 8/15/2025 | 3.2 |  |  | New Upgrade
PJM WEST | s3832.6 | Existing metering on the E Wooster-Orrville line (today's line name) is limited to 69 MVA, due to revenue metering at E Wooster sub. AEP to replace revenue metering at E Wooster, with Interconnection metering. CT's will be rated for higher than the 138kV line capacity. | AMPT |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 0.5 |  |  | New Upgrade
PJM WEST | s3832.5 | Relocate and reconstruct the 138 kV line between Apple Ave and Mineral Springs subs. | AMPT |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 3.541 |  |  | New Upgrade
PJM WEST | s3832.4 | Rebuild Orrville's Power Plant sub at a new location, to be called Mineral Springs sub. Construct a 4-cb 138 kV ring bus to terminate the two 138 kV lines and two 138/13 kV transformers. Work to include grading, fence, and new control house. The existing Power Plant sub has no space for the required 138 kV infrastructure. | AMPT |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 10.5 |  |  | New Upgrade
PJM WEST | s3832.3 | Expand Apple Ave sub to accomodate the new 138kV line to First Energy | AMPT |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 15.2 |  |  | New Upgrade
PJM WEST | s3832.2 | Construct a 138kV switchyard, intersecting the Star-Cloverdale 138 kV line. Provide a line terminal for the new Apple Ave-(new FE sub) line. | AMPT |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 18.4 |  |  | New Upgrade
PJM WEST | s3832.1 | Construct a new 138kV line from Apple Ave sub to FE's new switchyard on the Star-Cloverdale line. | AMPT |  |  | Customer Service^Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 20.6 |  |  | New Upgrade
PJM WEST | s3780.1 | Convert the Firestone three-breaker ring bus into a four-breaker ring bus by installing an additional circuit breaker to the existing substation layout. | ATSI |  |  | Operational Flexibility and Efficiency^Equipment Material Condition, Performance and Risk^Infrastructure Resilience |  |  | EP | 9/19/2025 | 9/19/2025 | 0.3 |  |  | New Upgrade
PJM WEST | s3779.1 | Expand the existing 138 kV bus at Tusc Substation from a four-breaker ring bus into a sixbreaker ring bus. Loop the Pine-Wadsworth 138 kV Line in/out of the Tusc Substation ring bus. The project will split the Pine-Wadsworth 138 kV Line to create the following two lines: Tusc - Wadsworth 138 kV Line (~8 miles) Pine - Tusc 138 kV Line (~7 miles) Adjust relays at the terminal ends. | ATSI |  |  | Operational Flexibility and Efficiency^Equipment Material Condition, Performance and Risk^Infrastructure Resilience |  |  | EP | 9/19/2025 | 9/19/2025 | 16.72 |  |  | New Upgrade
PJM WEST | s3778.1 | At Oak Mound Substation: Replace relaying. At Quiet Dell Substation: Replace disconnect switches, wave trap, line turner and coax, CVT and relaying. | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/19/2025 | 9/19/2025 | 2.63 |  |  | New Upgrade
PJM WEST | s3777.1 | At Oak Mound Substation: Install one prefabricated control building, surge arresters, CTs, circuit breakers, disconnect switches, substation conductor, line trap, line tuner, CVT and relaying. At Quiet Dell Substation: Install surge arresters. At Glen Falls Substation: Replace circuit breaker, line trap/CCVT, line tuner and relaying. | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/19/2025 | 9/19/2025 | 13.35 |  |  | New Upgrade
PJM WEST | s3776.1 | Construct a new FirstEnergy owned control building at Kammer Substation to house all relaying for FirstEnergy assets. Install prefabricated control enclosure with new relaying. Replace 765 kV disconnect switch on the high side of the Kammer No. 200 765/500 kV transformer with a 765 kV SCADA controlled switch. Replace 500 kV disconnect switch on the low side of the Kammer No. 200 765/500 kV transformer with a 500 kV circuit breaker. Kammer No. 200 765/500 kV Transformer Ratings: No change in ratings | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/9/2025 | 9/9/2025 | 9.25 |  |  | New Upgrade
PJM WEST | s3775.1 | Ivanhoe – Packard 138 kV Line tap: Install two main-line SCADA controlled switches. Install one tap-line SCADA controlled switch. Construct 0.2 miles of 138 kV line extension. Adjust relay settings at Ivanhoe and Packard substations. Install revenue metering. | ATSI |  |  | Customer Service |  |  | EP | 8/15/2025 | 8/15/2025 | 1.92 |  |  | New Upgrade
PJM WEST | s3774.1 | Carlisle Substation: Replace line relays, CCVTs, line arresters, line trap and disconnect switches. Lorain Substation: Replace line relays, CCVT, wave trap, and disconnect switches. | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/15/2025 | 8/15/2025 | 3.58 |  |  | New Upgrade
PJM WEST | s3773.1 | Rebuild Gore – Hampshire 138 kV Line approximately 6.4 miles and install new conductor. At Gore Substation, replace substation conductor and disconnect switches. At Hampshire Substation, replace substation conductor. | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/15/2025 | 8/15/2025 | 23.12 |  |  | New Upgrade
PJM WEST | s3772.1 | Rider - Weston 138 kV Line tap: Install two main-line SCADA controlled switches. Install one tap SCADA controlled switch. Construct 0.1 miles of 138 kV line extension. Adjust relay settings at Rider and Weston substations. Install revenue metering. | APS |  |  | Customer Service |  |  | EP | 8/15/2025 | 8/15/2025 | 0.92 |  |  | New Upgrade
PJM WEST | s3771.1 | Replace 138 kV disconnect switches, line trap, substation conductor, line tuners, CCVT, and relaying at Weirton Substation. Replace 138 kV circuit breakers, disconnect switches, line trap, substation conductor, CCVT, and relaying at Wylie Ridge Substation. | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/15/2025 | 8/15/2025 | 4.5 |  |  | New Upgrade
PJM WEST | s3770.1 | Replace 138 kV relaying at Leadsville Substation. Replace 138 kV circuit breaker, line tuner and coax, CVT, and relaying at Loughs Lane Substation. | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/15/2025 | 8/15/2025 | 2.3 |  |  | New Upgrade
PJM WEST | s3769.1 | Homer – Wellington 69 kV Line: Install two main-line switches and one tap switch. Construct approximately 0.1 miles of 69 kV transmission line. Adjust relay settings at Homer and Wellington substations. Install revenue metering. | APS |  |  | Customer Service |  |  | EP | 7/18/2025 | 7/18/2025 | 0.9 |  |  | New Upgrade
PJM WEST | s3768.1 | Crossland - Sharon 138 kV Z-112 Line: Install one main-line switch and one tap switch. Construct approximately 200 feet of transmission line. Adjust relay settings at Crossland and Sharon substations. Install revenue metering. | APS |  |  | Customer Service |  |  | EP | 7/18/2025 | 7/18/2025 | 0.9 |  |  | New Upgrade
PJM WEST | s3842.1 | Rebuild the ~8 mile 69 kV single circuit line utilizing 556 ACSR conductor between Structure 1 and Mousey Switch. Component includes Install / Removal and ROW expansion of existing easements | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 19.1742 |  |  | New Upgrade
PJM MA | s0980.1 | Upgrade the Ocean City 12 kV to 138/12 kV substation, and install two 138/12 kV transformers | AEC |  |  | Customer Service |  |  | EP | 7/29/2015 | 7/29/2015 | 64 |  |  | Scope/Cost Change
PJM WEST | s3839.4 | Protection and controls upgrades at East Elkhart station. | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 0.54394 |  |  | New Upgrade
PJM MA | s0980.2 | Build two new 138 kV feeders from BL England and Merion to the Ocean City substation | AEC |  |  | Customer Service |  |  | EP | 7/29/2015 | 7/29/2015 | 0 |  |  | Scope/Cost Change
PJM MA | s0980.3 | Establish a new Ocean City terminal at BL England 138 kV substation | AEC |  |  | Customer Service |  |  | EP | 7/29/2015 | 7/29/2015 | 0 |  |  | Scope/Cost Change
PJM WEST | s3839.3 | Protection and controls upgrades at Capital Avenue station | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 0.40408 |  |  | New Upgrade
PJM MA | s0980.4 | Establish a new Ocean City terminal at Merion 138 kV substation | AEC |  |  | Customer Service |  |  | EP | 7/29/2015 | 7/29/2015 | 0 |  |  | Scope/Cost Change
PJM WEST | s3839.2 | Install 0.2 miles of 138kV line into the new Cleveland station structure location | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 2.3092 |  |  | New Upgrade
PJM WEST | s3839.1 | Rebuild the existing Cleveland station with a 138kV bus tie breaker and MOABS on the line exits out of the station. Install two 138/13.09 30MVA distribution banks and associated distribution equipment. | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 3.8093 |  |  | New Upgrade
PJM WEST | s3837.1 | Replace transformer #3 with 138/69/34.5kV three winding 90MVA unit and install associated low side 69kV circuit breaker. Additionally, install high side 69kV circuit breaker on Transformer #4 and replace 138kV capacitor bank circuit switcher AA with circuit breaker, remove 138kV bus tie switch X3 and replace obsolete electro-mechanical, solid state and legacy microprocessor relays with IEDs and relocate to the control building. Retire older control house and add backup station service. | AEP |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | EP | 10/17/2025 | 10/17/2025 | 10.6242 |  |  | New Upgrade
PJM WEST | s3838.3 | Protection and controls settings updates at Notre Dame station | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 0.14332 |  |  | New Upgrade
PJM WEST | s3838.2 | Protection and controls settings updates at Olive station. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 0.12237 |  |  | New Upgrade
PJM WEST | s3838.1 | Install 138kV bus tie, replace 138kV MOAB Y facing Notre Dame, and replace distribution bank T1. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 2.4061 |  |  | New Upgrade
PJM WEST | s3841.1 | Install new 69 kV circuit switcher on the 69 kV capacitor bank at Abert Station. Relocate 69 kV Capacitor bank at Abert Station to create room for the installation of the new capacitor bank circuit switcher. The 69 kV POP Switch will be replaced with a 69 kV Box Bay. Station will be expanded to accommodate the new location of the circuit switcher and capacitor bank. Relaying will be updated the old EM relaying will be retired. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/14/2025 | 11/14/2025 | 3.4 |  |  | New Upgrade
PJM WEST | s3836.3 | Update the relay settings on Sowers - Lockwood Rd circuit at Lockwood Road station. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/17/2025 | 10/17/2025 | 0.1 |  |  | New Upgrade
PJM WEST | s3836.2 | Update the relay settings on Sowers - Lockwood Rd circuit at Sowers station. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/17/2025 | 10/17/2025 | 0.1 |  |  | New Upgrade
PJM WEST | s3836.1 | Rebuild ~14.4 miles of Rob Park-Richland 138kV line asset from the Ohio border near Sowers station to Lockwood Road station. The rebuild will only include Structure 1 – 23 (3.0 miles) and structures 25-103 (11.4 miles). Telecom infrastructure (ADSS) will be installed in the area to support relaying and communication. | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/17/2025 | 10/17/2025 | 35.808 |  |  | New Upgrade
PJM WEST | s3840.3 | Install ~1.0 mile of greenfield 69kV transmission line and fiber to serve the customer facility. | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 2.036 |  |  | New Upgrade
PJM WEST | s3840.2 | Cut-in to Upper-Sandusky - Forest (OP) 69kV line to install Helium Switch to serve the customer | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 1.3253 |  |  | New Upgrade
PJM WEST | s3840.1 | Build a 3-way Auto-sectionalizing POP switch on the Upper Sandusky – Forest 69kV circuit and upgrade remote end relay settings at Forest and Upper Sandusky stations. install metering equipment for the customer. | AEP |  |  | Customer Service |  |  | EP | 11/14/2025 | 11/14/2025 | 1.54 |  |  | New Upgrade
PJM MA | s3793.1 | Replace Windy Edge circuit breaker B9 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2025 | 11/13/2025 | 0.7 |  |  | New Upgrade
PJM MA | s3795.1 | Replace Windy Edge Circuit Breaker B29 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2025 | 11/13/2025 | 0.7 |  |  | New Upgrade
PJM MA | s3794.1 | Replace Windy Edge circuit breaker B22 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2205 | 11/13/2205 | 0.7 |  |  | New Upgrade
PJM MA | s3792.1 | Replace Windy Edge circuit breaker B8 | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 11/13/2025 | 11/13/2025 | 0.7 |  |  | New Upgrade
PJM MA | s3783.1 | Replace 9 miles of 110572-A OH circuit with new UG line The estimated cost of the project is $229.7M Line ratings will not change due to remaining OH sections outside Finksburg and Westminster stations | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/15/2025 | 5/15/2025 | 229.7 |  |  | New Upgrade
PJM WEST | n9687.0 | Cooper 161kV breaker replacements | EKPC | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | s3827.1 | Install a new tap point on the existing Logan - Switchback 138 kV line between Baileysville and Trail Fork Stations with a single switch facing the customer. Install a new 138 kV delineation pole to connect the customer to the tap and add low side metering at the customer site. | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 0 |  |  | New Upgrade
PJM WEST | s3830.1 | Rebuild ~2.56 miles of line between the Busch - Lazelle 69 kV and Huntley - Greif 138 kV circuits, utilizing 1033.5 (54/7) ACSR conductor SE 69 kV (206 MVA) 138 kV (411 MVA); this rebuild consist of both single and double circuit sections (~1.18 miles of single circuit and ~1.38 miles of double circuit). | AEP |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/19/2025 | 9/19/2025 | 15.7001 |  |  | New Upgrade
PJM WEST | s3825.1 | Install a new tap point on the existing Bradley - Kanawha 138 kV line with a single switch facing the customer. Low-side metering to be installed at the customer site. Install a new 138 kV delineation pole for the customer to connect to. | AEP |  |  | Customer Service |  |  | EP | 8/15/2025 | 8/15/2025 | 0 |  |  | New Upgrade
PJM WEST | s3828.4 | Install 138kV in-and-out bus with line MOABs. Work on the distribution side includes installing a new 138/12kV transformer. | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 2.3028 |  |  | New Upgrade
PJM WEST | s3828.3 | Retire the existing Elcona Tap Switch 138kV | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 0.19514 |  |  | New Upgrade
PJM WEST | s3828.2 | Reconnect the existing Elcona Tap - Elcona and Elcona Tap - Dunlap branches to bypass the old switch point due to the switch retirement. | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 2.0684 |  |  | New Upgrade
PJM WEST | s3828.1 | Install 2.15 miles of single circuit 138kV line from near Elcona Tap to Elcona, creating the East Elkhart - Elcona 138kV circuit | AEP |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/19/2025 | 9/19/2025 | 13.5621 |  |  | New Upgrade
PJM WEST | s3829.4 | Construct ~1.5 miles of greenfield single circuit 69kV transmission line from Erin Hills Switch to the customer’s station | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 5.7114 |  |  | New Upgrade
PJM WEST | s3829.3 | Cut-in to the Harrison - Madison 69 kV circuit and connect it to Erin Hills Switch | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 2.2259 |  |  | New Upgrade
PJM WEST | s3829.2 | Install 1 – 69kV cap bank (10.8 MVAR) with a 420A 18kA cap switcher at Harrison station. | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 1.3477 |  |  | New Upgrade
PJM WEST | s3829.1 | Install a 69 kV, 1200A 3-way phase-over-phase switch with MOAB switches | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 1.7302 |  |  | New Upgrade
PJM WEST | s3831.3 | Install phase over phase switch cut into the Sunnyside - Carrollton 138 kV circuit | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 1.101 |  |  | New Upgrade
PJM WEST | s3831.2 | Build ~0.1-mile extension from the switch structure to the customer substation | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 0.44603 |  |  | New Upgrade
PJM WEST | s3831.1 | Cut into the Sunnyside - Carrollton 138 kV circuit to install new phase over phase switch to the customer substation | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 0.90753 |  |  | New Upgrade
PJM WEST | s3826.3 | Install a new phase over phase switch to replace the existing hard tap. | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 0.58 |  |  | New Upgrade
PJM WEST | s3826.2 | Install roughly 0.2 miles of new 69kV line to connect the delivery point to the new phase over phase switch. | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 0.97 |  |  | New Upgrade
PJM WEST | s3826.1 | Install roughly 0.8 miles of new 69kV structures but reuse existing conductor to get the line to the new phase over phase switch location. | AEP |  |  | Customer Service |  |  | EP | 9/19/2025 | 9/19/2025 | 2.44 |  |  | New Upgrade
PJM WEST | s3806.1 | Duke Energy Ohio and Kentucky’s line work is limited to sections between Miami Fort substation and the Ohio/Indiana State border, approximately one mile in circuit length. Replace the single circuit structures on the Miami Fort-Greendale 138 kV circuit with dual-circuit structures. Replace the existing Miami Fort-Greendale conductor with 954 ACSS. Install 954 ACSS for the new circuit to Sutton Ridge. Install a 138 kV, 2000A, 63kA circuit breaker with two 2000A disconnects and three metering class CCVTs to connect the new Sutton Ridge circuit. The new ratings for both circuits will be 480/480 MVA summer, 520/520 MVA winter. | DEOK |  |  | Other | 6/1/2032 |  | EP | 3/14/2025 | 3/14/2025 | 5.3 |  |  | New Upgrade
PJM MA | s3757.1 | Raritan River - Werner 34.5 kV U99 Line Customer Connection Tap the Raritan River - Werner 34.5 kV U99 Line Extend tap line ~200 ft to customer Add SCADA controlled switches Modify relay settings at Raritan River Substation and Werner Substation | JCPL |  |  | Customer Service |  |  | EP | 2/13/2025 | 2/13/2025 | 0.5 |  |  | New Upgrade
PJM MA | s3756.1 | Raritan River - Werner 34.5 kV U99 Line Customer Connection Tap the Raritan River - Werner 34.5 kV U99 Line Extend tap line ~200 ft to customer Add SCADA controlled switches Modify relay settings at Raritan River Substation and Werner Substation | JCPL |  |  | Customer Service |  |  | EP | 2/13/2025 | 2/13/2025 | 0.7 |  |  | New Upgrade
PJM MA | s3759.1 | Old Bridge - Raritan River 34.5 kV Q69 Line Customer Connection: Tap the Old Bridge - Raritan River 34.5 kV Q69 Line on the Red Oak Tap line section Extend tap line 0.3 miles to customer POI Add SCADA controlled switches Modify relay settings at Old Bridge & Raritan River substations | JCPL |  |  | Customer Service |  |  | EP | 4/10/2025 | 4/10/2025 | 0.1 |  |  | New Upgrade
PJM MA | s3758.1 | Oceanview – Bradley Beach 34.5 kV D130 Line Customer Connection Tap the Belmar - Bradley Beach - Oceanview 34.5 kV D130 Line Extend tap line 0.1 miles to customer Add SCADA controlled switches Modify relay settings at Belmar, Bradley Beach, and Oceanview substations | JCPL |  |  | Customer Service |  |  | UC | 3/13/2025 | 3/13/2025 | 1.87 |  |  | New Upgrade
PJM MA | s3782.1 | Atlantic – Long Branch 34.5 kV P42 Line Customer Connection - 34.5 kV line loop and ring bus: Construct a four breaker 34.5 kV ring bus. Loop the Atlantic – Long Branch 34.5 kV P42 Line into the new substation. The loop is approximately 0.1 miles in length. Modify relay settings at Atlantic Substation and Long Branch Substation. | JCPL |  |  | Customer Service |  |  | EP | 9/19/2024 | 9/19/2024 | 8.1 |  |  | New Upgrade
PJM MA | s3760.1 | Briant Park – Traynor 34.5 kV I35 Line Customer Connection: Tap the Briant Park – Traynor 34.5 kV I35 Line and extend approximately one span to customer. Add one SCADA controlled in-line switch toward Traynor Substation and one SCADA controlled switch on tap toward customer. Modify relay settings at Briant Park and Traynor substations. | JCPL |  |  | Customer Service |  |  | EP | 6/12/2025 | 6/12/2025 | 0.5 |  |  | New Upgrade
PJM WEST | s3734.8 | Russia Station: Expand the existing ring bus at Russia substation to accommodate the new line to Water Street. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 4 |  |  | New Upgrade
PJM WEST | s3734.7 | Baker Rd Station Build new 3 breaker ring bus at Baker Rd. Retire Water Street Tap. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 11.2 |  |  | New Upgrade
PJM WEST | s3734.6 | Water Street - Russia 69 kV: Build approximately 5.5 miles of new single circuit 69kV line using 795 ACSR Drake conductor from the Water Street 69 kV sub to the AES Russia sub. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 11 |  |  | New Upgrade
PJM WEST | s3734.5 | Build approximately .8 miles of new single circuit 69kV line using 795 ACSR Drake conductor from the Greenlawn 69 kV sub to the new Baker Road sub. Install a line sectionalizing MOAB toward Baker Rd. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 3.9 |  |  | New Upgrade
PJM WEST | s3734.4 | Build approximately 6.0 miles of new single circuit 69kV line using 795 ACSR Drake conductor from the Greenlawn 69 kV sub to the new Subler Drive sub. Install line sectionalizing MOAB toward Subler Dr. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 15.1 |  |  | New Upgrade
PJM WEST | s3734.3 | Build approximately 1.2 miles of new single circuit 69kV line using 795 ACSR Drake conductor from the Water Street 69 kV sub to the new Subler Drive sub. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 3.8 |  |  | New Upgrade
PJM WEST | s3734.2 | Water Street 69 kV Rebuild existing Water Street 69 kV station to a three breaker ring bus to accommodate two 69 kV lines and one distribution transformer. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 9.3 |  |  | New Upgrade
PJM WEST | s3734.1 | Subler Drive 69 kV Build a new greenfield 69 kV station with two 69 kV circuit breakers and associated relays. Station should be able to accommodate one new distribution transformer. | AMPT |  |  | Customer Service |  |  | EP | 2/14/2025 | 2/14/2025 | 8.3 |  |  | New Upgrade
PJM WEST | s3755.1 | Tap the Dutch Fork - Windsor 138 kV Line at/near structure 122. Install two 1200 A SCADA controlled switches at tap location Construct approximately 0.9 miles of line to the interconnection point Install 138 kV revenue metering package Adjust relay settings at Dutch Fork and Windsor substations | APS |  |  | Customer Service |  |  | IS | 4/11/2025 | 4/11/2025 | 5.8 |  |  | New Upgrade
PJM WEST | s3608.7 | Modify the existing Fall Creek- Sunnyside 345kV line for greenfield Madison County station to cut in. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3608.6 | At Sullivan 345kV station, modify Sullivan 345kV to interconnect new 345kV lines Sullivan-Fairbanks 345kV #1, Sullivan-Fairbanks #2, Sullivan-Dresser 345kV #1, Sullivan-Dresser 345kV #2. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3608.5 | At Sorenson 765kV Station, modify Sorenson station to interconnect new 765kV lines Sorenson-Greentown 765kV and Sorenson-Lulu 765kV. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3608.4 | Modify the existing double circuit 345kV line Olive-University Park and Olive-Green Acres 345kV to cut into Babcock 345kV station. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3608.3 | Modify the existing Tanners Creek - Hanna 345kV line for Gwynneville station to cut in. Modify the future Gwynneville-Tanners Creek 345kV line for existing station Batesville to cut in. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3608.2 | Modify the existing Jefferson-Greentown 765kV line for Gwynneville station to cut in. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3608.1 | Modify the existing Sullivan-Rockport 765kV line for greenfield Pike County station to cut in. | AEP |  |  | Other |  |  | EP |  |  | 0 |  |  | New Upgrade
PJM WEST | s3765.1 | Cut into the Kenzie Creek - Valley 138kV line and install a new 138kV phase over phase switch to serve approximately 5.14 MVA of new load. AEP will own the first span to the structure inside the customer's station. Fiber will be installed on the new line and metering will be installed on the low side of the transformer. | AEP |  |  | Customer Service |  |  | EP | 7/18/2025 | 7/18/2025 | 3.7195 |  |  | New Upgrade
PJM WEST | s3762.1 | Reconductor the Hannibal - North Sub 138 kV circuit using 1033 ACSS 54/7 CURLEW to accommodate increased customer loading at North Sub Station. | AEP |  |  | Customer Service |  |  | On Hold | 2/14/2025 | 2/14/2025 | 0.39158 |  |  | New Upgrade
PJM WEST | s3763.1 | Construct a new station in a breaker and a half configuration consisting of eleven (11) 345kV 5000A 63kA breakers, two (2) 345kV meters, and station fiber cable to serve 437MW of new load. Construct two (2) 345kV bus ties from AEP's Navistar 345kV station to the customer station. Cut in the Dumont - New Prairie #1 and #2 345kV circuits into the new station. | AEP |  |  | Customer Service |  |  | EP | 4/1/2025 | 4/1/2025 | 50.3641 |  |  | New Upgrade
PJM WEST | s3764.2 | Bring the Edison - Creek Walker 138kV line into Olive station and install three (3) new 138kV 3000A 63kA breakers to complete the "K" string and create a new line exit position. | AEP |  |  | Customer Service |  |  | EP | 4/11/2025 | 4/11/2025 | 19.1084 |  |  | New Upgrade
PJM WEST | s3764.1 | Construct a new station in a ring bus configuration consisting of six (6) 138kV 3000A 40kA breakers, three (3) 138/13.8kV 50 MVA LTC transformers, three (3) 13.8kV meters and other associated distribution equipment, and station fiber cable to serve 90MW of new load. Cut into the Olive - Edison 138kV line and construct 2.8 miles of new double circuit 138kV line to the new station. | AEP |  |  | Customer Service |  |  | EP | 4/11/2025 | 4/11/2025 | 11.355 |  |  | New Upgrade
PJM MA | s3754.2 | Construct a 69-13kV Substation in the Mount Laurel Area. o Purchase property and construct a 69kV substation at Briggs Rd. o Install two (2) 69-13kV transformers. o Cut and loop Mount Holly – Lumberton 69kV circuit into new substation. o Add 69kV position to the substation at Cox’s Corner. o Construct one (1) new 69kV line from Cox’s Corner to new substation. | PSEG |  |  | Customer Service |  |  | Cancelled | 9/9/2025 | 9/9/2025 | 129.7 |  |  | Cancelled
PJM WEST | s3750.4 | Install 5x double circuit 138kV ~0.75 mile radials to customer owned stations from Zodiac station with fiber. | AEP |  |  | Customer Service |  |  | EP | 11/6/2024 | 11/6/2024 | 28.5 |  |  | New Upgrade
PJM WEST | s3750.3 | Cut into 2x existing double circuit 138kV lines, (4x circuits total) and install 4x double circuit 0.2 mile extension to new Zodiac 138kV station. Rebuild both ~3.7 mile 138kV double circuit lines from Allen-Zodiac Station (~7.4 mile double circuit total). | AEP |  |  | Customer Service |  |  | EP | 11/6/2024 | 11/6/2024 | 44 |  |  | New Upgrade
PJM WEST | s3750.2 | Install greenfield 138kv breaker and a half station. Zodiac 138kV station will include 8-138kV AEP circuit exits and customer terminations to 5 customer buildings. | AEP |  |  | Customer Service |  |  | EP | 11/6/2024 | 11/6/2024 | 38.1 |  |  | New Upgrade
PJM WEST | s3750.1 | Expand Allen station with 2x additional 345/138kV transformers. Install 3x 345kV breaker and 3x 138kV breaker for transformer protection. Land purchase for station expansion is included. The transformers are added for overloads identified under N-1-1 analysis for loss of Robison Park Transformer #5 and Allen Transformer #2, or N-1-1 loss of both existing transformers at Allen station. | AEP |  |  | Customer Service |  |  | EP | 11/6/2024 | 11/6/2024 | 58.5 |  |  | New Upgrade
PJM MA | s3743.2 | Carlisle Pike-Gardners 115 kV 976 Line Rebuild: Rebuild 7.5 miles of transmission line (Penelec Portion) | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/14/2025 | 8/14/2025 | 20.5 |  |  | New Upgrade
PJM MA | s3749.1 | Replace West Wharton 230-34.5 kV No. 2 Transformer | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/9/2025 | 9/9/2025 | 12 |  |  | New Upgrade
PJM MA | s3748.1 | Replace West Wharton 230-34.5 kV No. 1 Transformer | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/9/2025 | 9/9/2025 | 12 |  |  | New Upgrade
PJM MA | s3747.1 | Convert Spangler Substation 46 kV yard into a five-breaker ring bus. Replace 115/46 kV No. 2 Transformer. | PENELEC |  |  | Operational Flexibility and Efficiency^Equipment Material Condition, Performance and Risk |  |  | EP | 9/18/2025 | 9/18/2025 | 14.2 |  |  | New Upgrade
PJM MA | s3746.1 | Convert the Morgan Street 115kV Substation into a nine-breaker, breaker-and-a-half substation | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/18/2025 | 9/18/2025 | 26.91 |  |  | New Upgrade
PJM MA | s3745.1 | Convert the Edinboro South 115 kV Substation into a four-breaker ring bus | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | EP | 9/18/2025 | 9/18/2025 | 13.57 |  |  | New Upgrade
PJM MA | s3744.1 | Warrior Ridge - Huntingdon - Owens Corning 46 kV Line Rebuilds | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/14/2025 | 8/14/2025 | 5.1 |  |  | New Upgrade
PJM MA | s3743.1 | Carlisle Pike-Gardners 115 kV 976 Line Rebuild: Rebuild 13.0 miles of transmission line (MetEd Portion) | ME |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 8/14/2025 | 8/14/2025 | 32.35 |  |  | New Upgrade
PJM MA | s3742.1 | Install South Reading 230-69 kV No. 9 Transformer | ME |  |  | Operational Flexibility and Efficiency |  |  | EP | 8/5/2025 | 8/5/2025 | 20.4 |  |  | New Upgrade
PJM MA | s1640.2 | Replace Middletown Junction #2 (75 MVA) & #5 (75/84 MVA) 230/115 kV transformers with 180/240/300 MVA units | ME |  |  | Operational Flexibility and Efficiency |  |  | IS | 3/23/2018 | 5/25/2018 | 0 | 0 |  | Scope/Cost Change
PJM MA | s1769.1 | Dubois – Harvey Run – Whetstone 115 kV Line: Rehab approximately 14.25 miles of wood pole construction. Reconductor approximately 10.1 miles of existing transmission line | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/29/2018 | 10/6/2026 | 5.3 | 39.3 |  | Scope/Cost Change
PJM MA | b4036.17 | Reconfigure the Sunbury 500 kV substation. Install new 500 kV circuit breaker at bay 4 and move T24 to bay 4 making it breaker and half configuration. | PPL |  | 2025-W1-237 | Baseline Load Growth Deliverability & Reliability | 6/1/2031 |  | EP | 1/6/2026 | 1/6/2026 | 4.98 | 30 | 2/12/2026 | Scope/Cost Change
PJM MA | b4036.15 | *Final scope is subject to change Install two new 500 kV circuit breaker at North and south bus to terminate the 765-500 kV transformers leads. Upgrade protection settings at Juniata (PPL work). Build new Juniata 500 kV station adjacent to the existing Juniata station and re-terminate a portion of the 500 kV transmission lines at the new substation. | PPL |  | 2025-W1-237 | Baseline Load Growth Deliverability & Reliability | 6/1/2031 |  | EP | 1/6/2026 | 1/6/2026 | 9.95 | 131.53 | 2/12/2026 | Scope/Cost Change
PJM MA | s1775.2 | Summit - Construct a 46 kV breaker-and-a-half station with eight breakers | PENELEC |  |  | Equipment Material Condition, Performance and Risk^Operational Flexibility and Efficiency |  |  | IS | 10/29/2018 | 10/29/2018 | 26.8 |  |  | Scope/Cost Change
PJM MA | s3733.1 | Construct an eight-breaker breaker-and-a-half switchyard for the 115 kV bus at Roundtop Substation | ME |  |  | Operational Flexibility and Efficiency |  |  | EP | 8/14/2025 | 8/14/2025 | 22.1 |  |  | New Upgrade
PJM MA | s1809.1 | Construct a four breaker 230 kV ring bus at Morristown | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 11/28/2018 | 11/28/2018 | 73.7 |  |  | Scope/Cost Change
PJM MA | n9685.0 | Upgrade/Replace Wave Trap at Keystone on the Keystone-Cabot 500kV line. | PENELEC |  |  |  |  | 3/16/2029 | EP | [5 empty] | New Upgrade
PJM MA | n9684.0 | Rebuild 5.95 mi of AE2-211_Tap - Jackson 230 kV Line | ME |  |  |  |  | 3/16/2029 | EP | [5 empty] | New Upgrade
PJM MA | n9683.0 | Rebuild 12.09 mi of the TMI – AE2-211_Tap 230 kV Line | ME |  |  |  |  | 3/16/2029 | EP | [5 empty] | New Upgrade
PJM WEST | n9682.0 | Perform sag mitigation on the Powerton - Tazewell 345 kV Line and replace disconnect switches at Powerton substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 5.0174 |  |  | New Upgrade
PJM MA | s1919.1 | Build a four breaker 115 kV ring bus at the Philipsburg substation. | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | UC | 5/31/2019 | 11/19/2019 | 14.7 |  |  | Scope/Cost Change
PJM MA | s1919.4 | Replace line trap on Philipsburg 115 kV line exit at the Shawville substation and adjust line relaying as necessary. | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | UC | 5/31/2019 | 11/19/2019 | 2.7 |  |  | Scope/Cost Change
PJM MA | s2024.1 | Replace Bells Mill Rd T6 230/138 kV transformer | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/31/2019 | 7/31/2019 | 5 |  |  | Scope/Cost Change
PJM MA | s2024.2 | Replace Bells Mill Rd T4 230/138 kV transformer | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 7/31/2019 | 7/31/2019 | 5 |  |  | Scope/Cost Change
PJM WEST | n9680.0 | Sag mitigation - Remove and replace sixteen (16) existing double circuit towers with taller double circuit custom steel poles. (Towers 11, 14, 45, 47, 52, 57, 59, 61, 63, 66, 67, 71, 77, 84, 91, and 96). Remove and replace two (2) existing river crossing lattice towers with taller lattice structures. (Towers 2 and 140) | OVEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 24.006 |  |  | New Upgrade
PJM SOUTH | s3675.1 | Cut and loop future 230kV line between proposed Thicket substation and proposed Saltwood substation in and out of proposed Bunker substation. Lines to terminate in a 230kV four-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | EP | 1/7/2025 | 1/7/2025 | 13.4 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s3674.1 | Extend two 230kV lines from proposed Thicket substation to proposed Saltwood substation. Lines to terminate in a 230kV six-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | EP | 1/7/2025 | 1/7/2025 | 19 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3729.5 | Install cap bank at 69kV Kenilworth Data Center | PSEG |  |  | Customer Service |  |  | UC | 3/13/2025 | 3/13/2025 | 4.65 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3729.4 | Install cap bank at 69kV Galloping Hill | PSEG |  |  | Customer Service |  |  | EP | 3/13/2025 | 3/13/2025 | 6.15 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3729.3 | Install cap bank at 69kV Roselle | PSEG |  |  | Customer Service |  |  | UC | 3/13/2025 | 3/13/2025 | 4.35 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3729.2 | Construct a new 69kV circuit from the new customer substation to Stanley Terrace substation. (New circuit in-service date 06/2029) | PSEG |  |  | Customer Service |  |  | UC | 3/13/2025 | 3/13/2025 | 36 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3729.1 | Cut and loop the 69kV (prior approved) line from Roselle to Galloping Hill into the customer’s new substation. (Station In-Service date 06/2026) | PSEG |  |  | Customer Service |  |  | EP | 3/13/2025 | 3/13/2025 | 15.65 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s3701.1 | Construct Allman Switching Station north of existing Fredericksburg Substation, to accommodate ten, 230kV line terminals (six north, four south) in five strings of a breaker-and-a-half arrangement. GIS equipment will be utilized due to limited space. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 8/6/2024 | 8/6/2024 | 60 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s3684.7 | For the conversion of line from 115 kV to 230 kV, a new breaker must be added at the 230 side in Remington station. Also, the 115 side of the line #70 should be removed. | Dominion |  |  | Customer Service |  |  | EP | 2/4/2025 | 2/4/2025 | 2.8 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s3684.5 | Oak green is currently a 115 kV sub. When Line #1065 is converted, we need to expand Oak Green. Due to space constraints at existing station, Oak Green is relocated. | Dominion |  |  | Customer Service |  |  | EP | 2/4/2025 | 2/4/2025 | 43.8 |  | 11/18/2025 | Scope/Cost Change
PJM WEST | s2211.1 | Locust Ring Bus - Install four 69kV breakers in a ring bus configuration. Split the main feeder into two circuits. Terminate the two new main feeder circuits and the feeder to McGuffey each into their own position on the ring. | DEOK |  |  | Customer Service |  |  | IS | 3/19/2020 | 3/19/2020 | 7.6424 |  |  | Scope/Cost Change
PJM MA | s3617.1 | Chester No. 4 230-34.5 kV Transformer: Replace No. 4 230-34.5 kV Transformer at Chester Substation. Replace associated 230 kV Circuit Switcher Replace associated 34.5 kV Breaker. Replace Limiting Terminal Components. | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/4/2025 | 3/4/2025 | 7.3 |  | 11/18/2025 | Scope/Cost Change
PJM WEST | s3703.1 | Build a new 138 kV, 6-breaker ring bus substation named Front Street. Connect Front Street to West End with two feeders landing in non-adjacent positions, acting as a loop. In the remaining four positions install 138/13 kV, 33 MVA transformers to support four independent distribution bus sections each connecting three feeders and two switched 3.6 MVAR capacitors. At West End, install four 138 kV circuit breakers to create positions for the two feeders to Front. The feeders are each approximately 350 feet long, will be constructed of 954 ACSS conductor, and have capacities of 301/301 MVA summer, 378/378 MVA winter. | DEOK |  |  | Customer Service |  |  | EP | 4/11/2025 | 4/11/2025 | 41.9155 |  |  | Scope/Cost Change
PJM SOUTH | s2324.6 | Reconductor 230kV line segment between Sully and Takeoff using a standard high-capacity conductor (approx. 1.16 miles) | Dominion |  |  | Customer Service |  |  | EP | 2/9/2021 | 2/9/2021 | 1.74 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s2328.7 | Re-conductor the 230kV Line 2209 from Evergreen Mills to Yardley Ridge (0.16 miles) using a higher capacity conductor as well as terminal equipment upgrades to achieve an expected rating of 1574 MVA. | Dominion |  |  | Customer Service |  |  | UC | 10/6/2020 | 10/6/2020 | 5 |  |  | Scope/Cost Change
PJM SOUTH | s3698.1 | Install a 230kV circuit switcher, high side switch, and any associated transmission equipment and bus work needed for new 230/34.5kV transformer. | Dominion |  |  | Customer Service |  |  | IS | 11/6/2024 | 11/6/2024 | 5 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s3694.1 | Construct Allen Creek 230 kV substation with 4-breaker ring bus configuration. Customer will pay excess facility charges to install 6 more breakers. Cut Line #2258 (Finneywood – Cloud) and extend two 230kV lines to Allen Creek switching station. | Dominion |  |  | Customer Service |  |  | Cancelled | 7/9/2024 | 7/9/2024 | 30 |  | 11/18/2025 | Cancelled
PJM SOUTH | s3693.1 | Interconnect the new Devlin substation by cutting and extending Line #2163 (Vint Hill – Dawkins Branch) to the proposed Devlin Substation. Terminate both ends into a GIS 230 kV four-breaker arrangement expandable to an ultimate of nine 230 kV GIS breakers in a breaker-and-a-half scheme. | Dominion |  |  | Customer Service |  |  | UC | 7/9/2024 | 7/9/2024 | 42 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | n9658.0 | Remote end substation work at Twitty's Creek to support new interconnection substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.22097 |  |  | New Upgrade
PJM SOUTH | n9657.0 | Remote end substation work at Pamplin to support new interconnection substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.12857 |  |  | New Upgrade
PJM SOUTH | n9656.0 | Remote end substation work at Farmville to support new interconnection substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.12497 |  |  | New Upgrade
PJM SOUTH | n9655.0 | Remote end substation work at Chase City to support new interconnection substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.12859 |  |  | New Upgrade
PJM MA | n9654.0 | FirstEnergy work at new Interconnection Substation. Install (1) security system and camera system. Install (1) indoor security AC cabinet. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.2122 |  |  | New Upgrade
PJM SOUTH | n9651.0 | Wreck and rebuild 10.05 miles of Line 1059 between Northern Neck and Moon Corner with (2) 768.2 ACSS/TW (20/7) "MAUMEE" at 250 degrees C and replace line leads at Moon Corner (AE1-155) and Northern Neck. | Dominion |  |  |  | 3/31/2029 |  | EP | 11/3/2026 | 11/3/2026 | 28.477 |  |  | New Upgrade
PJM WEST | s3650.1 | Replace two aged 138kV oil breakers with modern breakers. | DL |  |  | Equipment Material Condition, Performance and Risk |  | 5/31/2026 | IS | 3/14/2025 | 3/14/2025 | 2.2 |  | 11/18/2025 | Scope/Cost Change
PJM WEST | n9631.0 | Install new overhead optical ground wire (OPGW) on the existing Summersville - Green County line sections for a total of 4.2 miles. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.061 |  |  | New Upgrade
PJM WEST | n9632.0 | Revise relay settings at Hodgenville Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.068 |  |  | New Upgrade
PJM WEST | n9633.0 | Revise relay settings at Stephensburg Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.068 |  |  | New Upgrade
PJM WEST | n9634.0 | Loop existing Glendale Tap - Stephensburg 69 kV line into new interconnection switching station and install overhead optical ground wire (OPGW) on the tie-ins from South Hardin - Stephensburg 69 kV line section and from the South Hardin - Glendale Tap line section | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.017 |  |  | New Upgrade
PJM WEST | n9393.0 | Timber Switch 138 kV: Review and revise the protective relay settings to account for the additional generation of AF2-376. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM WEST | n9394.0 | Proposed AG1-410 345 kV Station: Review and revise the protective relay settings at the AG1-410 Proposed 345 kV Station to account for the additional generation | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM SOUTH | n9399.0 | Remote Relay at Moon Corner Substation (including fiber) | Dominion | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 0.30742 |  |  | New Upgrade
PJM SOUTH | n9323.0 | Remote Relay at Stone Mill Substation | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.28863 |  |  | New Upgrade
PJM SOUTH | n9324.0 | Transmission Line Tie-in for new single breaker tap switching station for AE2-185 and AF2-404 | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.2576 |  |  | New Upgrade
PJM SOUTH | n9349.0 | Remote relay work at Chesapeake Substation. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.17303 |  |  | New Upgrade
PJM SOUTH | n9350.0 | Expansion of existing Yadkin Substation. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 7.8514 |  |  | New Upgrade
PJM SOUTH | n9460.0 | Remote Relay at Mount Laurel Substation | Dominion | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 0.12053 |  |  | New Upgrade
PJM SOUTH | n9461.0 | Remote Relay at Clay Mills Substation | Dominion | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 0.051902 |  |  | New Upgrade
PJM SOUTH | n9462.0 | Remote Relay at Chase City Substation | Dominion | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 0.051902 |  |  | New Upgrade
PJM SOUTH | n9463.0 | Re-arrange line #33 to loop into and out of the new three-breaker AG1-105 115 kV switching station | Dominion | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 3.1257 |  |  | New Upgrade
PJM SOUTH | n9464.0 | Build a new 115 kV three-breaker ring switching station located along VEPCO’s existing 115 kV, 33 line from Chase City Substation to Clays Mill Substation | Dominion | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 10.9346 |  |  | New Upgrade
PJM WEST | n9472.0 | Remote end upgrades | Dayton | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.0397 |  |  | New Upgrade
PJM WEST | n9473.0 | New Interconnecting Substation | Dayton | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 12.4121 |  |  | New Upgrade
PJM WEST | n9474.0 | Interconnecting Substation tie-in | Dayton | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.0157 |  |  | New Upgrade
PJM WEST | n9485.0 | Loop existing Summer Shade - Green County 161 kV line into new interconnection switching station. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.041 |  |  | New Upgrade
PJM WEST | n9487.0 | Revise Relay Settings at Summer Shade Sub. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.146 |  |  | New Upgrade
PJM WEST | n9488.0 | Revise Relay Settings at Greene County Sub. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.146 |  |  | New Upgrade
PJM MA | n9490.0 | Install/Test approximately 3.12 miles of new 48 count ADSS fiber from the AG1-548 substation control house to the nearest splice point on the Zayo-owned fiber backbone (near 41.914, -79.820). Utilize the Union City to Backbone ADSS fiber cable to create a full fiber path between AG1-548 and Union City. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.79764 |  |  | New Upgrade
PJM MA | n9491.0 | Design, installation, and testing/commissioning for Multiprotocol Label Switching (MPLS) equipment for Supervisory Control and Data Acquisition(SCADA) transport at AG1-548 Substation including: Crossbow engineering and materials, new All-Dielectric Self-Supporting(ADSS) Fiber installation, (1) in-sub fiber run from AG1-548 Substation control house to developer-built fiber run to support communications and control to generator site. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.0487 |  |  | New Upgrade
PJM MA | n9492.0 | The Erie South – Union City 115 kV, PNT-115-RC line will be cut and looped into the new interconnection substation at a point approximately 2.8 miles from Union City substation, between structures 116 and 117. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.3581 |  |  | New Upgrade
PJM MA | n9493.0 | Install new relaying and carrier equipment and modify drawings for line name change at Erie South Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.91274 |  |  | New Upgrade
PJM MA | n9494.0 | Install new relaying and modify drawings for line name change at Union City Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.65687 |  |  | New Upgrade
PJM WEST | n9495.0 | Proposed AF2-177 345 kV, 3M 345 kV, and Jay 345 kV Stations: Install two (2) station exit all dielectric loose tube (ADLT) station exit transitions and two (2) new fiber optic cable paths consisting of a total 6.9 miles of 144 count ADLT cable installed underground in new right of way. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.3777 |  |  | New Upgrade
PJM WEST | n9496.0 | Sorenson - Desoto #2 345 kV Circuit: Construct a new 345 kV breaker and a half station, initially populated with three (3) circuit breakers, expandable to six (6) circuit breakers. • Three (3) 5000A 63 kA circuit breakers with associated control relaying. • Nine (9) 3000A circuit breaker disconnect switches. • Two (2) single phase station service voltage transformers (SSVT). • One (1) 16' x 48' DICM. • Four (4) single phase wave traps, two (2) each on the line exits to the Desoto and Proposed AF1-148 345 kV Stations. • A directional comparison blocking (DCB) protective relaying scheme for the line to the Proposed AF1-148 345 kV Station. • A DCB protective relaying scheme for the line to the Desoto 345 kV Station. • Two (2) 3-phase coupling capacitor voltage transformers (CCVT), one each for the line exits to the Proposed AF1-148 and Desoto 345 kV Stations. • Two (2) A-Frame line exit structures, one each for the line exits to the Proposed AF1-148 and Desoto 345 kV Stations. • Associated conductors (buswork, ground grid, jumpers), telecom terminal equipment, insulators, arresters, foundations, and structures. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 14.9206 |  |  | New Upgrade
PJM WEST | n9497.0 | Sorenson - Desoto #2 345 kV Circuit: Proposed AF2-177 345 kV Station tie-in. • Remove two (2) tower structures (#419 and #421) along with approximately 0.4 miles of existing wire. • Install two (2) new 150’ custom steel, single circuit, single pole dead end structures on concrete piers with anchor bolt cages along the existing Sorenson - Desoto #2 345 kV Circuit. • Install two (2) new 130’ custom steel, single circuit, single pole, running angle structures on concrete piers with anchor bolt cages along the perimeter of the Proposed AF2-177 345 kV station. • Install four (4) spans of double bundle aluminum conductor steel-reinforced (ACSR) 2156 (Bluebird) transmission line conductor with 12/7 Guinea shield wire. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.8558 |  |  | New Upgrade
PJM WEST | n9498.0 | Proposed AF1-148 345 kV Station: • Review and revise the protective relay settings. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM WEST | n9499.0 | Desoto 345 kV Station: • Review and revise the protective relay settings. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM WEST | n9500.0 | Jay 345 kV Station: • Reconfigure the existing ethernet switch, installing one (1) new Small Form-Factor Pluggable (SFP) transceiver. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.070113 |  |  | New Upgrade
PJM WEST | n9501.0 | 3M 345 kV Station: • Reconfigure the existing ethernet switch, installing one (1) new Small Form-Factor Pluggable (SFP) transceiver. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.070113 |  |  | New Upgrade
PJM WEST | n9502.0 | Proposed AF2-177 345 kV, 3M 345 kV, and Jay 345 kV Stations: Final tie in for fiber installation in new right of way. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.37857 |  |  | New Upgrade
PJM WEST | n9360.0 | Perform Relaying Upgrades at ESS K323 CSL | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 0.26349 |  |  | Cancelled
PJM WEST | n9510.0 | Install new overhead optical ground wire (OPGW) on the existing Wayne County - Massingale Road and Massingale Road - Summer Shade 69 kV line sections for a total of 44.2 miles. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 5.457 |  |  | New Upgrade
PJM WEST | n9511.0 | Loop existing Upchurch Tap - Wayne County 69 kV line into new interconnection switching station | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.554 |  |  | New Upgrade
PJM WEST | n9512.0 | Revise Relay Settings at Wayne County Sub | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.063 |  |  | New Upgrade
PJM WEST | n9513.0 | Revise Relay Settings at Summer Shade Sub | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.063 |  |  | New Upgrade
PJM WEST | n9514.0 | Massingale Road Substation: Construct new 69 kV switching station | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 7.05 |  |  | New Upgrade
PJM MA | n9521.0 | Install equipment for anti-islanding scheme at Union City Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.4737 |  |  | New Upgrade
PJM MA | n9522.0 | Install equipment for anti-islanding scheme at Titusville Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.35033 |  |  | New Upgrade
PJM MA | n9523.0 | Install equipment for anti-islanding scheme at Erie South Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.29994 |  |  | New Upgrade
PJM MA | n9524.0 | Install equipment for anti-islanding scheme at Grandview Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.29994 |  |  | New Upgrade
PJM WEST | n9534.0 | Riverville - Gladstone 138 kV and Proposed AG1-124 138 kV Switching Station: Final Tie in for Fiber installation. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.36103 |  |  | New Upgrade
PJM WEST | n9535.0 | Proposed AG1-124 138 kV Switching Station: Install two (2) station exit transitions and two (2) new fiber optic cable paths, one (1) consisting of 0.3 miles of underground 144 count ADLT cable and the other consisting of 0.1 miles of optical ground wire (OPGW) fiber optic shield wire. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.42798 |  |  | New Upgrade
PJM WEST | n9536.0 | Riverville - Gladstone 138 kV Circuit: Proposed AG1-124 138 kV Switching Station tie-in. Install two (2) new steel, 75', double circuit, two-pole dead-end structures on concrete piers with anchor bolt cages, and three (3) spans of ACSR 795 26/7 (Drake) transmission line conductor with 7#8 Alumoweld shield wire in the existing Riverville - Gladstone 138 kV Right of Way, cutting in the proposed AG1-124 138 kV Station in an in-and-out arrangement from an existing structure. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.7549 |  |  | New Upgrade
PJM WEST | n9537.0 | Riverville - Gladstone 138 kV Circuit: Construct a new 138 kV ring bus station; initially populated with three (3) circuit breakers, expandable to four (4) breakers. • Three (3) 138 kV 40 kA circuit breakers with associated control relaying. • One (1) 16' x 27' DICM. • Six (6) breaker disconnect switches. • Three (3) line disconnect motor operated air breaker (MOAB) switches with associated control relaying, one (1) each on the line exits to the AG1-124 collector, Gladstone 138 kV, and Riverville 138 kV stations. • Six (6) single phase CCVTs, three (3) each on the line exits to the Riverville and Gladstone 138 kV Stations. • Two (2) single phase station service voltage transformers (SSVT). • Two (2) Monopole dead-end take off structures, one (1) each for the line exits to Riverville and Gladstone 138 kV Stations. • A direct fiber current differential line protection relay scheme for the line to the Riverville 138 kV Station. • A direct fiber current differential line protection relay scheme for the line to the Gladstone 138 kV Station. • Associated conductors (buswork, ground grid, jumpers), telecom terminal equipment, insulators, arresters, foundations, and structures. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 7.5325 |  |  | New Upgrade
PJM WEST | n9539.0 | Relay and SCADA Updates | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.065203 |  |  | New Upgrade
PJM WEST | n9541.0 | Valley 138 kV Station: Review and revise the protective relay settings to account for the additional generation. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM WEST | n9364.0 | Perform Relaying Upgrades at TSS95 Chestnut | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 0.41596 |  |  | Cancelled
PJM WEST | n9365.0 | Reroute L9515 transmission line for approximately 0.17 miles | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 4.308 |  |  | Cancelled
PJM WEST | n9366.0 | Expand the 345 kV ring bus TSS178 Blue Mound substation with a new breaker and bay position | ComEd | [5 empty] | Cancelled | 11/3/2026 | 11/3/2026 | 15.0706 |  |  | Cancelled
PJM WEST | n9325.0 | Extend existing distribution power 3 miles to tie in the auxilliary power for the new interconnection substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.277 |  |  | New Upgrade
PJM WEST | n9326.0 | Build new fiber path (estimated ~ 4 miles) from TSS 934 Herman Road substation to existing fiber at TSS 155 Nelson substation and new fiber path (estimated ~ 4 miles) from TSS 934 Herman Road substation to existing fiber at TSS 111 Electric Junction substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 4.9311 |  |  | New Upgrade
PJM WEST | n9327.0 | Cut the Nelson - Electric Junction 345 kV line to loop into the new TSS 934 Herman Road interconnection substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 6.4608 |  |  | New Upgrade
PJM WEST | n9328.0 | Perform relay upgrades at TSS 111 Electric Junction substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.75823 |  |  | New Upgrade
PJM WEST | n9329.0 | Perform relay upgrades at TSS 120 Lombard substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.26618 |  |  | New Upgrade
PJM WEST | n9330.0 | Perform relay upgrades at TSS 155 Nelson Substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.75823 |  |  | New Upgrade
PJM WEST | n9331.0 | Install new Integrated Communications Optical Network (ICON) nodes at four (4) remote end substations: STA 6 Byron, TSS 144 Wayne, TSS 937 Lee County and TSS 113 Waterman. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.40741 |  |  | New Upgrade
PJM WEST | n9556.0 | Valley 138 kV Station: Re-termination of the Stinger Circuit in the Valley 138 kV Station. • Remove the existing Stinger - Valley 138 kV Circuit connection to the Valley 138 kV Station by removing one (1) existing 65 ft. wood pole structure (#285) and one (1) span of line conductor with shield wire. • Install one (1) new custom 80 ft. steel, single circuit, single pole dead end structure on a concrete foundation with an anchor bolt cage. • Install one (1) span of ACSR 1033.5 54/7 (Curlew) transmission line conductor with 7#8 Alumoweld shield wire for the new Stinger line exit. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.57695 |  |  | New Upgrade
PJM WEST | n9557.0 | Valley 138 kV Station: Expansion of Station. • One (1) new 3000 A 138 kV 40 kA circuit breaker (breaker “Q”) with breaker control relaying for the Stinger Circuit relocation. • Two (2) new 3-phase 3000 A circuit breaker disconnect switches. • Three (3) single phase capacitor coupled voltage transformers (CCVTs) and associated structures for the Stinger Circuit relocation. • Three (3) single phase Arresters and associated structures for the Stinger Circuit relocation. • One 16 ft. x 18 ft. DICM expansion to the existing Valley 138 kV Station DICM control house. • Dual fiber-based integrated communications optical network multiplexor (ICON MUX) current differential relays for the protection scheme for the re-terminated Stinger Circuit. • Expansion of a 132' section of the Valley 138 kV Station fence by 20' to the East, across from the east side of the middle box bay. • Associated jumpers, insulators, grounding, fiber-optic relaying connectivity & equipment, cables, pull boxes and foundations. • Protection and control settings review for the existing relays at the Valley 138 kV Station and adjustment as needed. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.1665 |  |  | New Upgrade
PJM WEST | n9367.0 | Perform Relay Upgrades at STA4 Quad Cities station | ComEd |  |  |  | 3/15/2029 |  | EP | 11/3/2026 | 11/3/2026 | 0.41361 |  |  | New Upgrade
PJM WEST | n9368.0 | The existing 345 kV line L0403 will be rerouted to accommodate the expansion of TSS 940 Cordova. | ComEd |  |  |  | 3/15/2029 |  | EP | 11/3/2026 | 11/3/2026 | 4.2267 |  |  | New Upgrade
PJM WEST | n9369.0 | Expand existing 345 kV TSS 940 Cordova station from a bus ring switchyard to the ultimate breaker-and-a-half bus configuration. | ComEd |  |  |  | 3/15/2029 |  | EP | 11/3/2026 | 11/3/2026 | 28.5953 |  |  | New Upgrade
PJM WEST | n9558.0 | Stinger 138 kV Station: • One (1) 3000 A 40 kA circuit breaker with associated control relaying. • One (1) breaker disconnect switch. • Two (2) single phase CCVT for the line exit to the Brody 138 kV Station. • Expand the station by 24 ft. x 225 ft to the north. • Review and revision of the protective relay settings for the remainder of the Stinger 138 kV Station. • Associated conductors (buswork, ground grid, jumpers), telecom terminal equipment, insulators, arresters, foundations, and structures. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.1692 |  |  | New Upgrade
PJM WEST | n9564.0 | Jay 138 kV Substation: • Extend the north Bus #1 to the east. • Install one (1) new circuit breaker string with two (2) new 3000 A 138 kV 40 kA circuit breakers with associated control relaying. • Install four (4) new 4000 A circuit breaker disconnect switches. • Expand and extend the southeast corner of the Jay Substation by 170 ft. x 75 ft. to accommodate the relocated capacitor bank and associated equipment. • Relocate capacitor bank AA, circuit breaker AA, and associated equipment to the south side of the Jay 138 kV Bus #2. • Install associated and additional buswork, bus supports, jumpers, insulators, grounding, ground grid extension, SCADA (Supervisory Control and Data Acquisition) connectivity, fiber-optic relaying connectivity & equipment, cables, pull boxes, and foundations. • Review and revise the protective relay settings for the remainder of the Jay 138 kV Substation to account for the addition of the new circuit breakers and the AF2-068 generation source. | AEP |  |  |  | 10/15/2028 |  | EP | 11/3/2026 | 11/3/2026 | 1.4836 |  |  | New Upgrade
PJM WEST | n9568.0 | Fiber Installation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.5302 |  |  | New Upgrade
PJM WEST | n9569.0 | Perform Relaying Upgrades at TSS 964 Clear Creek (L90302) and Sta 21 Kincaid (L2105) | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.43338 |  |  | New Upgrade
PJM WEST | n9570.0 | Cut the STA. 21 Kincaid - Auburn Solar 345kV line (L2105/L9032) to loop into the new TSS 903 Tovey substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 7.4449 |  |  | New Upgrade
PJM WEST | n9571.0 | Extend existing distribution power to tie in the auxilliary power for the new interconnection substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.4915 |  |  | New Upgrade
PJM WEST | n9572.0 | Extend distribution power to tie in the auxiliary power for the new AE1-114 interconnection substation. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.4528 |  |  | New Upgrade
PJM WEST | n9573.0 | Install microwave communication at TSS 923 White Eagle Road and TSS 124 Maryland substations. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.8225 |  |  | New Upgrade
PJM WEST | n9574.0 | Interconnection Substation Tie-in | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 3.5293 |  |  | New Upgrade
PJM WEST | n9575.0 | Remote Relay at TSS124 Maryland | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.70156 |  |  | New Upgrade
PJM WEST | n9576.0 | Remote Relay at TSS119 Lancaster | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.48581 |  |  | New Upgrade
PJM WEST | n9577.0 | Remote Relay at TSS180 Lena | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.14341 |  |  | New Upgrade
PJM WEST | n9578.0 | Remote Relay at TDC 370 Eleroy | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.14341 |  |  | New Upgrade
PJM WEST | n9580.0 | Interconnection Substation Tie-In: Cut and loop Spurlock - North Clark 345 kV line into new insterconnection substation with four (4) total new guyed steel 3-pole dead-end structures. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.449 |  |  | New Upgrade
PJM WEST | n9581.0 | Fiber Installation in Existing ROW: Install overhead optical ground wire (OPGW) on the North Clark - Mason County and Mason County - Spurlock 345 kV line sections for a total of 45 miles. | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 6.916 |  |  | New Upgrade
PJM WEST | n9582.0 | Revise Relay Settings at Spurlock Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.057 |  |  | New Upgrade
PJM WEST | n9583.0 | Revise Relay Settings at North Clark Substation | EKPC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.057 |  |  | New Upgrade
PJM WEST | n9370.0 | Proposed AF1-119 345 kV station:Expansion. • Installation of one (1) new 5000A 63 kA 345 kV circuit breaker and associated control relaying. • Installation of two (2) new 3000 A breaker disconnect switches. • Installation of three (3) single-phase surge arresters on the generation lead to the Proposed AF2-388 collector station. • Associated buswork, bus supports, jumpers, insulators, grounding, SCADA (Supervisory Control and Data Acquisition) connectivity, structures, and foundations. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.3829 |  |  | New Upgrade
PJM WEST | n9585.0 | AG1-410 Proposed 345 kV Station: Install one (1) station exit transition from the AG1-410 proposed 345 kV Station, 0.7 miles of 96 ct all dielectric loose tube (ADLT) fiber cable in new underground right of way, and 0.6 miles of 96 ct all dielectric self supporting fiber optic cable along existing distribution structures to a splice an existing AEP fiber cable. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.32375 |  |  | New Upgrade
PJM WEST | n9586.0 | Maddox Creek - RP Mone 345 kV: Install two (2) station exit transitions and 3.05 miles of OPGW fiber cable along the existing Maddox Creek – RP Mone 345 kV circuit, terminating at the Maddox Creek 345 kV Station. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.98526 |  |  | New Upgrade
PJM WEST | n9587.0 | Van Wert 345 kV: Reconfigure the existing integrated communications optical network at the Van Wert Station, installing a new SFP transceiver. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.02339 |  |  | New Upgrade
PJM WEST | n9588.0 | Maddox Creek 345 kV: • Remove two (2) single phase line traps on the line exit to the AG1-410 proposed 345 kV Station. • Replace the protective relaying scheme at the Maddox Creek 345 kV Station with a dual, fiber-based integrated communications optical network multiplexor current differential scheme. • Reconfigure the existing integrated communications optical network at the Maddox Creek 345 kV Station, installing a new small form-factor pluggable (SFP) transceiver. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.40758 |  |  | New Upgrade
PJM WEST | n9589.0 | Maddox Creek - RP Mone 345 kV: Work required for the new station tie-in. Install two (2) steel, 150’ single circuit, single pole dead end structures on concrete piers with anchor bolt cages in the existing Maddox Creek - RP Mone 345 kV Circuit Right of Way, two (2) additional steel, single circuit, single pole, dead end structures on concrete piers with anchor bolt cages along the perimeter of the AG1-410 proposed 345 kV station, and four (4) spans of double bundle aluminum conductor steel-reinforced (ACSR) 954 (Cardinal) transmission line conductor with 96 fiber optical ground wire shield wire, cutting in the AG1-410 proposed 345 kV station in an in-and-out arrangement. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 2.0021 |  |  | New Upgrade
PJM WEST | n9590.0 | RP Mone 345 kV: Review and revise relay Settings. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.060764 |  |  | New Upgrade
PJM WEST | n9591.0 | Maddox Creek - RP Mone 345 kV: Construct a new 345 kV ring bus station, initially populated with three (3) circuit breakers, expandable to four (4) circuit breakers, including • Three (3) 63 kA circuit breakers with associated control relaying. • One (1) 16' x 48' DICM. • Six (6) motorized breaker disconnect switches. • Two (2) 3-phase coupling capacitor voltage transformers (CCVT), one (1) each on the line exits to the Maddox Creek and RP Mone 345 kV Stations. • Two (2) single phase station service voltage transformers (SSVT). • Two (2) A-Frame line exit structures, one (1) each for the line exits to the Maddox Creek and RP Mone 345 kV Stations. • Two (2) single phase line traps for the line exit to the RP Mone 345 kV Station. • Associated conductors (buswork, ground grid, jumpers), telecom terminal equipment, insulators, arresters, foundations, and structures. • A fiber-based integrated communications optical network multiplexor dual current differential line protective relay scheme for the line to the Maddox Creek 345 kV Station. • A directional comparison blocking (DCB) protective relay scheme for the line exit to the RP Mone 345 kV Station. • The civil work required to develop a site that accommodates the installation of the above station includes grading of a 460' x 350' pad. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 17.0904 |  |  | New Upgrade
PJM WEST | n9592.0 | Proposed AG1-226, Proposed AG1-237, Eugene, and Dequine 345 kV Stations: Final Tie in for Fiber installation in new right of way. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.48061 |  |  | New Upgrade
PJM WEST | n9593.0 | Proposed AG1-226, Proposed AG1-237, Eugene, and Dequine 345 kV Stations: • Install exit transitions at the Proposed AG1-226, Proposed AG1-237, and Eugene 345 kV Stations. • Install a new fiber optic cable path consisting of 25.1 miles of 144 count ADLT cable in new underground right-of-way. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 8.9527 |  |  | New Upgrade
PJM WEST | n9594.0 | Dequine 345 kV Station: Review and revise the protective relay settings. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.054764 |  |  | New Upgrade
PJM WEST | n9595.0 | Proposed AG1-237 345 kV Station: • Review and revise the protective relay settings. • Reconfigure the ICONs, installing SFP transceivers. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.25169 |  |  | New Upgrade
PJM WEST | n9596.0 | Eugene 345 kV Station: Review and revise the protective relay settings. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.27907 |  |  | New Upgrade
PJM WEST | n9597.0 | Eugene - Dequine 345 kV Circuit: Proposed AG1-226 345 kV Station tie-in. • Remove two (2) steel lattice structures, #354 and #355, with associated conductor and shield wire along the existing Eugene – Dequine 345 kV Circuit. • Install two (2) single pole, double circuit, steel dead end structures along the existing Eugene – Dequine 345 kV Circuit. • Install two (2) three pole, single circuit, horizontally configured steel dead end structures for the Dequine – Sullivan 345 kV Circuit. • Install two (2) new steel, 120' single circuit, single pole dead-end structures and two (2) spans of double bundle ACSR 1272 (Pheasant) transmission line conductor ACSR 159 (Guinea) shield wire routing the Eugene – Proposed AG1-237 circuit above the Dequine – Sullivan 345 kV Circuit, cutting in the Proposed AG1-226 345 kV Station in an in-and-out arrangement. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 7.0027 |  |  | New Upgrade
PJM WEST | n9598.0 | Eugene - Deguine 345 kV Circuit: Construct a new 345 kV breaker and a half station, to be operated as a three (3) circuit breaker ring bus, initially expandable to six (6) circuit breakers. • Three (3) 63 kA circuit breakers with associated control relaying. • One (1) 16' x 48' DICM. • Nine (9) motorized breaker disconnect switches. • Six (6) single phase CCVTs, three (3) each on the line exits to the Eugene and Proposed AG1-237 345 kV Stations. • Two (2) single phase station service voltage transformers (SSVT). • Two (2) A-Frame line exit structures, one (1) each for the line exits to Eugene and the Proposed AG1-237 345 kV Stations. • Associated conductors (buswork, ground grid, jumpers), telecom terminal equipment, insulators, arresters, foundations, and structures. • A dual, fiber-based, integrated communications optical network multiplexor (ICON MUX) current differential line protection relay scheme for the line to the Eugene 345 kV Station. • A dual, fiber-based, ICON MUX current differential line protection relay scheme for the line to the Proposed AG1-237 345 kV Station. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 16.052 |  |  | New Upgrade
PJM WEST | n9599.0 | Eugene 345 kV Station: Expansion. • Installation of one (1) terminal riser for the line exit to the AF1-204 generator lead circuit. • Review and revise the protective relay settings for the remainder of the Eugene 345 kV Station. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.39116 |  |  | New Upgrade
PJM WEST | n9332.0 | Extend existing distribution power 2 miles to tie in the auxilliary power for the new interconnection substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.4931 |  |  | New Upgrade
PJM WEST | n9333.0 | Build new fiber path (estimated ~7.5 miles) from TSS 971 Prairie to TSS 123 Marengo substation existing fiber and new fiber path (estimated ~5.5 miles) from TSS 971 Prairie to Garden Prairie area existing fiber | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 6.8177 |  |  | New Upgrade
PJM WEST | n9334.0 | Perform Relaying Upgrades at TSS156 Cherry Valley | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.30633 |  |  | New Upgrade
PJM WEST | n9335.0 | Perform Relaying Upgrades at TSS138 Silver Lake | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.30633 |  |  | New Upgrade
PJM WEST | n9336.0 | Cut the TSS 156 Silver Lake – TSS 138 Cherry Valley 345 kV line to loop intot he new TSS 971 Prairie substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 8.1989 |  |  | New Upgrade
PJM WEST | n9613.0 | Corey 138 kV Station: • Installation of one (1) new 3000A 40 kA 138 kV circuit breaker with associated control relaying. • Installation of one (1) three phase 3000 A circuit breaker disconnect switch. • Installation of one (1) three phase coupling capacitor voltage transformer and associated structures for the line exit to the Hydramatic 138 kV Station. • Installation of one (1) H-frame dead end structure for the line exit to the Hydramatic 138 kV Station. • Installation of associated and additional buswork, bus supports, jumpers, insulators, grounding, and foundations. | AEP |  |  |  | 2/28/2029 |  | EP | 11/3/2026 | 11/3/2026 | 0.80402 |  |  | New Upgrade
PJM WEST | n9337.0 | Fiber multiplexer installation at 6 remote substations: TSS 155 Nelson, TSS 937 Lee County, STA 6 Byron, TSS 144 Wayne, TSS 111 Electric Junction, TSS 113 Waterman | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.79718 |  |  | New Upgrade
PJM WEST | n9338.0 | Extend existing distribution power no more than 1 mile to tie in the auxilliary power for the new interconnection substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.72931 |  |  | New Upgrade
PJM WEST | n9339.0 | Build new fiber path (estimated ~9 miles) from TSS 953 Renner Road to TSS 155 Nelson substation existing fiber and new fiber path (estimated ~4 miles) from TSS 953 Renner Road to TSS 937 Lee County substation existing fiber | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 13.9503 |  |  | New Upgrade
PJM WEST | n9340.0 | Perform Relaying Upgrades at TSS 937 Lee County substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.67965 |  |  | New Upgrade
PJM WEST | n9341.0 | Perform Relaying Upgrades at TSS 155 Nelson substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.67965 |  |  | New Upgrade
PJM WEST | n9342.0 | Cut the L15501 transmission line to loop into the new TSS 953 Renner Road substation | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 8.0998 |  |  | New Upgrade
PJM MA | n9615.0 | Install carrier equipment at Eagle Valley Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.74599 |  |  | New Upgrade
PJM MA | n9616.0 | Install carrier equipment at Shawville Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.7805 |  |  | New Upgrade
PJM MA | n9617.0 | Install a new 115 kV breaker and associated controls direct connection of AG1-090/AG1-377/AG1-378 Generating Facility to the existing Philipsburg Substation. | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.772 |  |  | New Upgrade
PJM WEST | n9618.0 | Revise relay settings Ayersville. | ATSI | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.058252 |  |  | New Upgrade
PJM WEST | n9619.0 | Revise relay settings Midway. | ATSI | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.058252 |  |  | New Upgrade
PJM WEST | n9620.0 | Revise relay settings at Bowling Green No. 2. | ATSI | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.05831 |  |  | New Upgrade
PJM WEST | n9621.0 | Revise relay settings at Sand Ridge. | ATSI | [5 empty] | UC | 11/3/2026 | 11/3/2026 | 0.058252 |  |  | New Upgrade
PJM WEST | n9628.0 | Expand the Davis Creek 138 kV Substation to accommodate the AF2-095 Project | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 1.1668 |  |  | New Upgrade
PJM WEST | n9629.0 | TSS132 Substation Expansion Expand the TSS132 Garden Plain substation to accommodate the AF1-296 Project | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 11.672 |  |  | New Upgrade
PJM SOUTH | n9647.0 | Install a 300 MVAR STATCOM at Fentress Substation for Coastal Virginia Offshore Wind Project. | Dominion |  |  |  | 3/31/2029 |  | EP | 11/3/2026 | 11/3/2026 | 49.1633 |  |  | New Upgrade
PJM SOUTH | n9380.0 | Replace Existing Ladysmith XFRM 1 with 3-480 MVA Single Phase XFRM. | Dominion |  |  |  | 12/31/2029 |  | EP | 11/3/2026 | 11/3/2026 | 37.5876 |  |  | New Upgrade
PJM SOUTH | n9379.0 | Replace existing 230/500 kV T1 XFRM at Midlothian with 3-480 MVA Single Phase XFRM. | Dominion |  |  |  | 12/31/2029 |  | EP | 11/3/2026 | 11/3/2026 | 37.8363 |  |  | New Upgrade
PJM SOUTH | n9378.0 | Replace existing Carson transformer 2 with 3-480 MVA single phase transformer. | Dominion |  |  |  | 12/31/2029 |  | EP | 11/3/2026 | 11/3/2026 | 37.8013 |  |  | New Upgrade
PJM MA | s3604.1 | Replace existing 138/26kV transformers 132-1 and 132-2 & add two (2) 138kV transformer head breakers. | PSEG |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/19/2024 | 9/19/2024 | 41.9 |  | 11/17/2025 | Scope/Cost Change
PJM WEST | s3603.6 | Clinton - Fayette: Construct an ~ 27-mile 345 kV single circuit from Clinton substation to Fayette substation. These lines will be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. New expected ratings, Fayette 345kV – Clinton 345kV SN: 1263 MVA, SE: 1561 MVA WN: 1750 MVA WE: 1954. | Dayton |  |  | Customer Service |  |  | Cancelled | 4/1/2025 | 4/1/2025 | 100 |  |  | Cancelled
PJM WEST | s3603.5 | Clinton Substation: Expand the Clinton 345 kV substation to accommodate the additional 345 kV line, 2 customer feeds, and a new 250 MVAR Static VAR Compensator. | Dayton |  |  | Customer Service |  |  | Cancelled | 4/1/2025 | 4/1/2025 | 75 |  |  | Cancelled
PJM WEST | s3603.4 | Customer Service Lines from Fayette 1-4: Establish four ~0.5-mile 345 kV feed to the customer substations from AES’s Fayette substation. These lines will be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. | Dayton | X |  | Customer Service |  |  | Cancelled | 4/1/2025 | 4/1/2025 | 9 |  |  | Cancelled
PJM WEST | s3603.3 | Atlanta – Fayette 1 & 2: Construct an ~ 25-mile 345 kV double circuit line from Atlanta substation to Fayette substation. The line is projected to be built with 2-1024.5 ACAR conductor and strung with OPGW for communications. New expected ratings, Fayette 345kV – Clinton 345kV SN: 1263 MVA, SE: 1561 MVA WN: 1750 MVA WE: 1954. | Dayton |  |  | Customer Service |  |  | Cancelled | 4/1/2025 | 4/1/2025 | 192 |  |  | Cancelled
PJM WEST | s3603.2 | Atlanta Substation: Reconfigure the Atlanta 345kV substation into a breaker-and-a-half arrangement to accommodate the 2 additional 345 kV lines. | Dayton |  |  | Customer Service |  |  | Cancelled | 4/1/2025 | 4/1/2025 | 36 |  |  | Cancelled
PJM WEST | s3603.1 | Fayette Substation: Expand the Fayette 345 kV substation to breaker-and-a-half arrangement to accommodate the additional 345 kV lines and the customer feeds. And a 300 MVAR capacitor (two steps of 150 MVAR, ISD 1/1/2030) | Dayton | X |  | Customer Service |  |  | Cancelled | 4/1/2025 | 7/7/2026 | 51.9 |  |  | Cancelled
PJM WEST | n9315.0 | Upgrade station conductors and equipment at TSS 80 Pontiac Substation | ComEd |  |  |  | 12/31/2027 |  | EP | [5 empty] | New Upgrade
PJM MA | s3570.1 | Cut and loop 69kV line from Ridge Road Station to West Windsor Station into customer’s new station. | PSEG |  |  | Customer Service |  |  | UC | 1/16/2025 | 1/16/2025 | 4.2 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s2608.2 | Reconductor 230kV line #2187 segment Pioneer DP-Liberty using a higher capacity conductor as well as terminal equipment upgrades to achieve an expected rating of 1572 MVA. | Dominion |  |  | Customer Service |  |  | UC | 11/30/2021 | 11/30/2021 | 5.7 |  | 2/16/2022 | Scope/Cost Change
PJM SOUTH | s2608.3 | Reconductor 230kV line #2228 segment Pioneer DP-Liberty using a higher capacity conductor as well as terminal equipment upgrades to achieve an expected rating of 1572 MVA. | Dominion |  |  | Customer Service |  |  | UC | 11/30/2021 | 11/30/2021 | 5.7 |  | 2/16/2022 | Scope/Cost Change
PJM SOUTH | s2608.7 | Install (1) 840 MVA 500-230 kV transformer at Bristers Substation and associated 500 kV and 230 kV equipment. Expand Bristers Substation to the north of the existing site to accommodate the 230 kV breaker ring required for the addition of the new transformer. Line terminations for 115kV Line #183 Bristers– Ox), 230kV Line #2101 Bristers–Vint Hill 230 kV, and 500kV Line #539 Ox–Bristers) will be re-arranged to accommodate the expansion. | Dominion |  |  | Customer Service |  |  | UC | 11/30/2021 | 11/30/2021 | 65 |  | 2/16/2022 | Scope/Cost Change
PJM SOUTH | s2609.1 | Interconnect the new substation Interconnection by cutting and extending 230 kV Line 2152 Buttermilk-Beaumeade. Terminate both ends into a four breaker ring arrangement to create an Interconnection-Beaumeade line and an Interconnection-Nimbus-Buttermilk line. | Dominion |  |  | Customer Service |  |  | IS | 4/6/2021 | 4/6/2021 | 16 |  | 2/16/2022 | Scope/Cost Change
PJM WEST | s3584.2 | Install second 2500mm2 XLPE cable per phase on two 1.8 mile 138 kV underground lines from ComEd Elk Grove East substation (ComEd -2023-005) to ComEd Dierking substation (ComEd-2024-004). Install second 2500mm2 XLPE cable per phase on two 2.9 mile 138kV underground lines from ComEd Itasca substation to ComEd Pine substation (ComEd-2023-009). Install two new 138 kV CBs to the double ring bus configuration at ComEd Pine substation (ComEd-2023-009) to connect the new radial lines to the customer substation. Install two new 2.7 mile 138 kV underground lines from ComEd Pine substation (ComEd-2023-009) to the customer site. | ComEd |  |  | Customer Service |  |  | EP | 9/20/2024 | 9/19/2025 | 168 | 194.2 | 11/18/2025 | Scope/Cost Change
PJM SOUTH | s2630.2 | Extend a new 230 kV Line 0.25 miles between Winters Branch and Wakeman. Add a 230 kV breaker at Winters Branch and Wakeman substations to terminate the new 230 kV line. | Dominion |  |  | Customer Service |  |  | IS | 8/10/2021 | 8/10/2021 | 1.6 |  | 12/8/2021 | Scope/Cost Change
PJM WEST | s3584.1 | New customer will be radially served by two new 1.5 mile 138 kV underground lines consisting of 2500mm2 XLPE cables per phase from ComEd Dierking substation (ComEd-2024-004) to the customer site. Customer substation will be an eleven CB, 138 kV double ring bus configuration with three 138/34 kV, 112 MVA transformers. Install two new 138 kV CBs to the double ring bus configuration at ComEd Dierking substation (ComEd-2024-004) to connect the new radial lines to the customer substation. | ComEd |  |  | Customer Service |  |  | EP | 9/20/2024 | 9/19/2025 | 121.4 | 125.2 | 11/18/2025 | Scope/Cost Change
PJM MA | s3567.1 | Replace Windy Edge circuit breaker B28. Existing rating 1600A, 50kA Proposed rating 3000A, 63kA | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 2/13/2025 | 2/13/2025 | 0.7 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3566.1 | Replace Windy Edge circuit breaker B24. Existing rating 1600A, 50kA Proposed rating 3000A, 63kA | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 2/13/2025 | 2/13/2025 | 0.7 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3563.1 | Replace Waugh Chapel circuit breaker B12. Existing rating 2500A, 63kA Proposed rating 3000A, 63kA | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 2/13/2025 | 2/13/2025 | 0.7 |  | 11/18/2025 | Scope/Cost Change
PJM MA | s3561.1 | Replace Waugh Chapel circuit breaker B7. Existing rating 2500A, 63kA Proposed rating 3000A, 63kA | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 2/13/2025 | 2/13/2025 | 0.7 |  | 11/18/2025 | Scope/Cost Change
PJM SOUTH | n9293.0 | Construct 12.5 kV circuit to Tar River Substation | Dominion |  |  |  | 6/1/2028 |  | Cancelled | 10/8/2025 | 10/8/2025 | 4.5 |  | 11/18/2025 | Cancelled
PJM MA | n9287.0 | Line modifciations to tie in AF1-271A | PPL |  |  |  | 4/15/2026 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | b4000.201 | Smith Mountain 138 kV Upgrade: Replace 795 KCM AAC, 37-Str. 795 KCM AAC, 37-Str. PH A B2S1 B2S2 BS1 BS2. Replace 138 kV disconnect switches associated with breakers C and C2. | AEP |  | 2024-W1-81 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 1/7/2025 | 9/18/2026 | 0.4 | 1.4 | 2/26/2025 | Scope/Cost Change
PJM SOUTH | n9267.0 | Construct New 10.5 Mile Line 115 kV Line between Northern Neck and Moon Corner (AE1-155 Tap) | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 45.7301 |  |  | New Upgrade
PJM SOUTH | n9265.0 | Replace 230 kV wave trap 259WT at Basin 230 kV (Basin - Chesterfield B). | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9264.0 | Replace Line Lead at Surry for increased rating on Line 567 8SURRY 500 KV to 8CHCKAHM 500 KV ckt 1 | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9259.0 | Need for two 230 kV gas insulated switchgear ("GIS") bus ties for Coastal Virginia Offshore Wind ("CVOW"). | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 25.3049 |  |  | New Upgrade
PJM WEST | n9241.0 | Replace 8 Amp ITH(50FD) relay at Kittanning | APS |  |  |  | 6/1/2028 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n9240.0 | Replace GE 800 Amp Wave Trap at Kittanning | APS |  |  |  | 6/1/2028 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n9235.0 | Reconductor 2.2 miles of Richland – Stryker 138kV line from Stryker to AF2-321 | ATSI | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | n9226.0 | Upgrade bus side disconnect D212 at Beaver | ATSI | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM MA | n9225.0 | Replace 230 kV substation conductor and line drops at Shelocta substation for the Homer City-Shelocta 230 kV line terminal | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.10757 |  |  | New Upgrade
PJM SOUTH | n9220.0 | Wreck and rebuild 15.41 miles of 230 kV Line 298 from Buckingham to Bremo with dual (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C. Replace line lead at Bremo. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 44.4659 |  |  | New Upgrade
PJM SOUTH | n9217.0 | Wreck and Rebuild 12.73 miles of 230 kV Line 298 from Buckingham to Farmville with dual (2) 768 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 40.4148 |  |  | New Upgrade
PJM SOUTH | n9199.0 | Wreck and rebuild 1.63 miles of line 2193 between Fork Union and Bremo with (2) 768.2 ACSS/TW (20/7) "MAUMEE" @ 250C and replace line lead at Bremo. | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | n9195.0 | Installation of a new 345KV Circuit Breaker at Station 12 Dresden. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 5 |  |  | New Upgrade
PJM SOUTH | n9191.0 | Wreck and rebuild 41.13 miles of Line 576 between North Anna and Midlothian with (3) 1351.5 ACSR (45/7) "Dipper" at 110 degrees C and assoc substation work to achieve new rating of 4356/4356/5009 MVA | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | n9163.0 | Update relays at Beaver | ATSI | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM WEST | n9162.0 | Upgrade 345 kV disconnect switch (D74) at Beaver | ATSI | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9153.0 | Wreck and rebuild 5.74 miles of 230 kV line 2128 between Fentress and Thrasher with (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C and replace line lead at Fentress. | Dominion | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 33.2972 |  |  | New Upgrade
PJM SOUTH | n9139.0 | Wreck and rebuild 37.26 miles of LN 563 between Midlothian and Carson with (3) 1351.5 ACSR (45/7) "Dipper" at 110 degrees C and associated substation work to achieve new rating of 4356/4356/5009 MVA | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
Not Specified | n9133.0 | NIPS SN/SE ratings of 2133/2577 MVA achieved by change out of 2156 ACSR line conductor with 2-1590 ACSR conductor. | NIPSCO | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9131.0 | Substation work to energize the temporary Bremo transformer #7 which is not in service. | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM MA | n9119.0 | Reconductor/Rebuild the Shelocta – Keystone 230 kV Line, approximately 2.5 miles, with 1272 kcmil 45/7 ACSR 2-conductor | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 9.5336 |  |  | New Upgrade
PJM MA | n9116.0 | Rebuild approximately 11 miles of the Homer City-Shelocta 230 kV line with double bundled 795 kcmil 26/7 ACSS conductor | PENELEC | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 39.3122 |  |  | New Upgrade
Not Specified | n9113.0 | Upgrade wave trap and M.O. at GreenAcres substation. | NIPSCO | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | n9112.0 | Wreck and Rebuild 12.4 miles of 230 kV line 259 with (2) 768.2 ACSS/TW (20/7) "MAUMEE" conductor @ 250 degrees C and replace line lead at Chesterfield. | Dominion | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | b4000.359 | Relocate the Joshua Falls 765 kV substation. Install (5) 765 kV breakers and relocate Joshua Falls 765/138 kV transformer to the new site. Terminate the 765 kV Cloverdale line and the 765 kV Yeat line into the relocated station. Build 138 kV line to reconnect the existing Joshua Falls 138 kV yard to the relocated station. | AEP |  | 2024-W1-820 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 1/7/2025 | 8/4/2026 | 99.1 | 225.5 | 2/26/2025 | Scope/Cost Change
PJM SOUTH | b4000.352 | Cut into line 568 Ladysmith to Possum Point and run to the line of demarcation at Thornburg substation (Ladysmith - Thornburg portion). | Dominion |  | 2024-W1-967 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 1/7/2025 | 10/6/2026 | 3.6 | 1.1 | 2/26/2025 | Scope/Cost Change
PJM SOUTH | b4000.351 | Cut into line 568 Ladysmith to Possum Point and run to the line of demarcation at Thornburg substation (Ladysmith - Thornburg portion). | Dominion |  | 2024-W1-967 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 1/7/2025 | 10/6/2026 | 3.6 | 1.1 | 2/26/2025 | Scope/Cost Change
PJM WEST | n9107.0 | Replace 477 KCM station conductor at Moore Park. | AEP | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 0.15 |  |  | New Upgrade
PJM MA | s3009.1 | Construct a new 69/13kV station on PSE&G owned adjacent property to Keasbey station. o Build a new 69kV line to Rahway station. o Build a new 69kV line to Blair Rd. o Install one (1) 230/69kV transformer at South Edison. o Build a new 69kV line to South Edison | PSEG |  |  | Customer Service |  |  | EP | 9/5/2023 | 9/5/2023 | 220.68 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3030.2 | Cut 230kV Line #2075 and extend double circuit 230kV lines into White Oak Substation. Install 2-1200 Amp switches and upgrade bus work and existing equipment at the White Oak Substation. Add 3 additional 230kV breakers to terminate 230kV lines. | Dominion |  |  | Customer Service |  |  | UC | 8/9/2022 | 8/9/2022 | 29 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3047.1 | Reconductor approximately 9.2 miles of 230kV Line #2101 Nokesville - Bristers using a higher capacity conductor as well as terminal equipment upgrades to achieve a minimum normal summer conductor rating of 1573 MVA. | Dominion |  |  | Customer Service |  |  | UC | 2/7/2023 | 2/7/2023 | 23 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | n9101.0 | L1 8806-Brokaw - AB2-070 - AC1-053 345 Kv Line - Mitigate Sag on the Line. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 15 |  |  | New Upgrade
PJM MA | n9100.0 | Install new 69 kV terminal position at Ontario 69 KV substation | ACE |  |  |  | 2/28/2028 |  | Cancelled | 10/8/2025 | 10/8/2025 | 9.132 |  | 11/18/2025 | Cancelled
PJM WEST | s3127.1 | Install a new 4-breaker ring bus named Catlett Mountain near 85 Russ Johnson Rd, Front Royal, VA 22630. Cut the Page – Riverton RLU 138 kV Line near pole RLU-154 and extend 0.3-mile line in and out of the new Catlett Mountain substation. Protection/terminal end relay settings review required. Install revenue metering in Customer’s facilities | APS |  |  | Customer Service |  |  | Cancelled | 7/21/2023 | 7/21/2023 | 16 |  | 11/18/2024 | Cancelled
PJM MA | b3906.1 | Construct new Marley Neck 115 kV substation. Marley Neck 115kV portion will accommodate 10 breaker-and-a-half bays, with only 6 bays planned for initial service while accommodating 4 future bays. Two Standard 230/115kV transformers will be connected between the 230 and 115 kV equipment with appropriate isolation methods. | BGE |  | 2024-W1-295 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 12/3/2024 | 10/6/2026 | 107.62 | 122.07 | 2/26/2025 | Scope/Cost Change
PJM WEST | n9005.0 | Fiber Tie-in: Install two new All Dielectric Loose Tube (ADLT) fiber-optic cable station exit transitions, splicing into the new fiber-cables to be installed by the proposed AF2-205 Switching Station project. | AEP |  |  |  | 2/6/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.27385 |  | 11/18/2025 | Cancelled
PJM MA | s3181.1 | Install a new 69 kV tie breaker at Lamb substation to provide an additional terminal for distribution resources. | ACE |  |  | Customer Service |  |  | EP | 1/18/2024 | 1/18/2024 | 2.5 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | n9004.0 | AF2-133 345 kV: Review and revise protective relay settings | AEP |  |  |  | 2/6/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.071095 |  | 11/18/2025 | Cancelled
PJM MA | s3187.1 | Rebuild the entire 20-mile 69kV line on Corten Steel MonoPoles with 954 ACSR conductor and OPGW. The replacement line will stay within the existing ROW and clearances shall meet APLIC guidelines. | ODEC |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 10/19/2023 | 10/19/2023 | 17 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3203.1 | Replace the existing 138kV oil circuit breaker 7TS at Buzzard Point | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/19/2023 | 10/19/2023 | 0.675 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3539.1 | Replace the existing 138kV oil circuit breaker 8BT at Bells Mill | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/13/2023 | 12/13/2023 | 0.675 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3535.1 | Replace the existing 230kV oil circuit breakers 6C at Morgantown | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 12/5/2023 | 12/5/2023 | 0.81 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3534.1 | Replace the existing 230kV oil circuit breakers 6B at Morgantown | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 12/5/2023 | 12/5/2023 | 0.81 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3533.1 | Replace the existing 230kV oil circuit breakers 3B at Burches Hill | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/5/2023 | 12/5/2023 | 0.81 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3532.1 | Replace the existing 230kV oil circuit breakers 3A at Burches Hill | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/5/2023 | 12/5/2023 | 0.81 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3530.1 | The breakers are in deteriorating condition, have a lack of replacement parts, and have elevated maintenance cost. Replace the existing 230kV oil circuit breakers 2A. | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 12/5/2023 | 12/5/2023 | 0.81 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3222.1 | Rebuild approximately 44.3 miles of 230kV Line #246 between Earleys and Suffolk to current 230kV standards. The normal rating of the line conductor will be 1573 MVA. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 12/5/2023 | 12/5/2023 | 150 |  | 11/18/2024 | Scope/Cost Change
PJM MA | n8985.0 | Update relay settings at Lake Nelson for the two circuits entering the station from JCPL’s Raritan River station | PSEG |  |  |  | 11/30/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.307 |  | 11/18/2025 | Cancelled
PJM WEST | n8975.0 | Canton Central substation - Extend 0.3 miles fiber optic cable from control house to splice point | AEP |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8974.0 | Canton Central substation - replace two relays, remove 2000 A line trap, and install new control cabling | AEP |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8973.0 | Bluebell Substation - replace line relaying and provide direct transfer trip and anti-islanding protection | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8972.0 | Highland Substation - review relay settings | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8971.0 | Pidgeon Substation - review relay settings | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8970.0 | Berlin Substation - review relay settings | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8969.0 | Knox Substation - review relay settings | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8968.0 | Niles Substation - review relay settings | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM MA | s3268.1 | Westfall 115 kV Substation Replace the existing control building with a new Package Control Enclosure that can accommodate all relaying and equipment. | PENELEC |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 12/13/2023 | 12/13/2023 | 6.7 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | n8967.0 | Samis Substation - review relay settings | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8966.0 | Bluebell - Canton 138 kV line loop into AG1-239 interconnection substation | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8965.0 | AG1-239 Interconnection Substation - design, install, and test/commission MPLS Equipment for SCADA transport | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8964.0 | Install fiber from AG1-239 Interconnection substation to Canton Central for communication transport | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8963.0 | AG1-239 Interconnection Substation - construct 138 kV 3-breaker ring bus substation | ATSI |  |  |  | 9/30/2029 |  | Cancelled | [5 empty] | Cancelled
PJM MA | n8962.0 | Review and revise relay settings as required | MAIT |  |  |  | 12/31/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.064836 |  | 11/18/2025 | Cancelled
PJM MA | n8952.0 | Upgrade relay settings for South River Substation | JCPL |  |  |  | 11/30/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.060585 |  | 11/18/2025 | Cancelled
PJM MA | n8951.0 | Upgrade relay settings for Red Oak Substation | JCPL |  |  |  | 11/30/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.060585 |  | 11/18/2025 | Cancelled
PJM MA | n8950.0 | Upgrade relay settings for Parlin Substation | JCPL |  |  |  | 11/30/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.060585 |  | 11/18/2025 | Cancelled
PJM MA | n8948.0 | Reconfigure Raritan River substation and add a new 230 kV circuit breaker to support AF2-413 generator interconnection. | JCPL |  |  |  | 11/30/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 4.4741 |  | 11/18/2025 | Cancelled
PJM WEST | n8928.0 | Remote end relaying at Mutual substation | Dayton |  |  |  | 5/31/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.073 |  | 11/18/2025 | Cancelled
PJM WEST | n8927.0 | Remote end relaying at Darby substation | Dayton |  |  |  | 5/31/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.71 |  | 11/18/2025 | Cancelled
PJM WEST | n8926.0 | Remote end relaying at Urbana substation | Dayton |  |  |  | 5/31/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.68 |  | 11/18/2025 | Cancelled
PJM WEST | n8924.0 | Interconnection substation tie-in: Cut and loop the Urbana-Darby 138 kV line into the new substation and Re-route Givens Tap 138 kV line | Dayton |  |  |  | 5/31/2029 |  | Cancelled | 10/8/2025 | 10/8/2025 | 5.972 |  | 11/18/2025 | Cancelled
PJM MA | n8917.0 | Modify relays at Dauphin 69 kV Substation | PPL |  |  |  | 12/31/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.13733 |  | 11/18/2025 | Cancelled
PJM MA | n8916.0 | Modify relays at Sunbury 69 kV Substation | PPL |  |  |  | 12/31/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.13733 |  | 11/18/2025 | Cancelled
PJM MA | n8915.0 | Modify Sunbury-Dauphin 69 kV line to tie in the new Transmission Owner Interconnection Facility. | PPL |  |  |  | 12/31/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.90287 |  | 11/18/2025 | Cancelled
PJM WEST | n8898.0 | Final Tie in for Fiber installation in New ROW | AEP |  |  |  | 9/30/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.32041 |  | 11/18/2025 | Cancelled
PJM WEST | n8897.0 | Reconfigure the Carrier Ethernet Switch (CES) with a new Small Form-factor Pluggable (SFP) transceiver at the proposed AF2-205 345 kV Station. | AEP |  |  |  | 9/30/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.05475 |  | 11/18/2025 | Cancelled
PJM WEST | n8896.0 | Review and revision of the protective relay settings at the proposed AF1-215 345 kV Station. | AEP |  |  |  | 9/30/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.071095 |  | 11/18/2025 | Cancelled
PJM WEST | n8854.0 | IMTCo will review and revise (as necessary) the protective relay settings at the Allen 345 kV Station to account for the additional generation. | AEP |  |  |  | 12/23/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.060764 |  | 11/18/2025 | Cancelled
PJM WEST | n8853.0 | Final Tie in for Fiber installation in New ROW | AEP |  |  |  | 1/7/2027 |  | Cancelled |  |  |  |  | 2/26/2025 | Cancelled
PJM WEST | n8851.0 | IMTCo will reconfigure the Existing CES at the Perch 138 kV Station with a new SFP transceiver. | AEP |  |  |  | 1/7/2027 |  | Cancelled |  |  |  |  | 2/26/2025 | Cancelled
PJM WEST | n8850.0 | IMTCo will review and revise (as needed) the protective relay settings at the proposed AF1-268 138 kV Station, IMTCo will reconfigure the proposed ICON at the AF1-268 138 kV Station with a new SFP transceiver. | AEP |  |  |  | 1/7/2027 |  | Cancelled |  |  |  |  | 2/26/2025 | Cancelled
PJM WEST | n8849.0 | IMTCo will replace the existing protective relays at the Jay 138 kV Station with dual fiber-based ICON MUX current differential relays, IMTCo will reconfigure the existing ICON and Carrier Ethernet Switch (CES) at the Jay 138 kV Station with two (2) new Small Form-factor Pluggable (SFP) transceivers. | AEP |  |  |  | 1/7/2027 |  | Cancelled |  |  |  |  | 2/26/2025 | Cancelled
PJM WEST | n8848.0 | IMPCo will install two (2) new steel, 85' single circuit, single pole dead-end structures and two (2) spans of aluminum conductor steel-reinforced (ACSR) 1590 (Falcon) transmission line conductor with 7#8 Alumoweld shield wire in the existing Jay - Perch section of the Jay - Desoto 138 kV Right of Way, cutting in the proposed 138 kV station in an in-and-out arrangement | AEP |  |  |  | 1/7/2027 |  | Cancelled |  |  |  |  | 2/26/2025 | Cancelled
PJM SOUTH | s3510.1 | Interconnect new Sloan Drive substation by providing two 230kV feeds from Dominion's proposed Bermuda Hundred substation. The lines will terminate into a 230kV six breaker ring bus arrangement | Dominion |  |  | Customer Service |  |  | UC | 6/4/2024 | 6/4/2024 | 30 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3509.1 | Interconnect new Bermuda substation by cutting in the existing 230kV Line #2050 from ICI to Allied. Lines to terminate in a 230kV six breaker ring bus arrangement | Dominion |  |  | Customer Service |  |  | UC | 6/4/2024 | 6/4/2024 | 15 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3502.1 | Interconnect the new Lost City substation by cutting in the existing 230kV Line 2282 from Techpark Place to White Oak. Lines to terminate in a 230kV four breaker ring arrangement with an ultimate arrangement of a six-breaker ring. | Dominion |  |  | Customer Service |  |  | IS | 1/9/2024 | 1/9/2024 | 12.3 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | n8789.0 | Expansion of the Allen 345 kV Station to the southeast by 450’ x 170’ including civil pad work, fencing, and ground grid. Extension of 100 feet of new tubular station bus to the southeast. Installation of a new circuit breaker string “D”. Installation of two (2) new 5000A 345 kV circuit breakers with control relaying. Installation of two (2) new 345 kV breaker disconnect switches. Replacement of one (1) disconnect switch “C1S1” due to clearance restrictions imposed by the station expansion. Associated conductors, insulators, arresters, foundations, and structures. Review and revision (as necessary) of the protective relay settings for the remainder of the Allen 345 kV Station. | AEP |  |  |  | 12/23/2027 |  | Cancelled |  |  |  |  | 2/26/2025 | Cancelled
PJM WEST | s3469.1 | Galion – Roberts North 138 kV Line and Galion – Roberts South 138 kV Line: Rebuild the double circuit Galion – Roberts North 138 kV Line and Galion – Roberts South 138 kV Line on shared structures. Galion: Replace circuit breakers and associated disconnect switches. Roberts - Replace substation conductor. | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 5/17/2024 | 5/17/2024 | 66.5 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | s3499.1 | Install one tap-line SCADA controlled switch. Install SCADA controlled on existing main-line switch. Construct 0.6 miles of 138 kV line extension. Adjust relay settings at Cloverdale and Harmon substations. Install revenue metering. | ATSI |  |  | Customer Service |  |  | Cancelled | 6/14/2024 | 6/14/2024 | 0.7 |  | 11/18/2024 | Cancelled
PJM WEST | n8780.0 | Relay Modification at AEP's Olive Substation | AEP |  |  |  | 8/1/2026 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8779.0 | Modify Relay Settings at TSS 66 East Frankfort Substation | ComEd |  |  |  | 8/1/2026 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n8778.0 | Modify Relay Settings at TSS 970 University Park Substation | ComEd |  |  |  | 8/1/2026 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | s3443.1 | Tap the existing feeder adjacent to customer’s new substation. Install three steel poles: one at the tap, one to support a line switch, and one to support two spans to the customer’s substation. Install a motorized line switch with SCADA control. Connect all with 954 ACSR conductor. Install revenue metering in the customer’s new substation. | DEOK |  |  | Customer Service |  |  | IS | 7/19/2024 | 7/19/2024 | 0.499 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s3411.1 | Replace relaying and limiting substation conductor at Atlantic and Red Bank 230 kV Substations | JCPL |  |  | Operational Flexibility and Efficiency^Equipment Material Condition, Performance and Risk |  |  | EP | 10/31/2023 | 10/31/2023 | 2 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | s3382.1 | Tap into the 69 kV Todhunter-Monroe feeder. Replace a 600A switch between Todhunter and the new tap with a 2000A switch to increase the capacity of the feeder. Install 0.9 miles of feeder from the new tap to Dayton Technologies using 17 steel poles with 954 ACSR conductor. Install a tap with a switch and drop to connect Worthington Steel. This configuration allows Worthington Steel and Dayton Technologies to be fed from either direction and the isolation of both individually. | DEOK |  |  | Operational Flexibility and Efficiency |  |  | UC | 10/20/2023 | 10/20/2023 | 5.773 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | s3378.1 | Retire the existing Merrel substation. Expand the substation area to allow for new equipment installation meeting adequate safety clearances. Install new 69 kV bus, switch separated into two sections. Reconnect the 69 kV feeders to the bus with motorized switches and transmission line sectionalizing. Install two 69/13 kV, 22 MVA transformers, each connected to the 69 kV bus with circuit switchers. Install two new open air breaker sections of 13 kV bus to reconnect distribution feeders. | DEOK |  |  | Customer Service |  |  | UC | 5/17/2024 | 5/17/2024 | 2.55 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | s3377.1 | Relocate 138/69 kV TB 4 to make room for a 2nd 22 MVA distribution transformer, TB 6. Install a circuit breaker on the high side of TB 4 to reconnect it to 138 kV Bus 4. Install a circuit switcher on the high side of TB 6 to connect it to 138 kV Bus 4. Rework distribution feeders transferring some load from the existing distribution transformer to TB 6. | DEOK |  |  | Customer Service |  |  | IS | 5/17/2024 | 5/17/2024 | 1.87 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | s3369.1 | At Grafton Substation, replace circuit breaker, disconnect switches, substation conductor and relaying. At Pruntytown Substation, replace disconnect switches, line trap, substation conductor and relaying | APS |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 3/15/2024 | 3/15/2024 | 1.8 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | n8632.0 | Replace line realy and carrier equipment at Millville | APS |  |  |  | 8/31/2028 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8631.0 | Replace line realy and carrier equipment at Shepherdstown | APS |  |  |  | 8/31/2028 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8630.0 | Install Power line carrier equipment at Bedington | APS |  |  |  | 8/31/2028 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8629.0 | Convert existing Sleepy Hollow substation to a five-breaker ring bus. | APS |  |  |  | 8/31/2028 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8628.0 | Installation of MW Radio to support RTU installation at Sleepy Hollow substation. | APS |  |  |  | 8/31/2028 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n8627.0 | Design, installation, and testing/commissioning for Point-to-Point Microwave Radio equipment for SCADA transport at North Mountain Substation. | APS |  |  |  | 8/31/2028 |  | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | n8620.0 | Expand the Waugh Chapel 230 kV substation by adding a new breaker in position B29. | BGE | [5 empty] | Cancelled | 10/8/2025 | 10/8/2025 | 8.339 |  | 11/18/2025 | Cancelled
PJM WEST | s3169.0 | Rebuild the 14.11 mile, North Springfield-Loretto 69 kV line using 556.5 conductor and steel pole construction. | EKPC |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 11/17/2023 | 11/17/2023 | 12.97 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | s3343.2 | Cut into existing 138 kV 0901 line (Davis Creek-East Frankfort-Joliet) and extend two 1.1 mile circuits to a new 138 kV breaker-and-a-half substation. New substation will have twelve 138 kV CBs and supply four 138/12.5 kV distribution transformers. | ComEd |  |  | Customer Service |  |  | EP | 3/15/2024 | 9/19/2025 | 64 | 62.4 | 11/18/2024 | Scope/Cost Change
PJM SOUTH | b3800.375 | Construct new Woodside-Goose Creek 500 kV line for ~3 miles on single circuit monopole structures within the Doubs-Goose Creek Corridor. (DOM Portion) | Dominion |  | 2022-W3-853 | Baseline Load Growth Deliverability & Reliability | 6/1/2029 |  | EP | 7/10/2024 | 10/6/2026 | 15.6 | 38.35 | 8/7/2024 | Scope/Cost Change
PJM MA | n8586 | Roxbury Substation: Install new 23 kV PT on the Arco line. Revise relay settings for new customer tap. Replace existing 23 kV KRB ARCO relays with SEL-0351S line panel | PENELEC |  |  |  | 8/31/2027 | 8/31/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 2.8157 |  | 11/18/2025 | Cancelled
PJM MA | s3325.1 | Replace the 115-34.5 kV No. 1 Transformer at Flanders Substation. Replace the 115 kV circuit switcher with a circuit breaker. Upgrade the transformer relaying. Install new control enclosure. | JCPL |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 4/18/2024 | 4/18/2024 | 8.1 | 8.1 | 11/18/2024 | Scope/Cost Change
PJM MA | n8582 | Replace line relaying panel at Warrior Ridge substation | PENELEC |  |  |  | 8/1/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.4651 |  | 11/18/2025 | Cancelled
PJM MA | n8581 | Install two SCADA operated switches on the Miller REC - Warrior Ridge 46 kV Line | PENELEC |  |  |  | 8/1/2027 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.6124 |  | 11/18/2025 | Cancelled
PJM MA | n8571 | Portland Substation: Relay Setting Changes | ME |  |  |  | 5/31/2028 | 5/31/2028 | Cancelled | 10/8/2025 | 10/8/2025 | 0.061108 |  | 11/18/2025 | Cancelled
PJM MA | n8570 | Newton Substation: Relay Setting Changes | JCPL |  |  |  | 5/31/2028 | 5/31/2028 | Cancelled | 10/8/2025 | 10/8/2025 | 0.066058 |  | 11/18/2025 | Cancelled
PJM MA | n8569 | Yards Creek Substation: Relay Setting Changes | JCPL |  |  |  | 5/31/2028 | 5/31/2028 | Cancelled | 10/8/2025 | 10/8/2025 | 0.06502 |  | 11/18/2025 | Cancelled
PJM MA | n8568 | Kittatinny Substation: Install new 230 kV breakers, disconnect switches and line terminal for AG1-511 direct connection. | JCPL |  |  |  | 5/31/2028 | 5/31/2028 | Cancelled | 10/8/2025 | 10/8/2025 | 4.6974 |  | 11/18/2025 | Cancelled
PJM MA | n8567 | Whitings Substation: Revise relay settings | JCPL |  |  |  | 3/31/2027 | 3/31/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 0.067 |  | 11/18/2025 | Cancelled
PJM MA | n8566 | Oyster Creek Substation: Revise relay settings | JCPL |  |  |  | 3/31/2027 | 3/31/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 0.068 |  | 11/18/2025 | Cancelled
PJM MA | n8565 | Oyster Creek – Whitings 34.5 kV: Install (2) line switches, one on each side of tap on the Q121 Oyster Creek – Whitings 34.5 kV Line, approximately 1.5 miles from Bamber Lake to the generator facility near structure 90200. | JCPL |  |  |  | 3/31/2027 | 3/31/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 1.085 |  | 11/18/2025 | Cancelled
PJM WEST | n8558 | Replace the protective relays and circuit breaker control and install a new ethernet switch at Olive 345 kV | AEP | [5 empty] | Cancelled | 10/8/2025 | 10/8/2025 | 0.85411 |  | 11/18/2025 | Cancelled
PJM WEST | n8545 | Fort Martin Substation: Revise Relay Settings | APS |  |  |  | 10/1/2027 | 10/1/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 0.058188 |  | 11/18/2025 | Cancelled
PJM WEST | n8544 | Hatfield Substation: Revise Relay Settings | APS |  |  |  | 10/1/2027 | 10/1/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 0.058188 |  | 11/18/2025 | Cancelled
PJM WEST | n8543 | Ronco Substation: Revise Relay Settings | APS |  |  |  | 10/1/2027 | 10/1/2027 | Cancelled | 10/8/2025 | 10/8/2025 | 0.060008 |  | 11/18/2025 | Cancelled
PJM MA | n8538 | Update relaying at Roadstown substation for the #06XX Line from the new AF1-208 substation to Roadstown. | ACE |  |  |  | 12/31/2028 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.125 |  | 11/18/2025 | Cancelled
PJM MA | n8537 | Update relaying at Laurel substation for the #0799 Line from Laurel to the new AF1-208 substation. | ACE |  |  |  | 12/31/2028 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.125 |  | 11/18/2025 | Cancelled
PJM MA | n8536 | Cut and loop in #0799 transmission line (Laurel - Roadstown) to the new 69 kV three-position ring bus substation. The line from the new ring bus to Laurel will remain as #0799, while the line from the new ring bus to Roadstown will be named #06XX. | ACE |  |  |  | 12/31/2028 |  | Cancelled | 10/8/2025 | 10/8/2025 | 1.946 |  | 11/18/2025 | Cancelled
PJM MA | n8535 | Construct a new 69 kV three-position ring bus substation off the right-of-way for line (Laurel - Roadstown) #0799. Two of the positions will be transmission line terminals for the tie-in of line #0799 to the substation. The third position will be a terminal configured for the interconnection of the AF1-208 generator. | ACE |  |  |  | 12/31/2028 |  | Cancelled | 10/8/2025 | 10/8/2025 | 12.949 |  | 11/18/2025 | Cancelled
PJM SOUTH | b3850.3 | At Fentress substation, since the new 500kV line will be using fiber, the wave trap will be removed and the line protection scheme will be updated. | Dominion |  | 2023-W2-367 | TO Criteria Violation | 6/1/2028 |  | UC | 6/4/2024 | 10/6/2026 | 0.14 | 3.5 | 8/7/2024 | Scope/Cost Change
PJM SOUTH | b3850.2 | Line #588 terminal equipment at Yadkin substation will be upgraded to a rating of 5000A. Since the new 500kV line will be using fiber, the wave trap will be removed and the line protection scheme will be updated. | Dominion |  | 2023-W2-367 | TO Criteria Violation | 6/1/2028 |  | EP | 6/4/2024 | 10/6/2026 | 0.962 | 2.66 | 8/7/2024 | Scope/Cost Change
PJM SOUTH | b3850.1 | Rebuild approximately 13.51 miles of 500 kV line #588 from structure 588/184 inside Yadkin substation to structure 588/254 outside of Fentress substation. | Dominion |  | 2023-W2-367 | TO Criteria Violation | 6/1/2028 |  | UC | 6/4/2024 | 10/6/2026 | 78.6 | 107.64 | 8/7/2024 | Scope/Cost Change
PJM MA | n8446.4 | Install a new single circuit, custom foundation, custom steel pole, full terminal deadend structure (PCO) between Sunbury - Dauphin 69 kV line. The PCO structure must be outside of the Project Developer’s Substation fenced area. | PPL |  |  |  | 12/31/2027 | 12/31/2027 | Cancelled | 10/8/2024 | 10/8/2024 | 0.01 |  | 2/26/2025 | Cancelled
PJM MA | s3291.1 | Warren – Falconer 115 kV Line – New Customer: Tap the Warren –Falconer 115 kV Line, install switches and build approximately 190 ft of transmission line from the tap point to customer substation. Construct new 115 kV switching station near the Warren - Falconer 115 kV Line Install two SCADA controlled transmission line disconnect switches with full load break interrupters Install one 115 kV circuit breaker (Normally Open) Install one 115 kV revenue metering package at customer substation Adjust relay settings at Warren Substation solution component removed on 5/15/2025 - Operate disconnect switch towards Falconer Substation as normally open) | PENELEC |  |  | Customer Service |  | 4/28/2028 | EP | 2/15/2024 | 2/15/2024 | 1.5 | 8.45 | 11/18/2024 | Scope/Cost Change
PJM MA | s3279.1 | Rebuild Riverside 115kV station as 12 position GIS Breaker and Half Substation on existing BGE owned property. Install 115 kV, 4000A, 63kA interrupting current equipment. Install Relay and Control Panels. Re-terminate existing transmission lines and transformer connections into new GIS equipment. | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 2/15/2024 | 2/15/2024 | 84.3 | 84.3 | 11/18/2024 | Scope/Cost Change
PJM MA | s3276.1 | Construct new fiber path between New Freedom – E Windsor - Deans o Replace 53 miles of static wire on 5038 (New Freedom – E Windsor) and 15 miles of static wire on 5022 (E Windsor - Deans) o Upgrade line relay equipment and remove Power Line Carrier (PLC) equipment o This project will replace Project s0473 .Will be coordinated with JCPL-2023-064 | PSEG |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 2/6/2024 | 2/6/2024 | 39.2 |  | 11/18/2024 | Scope/Cost Change
PJM WEST | n8510 | Review and revise the protective relay settings at the proposed AE2-048 345 kV Station to account for the additional generation of AE2-136 | AEP | [5 empty] | Cancelled | 10/8/2025 | 10/8/2025 | 0.058 |  | 11/18/2025 | Cancelled
PJM WEST | n8509.2 | Install deadend and metering to interconnect AF2-032 | ComEd |  |  |  | 8/30/2026 | 8/30/2026 | Cancelled | 10/8/2025 | 10/8/2025 | 2.8 |  | 11/18/2025 | Cancelled
PJM WEST | n8509.1 | Install bus-tie circuit breaker and all related relays and appurtenance at STA 21 Kincaid to interconnect AF2-032 | ComEd |  |  |  | 8/30/2026 | 8/30/2026 | Cancelled | 10/8/2025 | 10/8/2025 | 3.5 |  | 11/18/2025 | Cancelled
PJM WEST | n8505.4 | Replace the protective relays and circuit breaker controls, replace the existing coupling capacitor voltage transformer (CCVT) with a new 3-phase CCVT and Install a new surge arrester at South Van Wert 69 kV | AEP |  |  |  |  | 12/30/2026 | Cancelled | 10/8/2024 | 10/8/2024 | 0.5196 |  | 2/26/2025 | Cancelled
PJM WEST | n8505.3 | Replace the protective relays and circuit breaker controls, replace the existing coupling capacitor voltage transformer (CCVT) with a new 3-phase CCVT and Install a new surge arrester at Haviland 69 kV | AEP |  |  |  |  | 12/30/2026 | Cancelled | 10/8/2024 | 10/8/2024 | 0.46964 |  | 2/26/2025 | Cancelled
PJM WEST | n8505.2 | Install two (2) new steel, 75' single circuit, single pole dead-end structures on concrete piers with anchor bolt cages and two (2) spans of drake transmission line conductor with 7#10 alumoweld shield wire on the Cavett Switch - West Van Wert 69 kV line | AEP |  |  |  |  | 12/30/2026 | Cancelled | 10/8/2024 | 10/8/2024 | 1.0064 |  | 2/26/2025 | Cancelled
PJM WEST | n8505.1 | Install two (2) new fiber optic cable paths consisting of 3 miles of 144 count all-dielectric self-supporting (ADSS) cable installed on existing AEP structures, 0.2 miles of 144 count ADLT cable installed in new underground right of way (ROW), and associated terminating equipment and devices between the proposed AE2-298 switching station, Haviland, and South Van Wert 69 kV stations | AEP |  |  |  |  | 12/30/2026 | Cancelled | 10/8/2024 | 10/8/2024 | 0.38673 |  | 2/26/2025 | Cancelled
PJM MA | n8488 | Install 34.5 kV Potential Transformer and replace Oil Creek phase and RC relays with SEL-351S at Titusville 34.5 kV Substation | PENELEC |  |  |  |  | 7/31/2027 | Cancelled | 10/8/2024 | 10/8/2024 | 0.649 |  | 2/26/2025 | Cancelled
PJM SOUTH | s3072 | Interconnect the new substation Southall by cutting and extending 230kV Line #255 (North Anna - Desper). Lines to terminate in a 230kV four-breaker ring arrangement with an ultimate arrangement of a six-breaker ring. | Dominion |  |  | Customer Service |  |  | IS | 6/6/2023 | 6/6/2023 | 55 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3071 | Interconnect the new substation Trident by cutting and extending Line #2161 (Gainesville – Wheeler). Lines to terminate into a 230 kV six-breaker ring arrangement. | Dominion |  |  | Customer Service |  |  | IS | 6/6/2023 | 6/6/2023 | 15.75 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3053 | Install (2) 1200 Amp, 50kAIC circuit switchers and associated equipment (bus, relaying, etc.) to feed the 3rd & 4th transformers at Roundtable. | Dominion |  |  | Customer Service |  |  | IS | 7/11/2023 | 7/11/2023 | 1 |  | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3052 | Remove ground switches and install circuit switchers at 4 substations – Deep Creek Tx# 1 & 2, Alexander Corner Tx# 1, Tunis Tx# 2 & Brown Boveri Tx# 1. | Dominion |  |  | Operational Flexibility and Efficiency |  |  | EP | 3/16/2023 | 1/15/2026 | 2.5 | 1.86 | 11/18/2024 | Scope/Cost Change
PJM SOUTH | s3043 | Interconnect the new Germanna substation by cutting and extending 230kV Line #2199 Cirrus-Gordonsville. Lines to terminate in a 230kV four-breaker ring arrangement with an ultimate arrangement of a six-breaker ring. | Dominion |  |  | Customer Service |  |  | UC | 10/31/2023 | 10/31/2023 | 55 |  |  | New Upgrade
PJM SOUTH | s3028 | Cut and extend 230kV Line #2231 Global Plaza-Pacific to the proposed Ocean Court Substation. Terminate lines in a four-breaker 230kV ring bus with an ultimate arrangement of six-breaker ring. | Dominion |  |  | Customer Service |  |  | UC | 8/9/2022 | 8/9/2022 | 10 |  | 11/18/2024 | Scope/Cost Change
PJM MA | s2976 | Replace the existing 230kV oil circuit breaker 3C at Palmers Corner | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/11/2023 | 7/11/2023 | 0.6 |  | 12/11/2023 | Scope/Cost Change
PJM MA | s2974 | Replace the existing 230kV oil circuit breaker 6A at Quince Orchard | PEPCO |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 7/11/2023 | 7/11/2023 | 0.6 |  | 12/11/2023 | Scope/Cost Change
PJM WEST | s2979 | At Wilder substation, remove 138/69/34 kV Transformer 2. Install a 138/69 kV, 150 MVA transformer to feed the 69 kV bus and a 138/34 kV, 33 MVA transformer to feed the 34 kV bus. Install a circuit switcher for the new high side connection to the 138/34 kV transformer. Expand the substation and relocate transmission lines and structures to accommodate the new equipment. | DEOK |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 7/21/2023 | 7/21/2023 | 10.991 |  | 12/11/2023 | Scope/Cost Change
PJM WEST | s2971 | Aicholtz: Disconnect the 69 kV feeders from the substation. Remove 69 kV bus, switches and the 69/13 kV transformers. Refeed the substation with the immediately adjacent Beckjord – Summerside 138 kV circuit. Expand the substation and install bus work with two 2000A air-break switches to create positions for three transformers. Install two 2000A motor operated line disconnects with an automatic throw over (ATO) scheme. Install two 138/13 kV, 22 MVA transformers connected with circuit switchers to the 138 kV bus. Install 13 kV switchgear to connect the existing distribution feeders. | DEOK |  |  | Customer Service |  |  | UC | 5/19/2023 | 5/19/2023 | 6.7 |  | 12/11/2023 | Scope/Cost Change
PJM MA | s2951 | Construct new 69-13kV substation with two transformers in acquired property in Prospect Park. Cut and loop Hinchmans – North Paterson and Hawthorne – Customer Sub 69kV lines into the new 69kV bus | PSEG |  |  | Customer Service |  |  | UC | 4/20/2023 | 4/20/2023 | 63 |  | 12/11/2023 | Scope/Cost Change
PJM WEST | n8470 | Perform relay, protection and line metering at TSS 171 Wempletown to support the J1377 interconnection. | ComEd | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | s2918 | Disconnect the 69 kV feeder loop connecting Brighton substation. Demolish and remove Brighton. Build Camp Washington, a new 3-breaker ring bus substation to serve area load formally served by Brighton. Install three 138/13 kV, 22 MVA transformers and switchgear for distribution feeders. Due to land constraints two of the ring positions in this small substation will also loop the South Fairmount-Metro Sewer 138 kV feeder through Camp Washington. | DEOK |  |  | Other |  |  | IS | 3/17/2023 | 3/17/2023 | 19.5 |  | 12/11/2023 | Scope/Cost Change
PJM WEST | s2876 | Install a new 69 kV breaker at EKPC’s Hebron substation, construct a new 7.6 mile 69 kV transmission line from EKPC’s Hebron 69 kV substation to serve a new 69/13.2 kV, 12/16/20 MVA Mineola Pike distribution substation. | EKPC |  |  | Customer Service |  |  | UC | 11/18/2022 | 11/18/2022 | 0.73 |  | 12/11/2023 | Scope/Cost Change
PJM WEST | s2846 | Disconnect Brown TB1’s 34 kV tertiary winding. Install a new 138 kV circuit breaker into the ring bus to create a new position. Connect a new 138/34 kV, 60 MVA transformer in this position. Feed the 34 kV distribution bus from the new transformer. Expand the substation to make room for the new transformer and equipment. | DEOK |  |  | Infrastructure Resilience |  |  | UC | 11/18/2022 | 11/18/2022 | 1.26 |  | 12/11/2023 | Scope/Cost Change
PJM MA | n8327 | Replace existing 23kV Bedford relaying with (1) SEL-351S and install (1) SATEC meter. | PENELEC |  |  |  | 9/15/2022 | 2/2/2025 | Cancelled | 10/3/2023 | 10/3/2023 | 0.774 |  | 2/26/2025 | Cancelled
PJM SOUTH | n8282 | Install 1 new interconnect at Chesterfield 230 kV Station | Dominion |  |  |  | 12/1/2025 |  | UC | 11/3/2026 | 11/3/2026 | 3.748 |  |  | New Upgrade
PJM WEST | n8233 | Morgans Cut Station Circuit Breaker Addition and Associated Work | AEP |  |  |  | 11/1/2020 |  | Cancelled | 1/9/2024 | 1/9/2024 | 1.2606 |  |  | Cancelled
PJM WEST | n8232 | Install Diverse UG/ADSS Fiber-Optic Cable Path | AEP |  |  |  | 11/1/2020 |  | Cancelled | 1/9/2024 | 1/9/2024 | 0.3667 |  |  | Cancelled
PJM MA | b3771 | Reconductor two (2) 230 kV circuits from Conastone to Northwest #2 | BGE |  | 2022-W1-94 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | UC | 12/6/2022 | 10/6/2026 | 37.76 | 136.2 | 2/15/2023 | Scope/Cost Change
PJM MA | b3770 | Rebuild 1.4 miles of existing single circuit 230 kV tower line between BGE's Graceton substation to the Brunner Island PPL tie-line at the MD/PA state line to double circuit steel pole line with one (1) circuit installed to uprate 2303 circuit | BGE |  | 2022-W1-912 | Baseline Load Growth Deliverability & Reliability | 6/1/2027 |  | UC | 12/6/2022 | 10/6/2026 | 8.4 | 11.04 | 2/15/2023 | Scope/Cost Change
PJM SOUTH | n8218 | Add 4th breaker to interconnection switchyard | Dominion |  |  |  | 12/1/2023 |  | IS | 11/3/2026 | 11/3/2026 | 0.844 |  |  | New Upgrade
PJM WEST | n8202 | Increase the maximum operating temperature of the 266 MCM ACSR conductor in the McKinney Corner Tap-Knob Lick 69 kV line section to 212 degrees F (12.53 miles) | EKPC | [5 empty] | Cancelled | 1/9/2024 | 1/9/2024 | 0.72 |  |  | Cancelled
PJM WEST | n8162 | ComEd 345kV L0304 SSTE rating is 1512 MVA. The upgrade will be to mitigate the sag on the Poweton - Tazewell 345 kV line and replace a 345kV disconnect switch. A preliminary estimate for this work is $9.7M with a estimated construction timeline of 30 months. Upon completion of this upgrade the new ratings will be 1679/2058/2107/2280/2622 MVA (SN/SLTE/SSTE/SLD/ALDR). | ComEd | [5 empty] | Cancelled | 10/8/2024 | 10/8/2025 | 3.7 |  | 2/26/2025 | Cancelled
PJM WEST | n8158 | Expand the Jug Street 138kV Station, including the addition of one (1) 138 kV circuit breaker, installation of associated protection and control equipment, line risers, switches, jumpers and supervisory control and data acquisition (SCADA) equpment. | AEP |  |  |  | 7/31/2019 | 6/1/2023 | Cancelled | 10/8/2024 | 10/8/2024 | 0.9386 |  | 2/26/2025 | Cancelled
PJM SOUTH | n8152 | dom-378: Add Additional 500/230 kV Transformer at Midlothian Substation | Dominion |  |  |  | 12/31/2022 | 12/31/2022 | Cancelled | 10/8/2025 | 10/8/2025 | 40 |  | 11/18/2025 | Cancelled
PJM MA | s2729 | South Plainfield Area Upgrade | PSEG |  |  | Customer Service |  |  | UC | 4/19/2022 | 4/19/2022 | 96.6 |  | 12/6/2022 | Scope/Cost Change
PJM MA | n8119 | AE2-256 Substation: Estimated in-sub fiber run to customer built fiber run outside AE2-256 substation. Estimated SCADA work at North Lebanon substation to support relay installation and updated relay settings. | ME |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.0518 |  | 11/18/2025 | Cancelled
PJM MA | n8118 | AE2-256 Substation: Construct a new 3-breaker ring bus on the 230 kV (1094) line between Copperstone and North Lebanon. Includes Project Management, Environmental, Forestry, Real Estate and Right of Way. | ME |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 6.1399 |  | 11/18/2025 | Cancelled
PJM SOUTH | s2705 | Using current 230kV standards and a minimum summer emergency rating of 1047 MVA, wreck and rebuild approximately 12 miles of double circuit 230kV Line #252 and 115kV Line #29 from Aquia Harbour Switching Station to Possum Point. At Possum Point, upgrade the wave trap on 230kV Line #252 to 3000A. At Aquia Substation, upgrade the 230kV Line #252 switches and leads to 3000A. At Aquia Harbour Switching Station, upgrade the 230kV Line #252 wave trap and a circuit breaker switch to 3000A. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 10/5/2021 | 10/5/2021 | 38 |  | 12/6/2022 | Scope/Cost Change
PJM SOUTH | s2701 | Rebuild approximately 15.7 miles of 115kV Line #105 Tarboro to normally open switch 96T105 with current 115kV standard construction practices. This includes replacing four COR-TEN® double circuit towers and excludes the double circuit tap to Shiloh DP. The new conductor will have a minimum normal summer rating of 393 MVA. Terminal equipment will be upgraded as needed. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 12/20/2021 | 12/20/2021 | 24.5 |  | 12/6/2022 | Scope/Cost Change
PJM SOUTH | n8049 | Build a new 115 kV Solar Farm to interconnect into the Suffolk Station Project AE2-104 provides for the construction of one new 115kV interconnect into Suffolk Substation. The objective of this project is to add one new line position and one new 115kV breaker installed at Suffolk Substation to support the new 49MW solar farm built by Switchgrass Solar I, LLC. Additional modifications will be required to accommodate this additional infrastructure. | Dominion |  |  |  | 12/30/2024 | 12/30/2024 | Cancelled | 1/9/2024 | 1/9/2024 | 3.349 |  |  | Cancelled
PJM WEST | n8047 | North Waldo Fiber Exenstion | AEP |  |  |  | 9/22/2017 | 6/1/2027 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | n8022 | Copperstone Substation (PPL): Replace CVT & Line/carrier Relaying. | PPL |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.5175 |  | 11/18/2025 | Cancelled
PJM MA | n8021 | North Hershey – North Temple 230 kV: Install one steel pole strain structure on the existing North Hershey-North Temple 230 kV line to avoid clearance violations to new loop structures on the 1094-1 (Copperstone-North Lebanon) 230 kV line | ME |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 1.041 |  | 11/18/2025 | Cancelled
PJM MA | n8020 | Copperstone – North Lebanon 230 kV: Loop the 1094-1(Copperstone- North Lebanon) 230 kV line into a new substation, approximately 7.5 miles from the North Lebanon substation. | ME |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 2.3331 |  | 11/18/2025 | Cancelled
PJM MA | n8019 | North Lebanon Substation: Replace CVT & Line/carrier Relaying. | ME |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.6673 |  | 11/18/2025 | Cancelled
PJM MA | n8018 | AE2-256 Substation: Design, install, and test/commission MPLS Equipment for SCADA transport. | ME |  |  |  | 6/30/2022 |  | Cancelled | 10/3/2023 | 10/3/2023 | 0.2946 |  | 11/18/2025 | Cancelled
PJM WEST | n7990 | Upgrade line protection and controls at the West Mount Vernon 138kV station | AEP |  |  |  | 9/22/2017 | 6/1/2027 | Cancelled | [5 empty] | Cancelled
PJM WEST | n7989 | North Waldo-LaRue 138kV T-Line Cut In | AEP |  |  |  | 9/22/2017 | 6/1/2027 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n7988 | New 138 kV Station Oversight | AEP |  |  |  | 9/22/2017 | 6/1/2027 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n7968 | Wheatland (AD2-158 Interconnect): Upgrade relaying as needed to accommodate the new AE2-226 generation queue project interconnection of 99 MW MFO. | APS |  |  |  | 12/1/2022 | 12/31/2026 | Cancelled | 10/3/2023 | 10/3/2023 | 0.3575 |  | 2/26/2025 | Cancelled
PJM WEST | n7941 | perform sag mitigation on the line | ComEd |  |  |  | 12/31/2023 |  | EP | [5 empty] | New Upgrade
PJM SOUTH | s2607 | Replace Harrisonburg TX#6 with a new three phase, 230/69/13.2 kV, 168 MVA unit. Include other ancillary equipment (arresters, switches, relays, etc.) as needed. | Dominion |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 6/8/2021 | 6/8/2021 | 3.2 |  | 12/8/2021 | Scope/Cost Change
PJM MA | s2588 | Construct second half of 230-13kV Class H station at existing North Bergen station. Install Two (2) additional new 230-13kV transformers and associated equipment. Transfer load from heavily loaded Homestead and Penhorn to the new second half North Bergen 230kV station. | PSEG |  |  | Customer Service |  |  | IS | 8/31/2021 | 8/31/2021 | 28.9 |  | 12/6/2022 | Scope/Cost Change
PJM WEST | n7908 | Replace the Claytor 138 kV Station remote end Circuit Breaker “A” line relays with a dual carrier system and implement required settings. Install breaker controls and a second line trap | AEP |  |  |  | 11/1/2020 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 0.4193 |  |  | Cancelled
PJM WEST | n7907 | Upgrade line protections & controls at the Glen Lyn 138kV Station | AEP |  |  |  | 3/28/2018 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 0.5 |  |  | Cancelled
PJM WEST | n7906 | Claytor - Glen Lyn 138 kV #2 Ckt T-Line New Station Cut-In & OPGW to Morgans Cut | AEP |  |  |  | 11/1/2020 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 1.4996 |  |  | Cancelled
PJM WEST | n7905 | 138kV Revenue Meter, Generator lead transmisison line first span exiting the POI station, including the first structure outside the fence | AEP |  |  |  | 3/28/2018 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 1.7752 |  |  | Cancelled
PJM WEST | n7904 | Construct a new three (3) circuit breaker AD2-179 138 kV station | AEP |  |  |  | 11/1/2020 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 4.3716 |  |  | Cancelled
PJM MA | b3372 | East Towanda – North Meshoppen 115 kV Line: Rebuild 2.5 miles of 636 ACSR with 1113 ACSS conductor using single circuit construction. Upgrade all terminal equipment to the rating of 1113 ACSS | PENELEC |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2026 |  | Cancelled | 11/18/2021 | 11/18/2021 | 6.66 |  |  | Cancelled
PJM MA | b3370 | Upgrade terminal equipment on the Loretto - Fruitland 69 kV circuit: Replace the 477 ACSR stranded bus on the 6711 line terminal inside Loretto substation and the 500 SDCU stranded bus on the 6711 line terminal inside Fruitland substation with 954 ACSR conductor | DPL |  |  | Baseline Load Growth Deliverability & Reliability | 6/1/2026 |  | Cancelled | 11/18/2021 | 11/18/2021 | 0.8 |  |  | Cancelled
PJM MA | n7890 | Short Circuit Study, Review IC Engineering Package, and Remote End Work at the Milton 69 kV Substation | PPL |  |  |  | 3/5/2021 | 12/15/2022 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | n7889 | Complete MILT-MVIL line modifications to tie in the new AE2-084 Attachment Facilities. This includes connecting the conductors and OPGW from the MILT-MVIL line to the new tap structure. | PPL |  |  |  | 3/5/2021 | 12/15/2022 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM MA | n7888 | 69 kV Tap line, MOLBAB Switch, Poles, structure, and foundations. | PPL |  |  |  | 3/5/2021 | 12/15/2022 | Cancelled |  |  |  |  | 11/18/2025 | Cancelled
PJM WEST | n7881 | Perform a sag study on the Dearborn – Pierce 345kV line transmission line. OVECs cost estimate for performing the sag study is $125K. Sag study results (from AE2-297 Fac Study) show the need to replace 16 tangent structures, 3 dead end structures, and conductor over one Ohio river crossing. Cost estimate is $11.383 M. New SE rating to be 1165 MVA | OVEC |  |  |  | 12/31/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 11.38 |  | 2/26/2025 | Cancelled
PJM MA | s2564 | Install a new 230kV substation (Oak Tree Road) with two (2) 230/13kV transformers. Cut and loop the New Dover-Metuchen 230kV line in to the 230kV bus and transfer load from heavily loaded New Dover and Kilmer to the new station | PSEG |  |  | Customer Service |  |  | UC | 3/9/2021 | 3/9/2021 | 48 |  | 12/8/2021 | Scope/Cost Change
PJM SOUTH | n7553 | Replace Northern Neck 115/230 kV transformer #6 with a 224 MVA (260/271/295 MVA). | Dominion |  |  |  | 10/31/2023 | 10/31/2023 | EP | 11/3/2026 | 11/3/2026 | 7.2423 |  |  | New Upgrade
PJM SOUTH | n7526 | dom-429: Reconductor 0.877 miles of 115 kV Line 65 from Whitestone to Rappahannock with 768.2 ACSS 250 C | Dominion |  |  |  | 12/31/2022 | 12/31/2022 | Cancelled | 10/8/2025 | 10/8/2025 | 1.1401 |  | 11/18/2025 | Cancelled
PJM SOUTH | n7513 | dom-474: Rebuild 1.07 miles of 230 kV Line 299 from Marsh Run to Remington CT with 2-636 ACSR 150 C | Dominion |  |  |  | 12/1/2023 | 12/1/2023 | Cancelled | 10/8/2025 | 10/8/2025 | 2.9 |  | 11/18/2025 | Cancelled
PJM WEST | n7467 | Replace Marysville breaker on the AF2-137 Tap - Marysville 765 kV line | AEP |  |  |  | 7/16/2026 |  | UC | [5 empty] | Scope/Cost Change
PJM MA | s2537 | Construct a new Constable Hook 69/13kV substation in the Bergen Neck Area to feed Bergen Point load and provide for future load growth. | PSEG |  |  | Equipment Material Condition, Performance and Risk^Other |  |  | UC | 4/14/2021 | 4/14/2021 | 116 |  | 12/8/2021 | Scope/Cost Change
PJM WEST | s2532 | Rebuild the 22.1 mile, KU Carrollton-Bedford 69kV line using 556.5 ACSR/TW conductor and steel poles & structures (All of the single structures will be replaced; The H-Frame tangent structures will be evaluated on structure by structure basis). | EKPC |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 5/21/2021 | 5/21/2021 | 12.3 |  | 12/8/2021 | Scope/Cost Change
PJM WEST | s2531 | Rebuild the 12.3 mile, Maytown Tap-Hot Mix Road Tap 69kV line using 556.5 ACSR/TW conductor and steel poles & structures (12.3 miles of H-Frame tangent structures will be evaluated on structure by structure basis). | EKPC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 5/21/2021 | 5/21/2021 | 8.78 |  | 12/8/2021 | Scope/Cost Change
PJM WEST | s2530 | Rebuild the 14.2 mile, Peyton Store-Liberty Jct 69kV line using 556.5 ACSR/TW conductor and steel poles & structures (2.42 miles of single structures will be replaced; 11.78 miles of H-Frame tangent structures will be evaluated on structure by structure basis). | EKPC |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 5/21/2021 | 5/21/2021 | 9.6 |  | 12/8/2021 | Scope/Cost Change
PJM MA | n7421 | Tyrone North Substation: Relay settings changes | PENELEC |  |  |  | 9/1/2021 |  | Cancelled | [5 empty] | Cancelled
PJM MA | n7420 | Warrior Ridge Substation: Relay settings changes | PENELEC |  |  |  | 9/1/2021 |  | Cancelled | [5 empty] | Cancelled
PJM MA | n7419 | Williamsburg Substation: Relay settings changes | PENELEC |  |  |  | 9/1/2021 |  | Cancelled | [5 empty] | Cancelled
PJM MA | n7418 | Warrior Ridge – Williamsburg 46 kV Line Tap: Tap the Warrior Ridge-Williamsburg 46kV line to provide interconnection facilities to the customer substation, approximately 2.9 miles from the ABW Tap. | PENELEC |  |  |  | 9/1/2021 |  | Cancelled | [5 empty] | Cancelled
PJM MA | n7399 | 69 kV Tap line, MOLBAB Switch, Poles, structure, and foundations. | PPL |  |  |  | 9/30/2020 | 12/31/2022 | Cancelled | [5 empty] | Cancelled
PJM MA | n7401 | • Model IC in CAPE and conduct a wide area short circuit study two busses away from the IC facilities. Identify affected relays and revise settings as needed. Conduct a detailed review of the IC relay settings and engineering packaged submitted by IC to the PPL EU. Modify relays accordingly. | PPL |  |  |  | 9/30/2020 | 12/31/2022 | Cancelled | [5 empty] | Cancelled
PJM MA | n7400 | • Replace existing steel monopole structure (grid # 25248S55793) with a new custom steel monopole with foundation, double circuit tap structure. • Reframe structures 25249S55863 and 25245S55718, adjacent to the new tap pole, from suspension to tension | PPL |  |  |  | 9/30/2020 | 12/31/2022 | Cancelled | [5 empty] | Cancelled
PJM MA | s2491 | Convert existing Elizabeth 26/4kV substation to a 69/4kV substation | PSEG |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 2/16/2023 | 2/16/2023 | 97.8 |  | 12/8/2021 | Scope/Cost Change
PJM MA | s2483 | Convert existing Spring Valley Rd 69/4kV substation to a 69/13kV substation. Replace three (3) 69/4kV transformers with two (2) 69/13kV transformers at Spring Valley Rd | PSEG |  |  | Customer Service |  |  | IS | 1/14/2021 | 1/14/2021 | 13.2 |  | 12/8/2021 | Scope/Cost Change
PJM WEST | n7353 | Clark 138 k Substation: Install two (2) 138 kV wave traps and tuners. Update Relay Settings. | ATSI |  |  |  | 5/29/2020 | 12/31/2024 | Cancelled |  |  | 0.1303 |  |  | Cancelled
PJM WEST | n7354 | Greene 138 kV Substation: Modify relaying. | Dayton |  |  |  | 5/29/2020 | 12/31/2024 | Cancelled |  |  | 0.15 |  |  | Cancelled
PJM WEST | n7352 | AD1-140 Clark-Green 138 kV Line Loop: Loop the Clark-Greene 138kV circuit into the new AD1-140 Interconnection Switchyard. The proposed location of the new ring bus is near structure #5604. Includes project management, environmental, forestry, real estate and right-of-way. | ATSI |  |  |  | 5/29/2020 | 12/31/2024 | Cancelled |  |  | 0.4127 |  |  | Cancelled
PJM WEST | n7351 | Fiber Communication: ADSS fiber run from AD1-140 Interconnection Switchyard control house to Greene-East Springfield line fiber and to developer built fiber run to support communications and control to the generator site. | ATSI |  |  |  | 5/29/2020 | 12/31/2024 | Cancelled |  |  | 0.0811 |  |  | Cancelled
PJM WEST | n7350 | AD1-140 Supervisory Control and Data Acquisition (SCADA): Design, install and test/commission Multiprotocol Label Switching (MPLS) equipment for SCADA transport. | ATSI |  |  |  | 5/29/2020 | 12/31/2024 | Cancelled |  |  | 0.1988 |  |  | Cancelled
PJM WEST | n7349 | Engineering and construction oversight for a new 3-breaker ring bus on the Greene-Clark 138 kV line for the AD1-140 customer. Includes review of drawings, nameplates, and relay settings for FirstEnergy standards. Includes Project Management, Environmental and Right of Way. | ATSI |  |  |  | 5/29/2020 | 12/31/2024 | Cancelled |  |  | 0.7156 |  |  | Cancelled
PJM WEST | n7288 | Dual Fiber Telecom from Payne to the IPP station | AEP |  |  |  | 9/28/2017 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 1.7344 |  |  | Cancelled
PJM WEST | n7287 | Installation of gen tie line connecting Payne station to the IPP generator | AEP |  |  |  | 9/28/2017 | 12/31/2022 | Cancelled | 1/9/2024 | 1/9/2024 | 0.108 |  |  | Cancelled
PJM MA | s2415 | New 69/13kV Stationin Eastern Bergen County Area. | PSEG |  |  | Equipment Material Condition, Performance and Risk^Customer Service |  |  | IS | 11/18/2020 | 11/18/2020 | 99.2 |  | 12/8/2021 | Scope/Cost Change
PJM SOUTH | n7180 | Rebuild 7.2 miles of 230 kV Line 235 from Prince EDW to Farmville with (2) 768.2 ACSS/TW (20/7) "MAUMEE" at 250 C. | Dominion |  |  |  | 12/31/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 20.7 |  | 2/26/2025 | Cancelled
PJM WEST | n6933 | Update relays | ComEd |  |  |  |  | 12/26/2022 | Cancelled | [5 empty] | Cancelled
PJM WEST | n6932 | Update relays | ComEd |  |  |  |  | 12/26/2022 | Cancelled | [5 empty] | Cancelled
PJM WEST | n6931 | Install communications equipment | ComEd |  |  |  |  | 12/26/2022 | Cancelled | [5 empty] | Cancelled
PJM WEST | n6930 | Cut circuit and loop into new substation | ComEd |  |  |  |  | 12/26/2022 | Cancelled | [5 empty] | Cancelled
PJM WEST | n6929 | Construct new substation | ComEd |  |  |  |  | 12/26/2022 | Cancelled | [5 empty] | Cancelled
PJM MA | n6928 | Install an additional 138kV circuit breaker (CB 135), 138kV line disconnect switch, 138kV CCVTs (P7), and new protection & control relaying at Carville 138 kV substation | DPL |  |  |  | 6/3/2024 |  | Cancelled | 11/1/2022 | 11/1/2022 | 1.09 |  |  | Cancelled
PJM MA | s2385 | Construct new 230-13kV Station along the existing ROW in Pennsauken, cut and loop the Camden-Cinnaminson 230kV line into the new 230kV bus (Pennsauken), and install a 230kV station with two (2) 230/13kV transformers. Transfer load from heavily loaded Cuthbert Blvd to the new station. | PSEG |  |  | Customer Service |  |  | UC | 10/6/2020 | 10/6/2020 | 48.6 |  | 12/8/2021 | Scope/Cost Change
PJM MA | s2318 | Construct a new Central Ave 69/4 kV Station in Western Newark Area | PSEG |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 8/13/2020 | 8/13/2020 | 34.3 | 34.3 |  | Scope/Cost Change
PJM MA | n6867 | Upgrade relaying at East Flemington 34.5 kV. | JCPL |  |  |  | 4/17/2020 | 6/30/2026 | Cancelled | 10/8/2024 | 10/8/2024 | 0.403 |  | 2/26/2025 | Cancelled
PJM MA | n6865 | Construct a tap and install 3-34.5 kV load-break air switches on the West Flemington Tap - Frenchtown Solar 2 portion of the East Flemington - Frenchtown (A729) 34.5 kV line. | JCPL |  |  |  | 4/17/2020 | 6/30/2026 | Cancelled | 10/8/2024 | 10/8/2024 | 0.403 |  | 2/26/2025 | Cancelled
PJM MA | n6864 | Add a new position to Harrington Substation’s 69 kV ring bus by installing a new circuit breaker between the capacitor bank position and the Line 6739 position | DPL |  |  |  | 2/1/2021 |  | EP | [5 empty] | New Upgrade
PJM WEST | n6776 | Sag Study will be required on 37.9 miles of line between Bixby and Kirk | AEP | [5 empty] | Cancelled | 10/8/2025 | 10/8/2025 | 0.1516 |  | 11/18/2025 | Cancelled
PJM MA | n6728 | To mitigate the (ACE) Cedar Oyster Creek 230 kV line (from bus 227955 to bus 206302 ckt 1) overload, it will require increasing the emergency rating of the Cedar to Oyster Creek 230 kV line by rebuilding the circuit. The rebuild will include the installation of new poles, foundations, insulators, and conductor. In addition, various terminal reinforcements are required at Cedar. | AEC | [5 empty] | Active | 1/9/2024 | 1/9/2024 | 63 |  |  | Scope/Cost Change
PJM SOUTH | n6716 | Modify protection and communication work to support interconnection of new AC1-191 generator | Dominion |  |  |  | 12/31/2020 |  | Cancelled | 10/8/2025 | 10/8/2025 | 0.169 |  | 11/18/2025 | Cancelled
PJM SOUTH | n6715 | Build new structures to cut and loop the transmission line into AC1-191 115 kV substation | Dominion |  |  |  | 12/31/2020 |  | Cancelled | 10/8/2025 | 10/8/2025 | 2.29 |  | 11/18/2025 | Cancelled
PJM MA | n6690 | Relay Modification Scope of Work | PPL |  |  |  | 9/30/2020 |  | Cancelled |  |  | 0.2046 |  |  | Cancelled
PJM MA | n6689 | Modifications to the Face Rock - Kinzer 69 kV line to tie in the AE1-226 Attachment Facilities | PPL |  |  |  | 9/30/2020 |  | Cancelled |  |  | 0.0929 |  |  | Cancelled
PJM MA | n6688 | Attachment Facilities: 69 kV Tap line, MOLBAB Switch, Poles, structure and foundations | PPL |  |  |  | 9/30/2020 |  | Cancelled |  |  | 0.8358 |  |  | Cancelled
PJM SOUTH | n6657 | Modify protection and communication work to support interconnection of new AC2-112 generator | Dominion |  |  |  | 10/31/2018 |  | Cancelled | 11/1/2022 | 11/1/2022 | 0.12 |  |  | Cancelled
PJM SOUTH | n6650 | Modify protection and communication work to support interconnection of new AC1-143 generator | Dominion |  |  |  | 6/30/2018 |  | Cancelled |  |  | 0.15 |  |  | Cancelled
PJM SOUTH | n6649 | Build new structures to cut and loop the transmission line into AC1-143 115 kV sustation | Dominion |  |  |  | 6/30/2018 |  | Cancelled |  |  | 1.8 |  |  | Cancelled
PJM SOUTH | n6648 | Build a three breaker 115 kV substation at the AC1-143 facility | Dominion |  |  |  | 6/30/2018 |  | Cancelled |  |  | 5.3 |  |  | Cancelled
PJM SOUTH | n6605 | Wreck and rebuild 0.99 miles of line 271 between Pocaty and Landstown with (2)-768 ACSS (20/7) “MAUMEE” conductor @ 250 degrees C. Replace the line lead at Landstown. | Dominion |  |  |  | 12/31/2026 |  | EP | 11/3/2026 | 11/3/2026 | 6.5558 |  |  | New Upgrade
PJM SOUTH | n6580 | Rebuild 16.45 miles of 500 kV Line 585 from AE2-094 Tap to Carson with 3-1351.5 125C ACSR. | Dominion |  |  |  | 6/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 50.995 |  | 2/26/2025 | Cancelled
PJM SOUTH | n6574 | Rebuild 14.53 miles of 500 kV Line 575 from North Anna to Ladysmith with 3-1351.5 113C ACSR | Dominion |  |  |  | 12/31/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 45.043 |  | 2/26/2025 | Cancelled
PJM SOUTH | n6437 | Rebuild 20.57 miles of 230 kV Line 2034 from Cashie to Earleys with 2-636 ACSR. | Dominion |  |  |  | 11/15/2020 |  | Cancelled | 1/9/2024 | 1/9/2024 | 30.855 |  |  | Cancelled
PJM MA | n6406 | R-PL-0003A: Rebuild AE1-058 yard-SIEG 230kV line. | PPL | [5 empty] | Cancelled | [5 empty] | Cancelled
PJM SOUTH | s2131 | Cut existing 230 kV line between Cannon Branch and Winters Branch substations. At Brickyard, install four (4) 230 kV breakers to terminate the two lines. Install two (2) 230 kV circuit switchers and any necessary high side switches and bus work for two initial transformers. | Dominion |  |  | Customer Service |  |  | IS | 10/17/2019 | 10/17/2019 | 2 |  |  | Scope/Cost Change
PJM SOUTH | n6378 | Rebuild 6.42 miles of 115 kV Line 91 from AE2-092 Tap to Sherwood with 2-636 ACSR. | Dominion | [5 empty] | Cancelled | 1/9/2024 | 1/9/2024 | 16.05 |  |  | Cancelled
PJM SOUTH | n6373 | Rebuild 5.07 miles of 115 kV Line 198 from Todds Tavern DP to Ni River DP with 768 ACSS. | Dominion | [5 empty] | Cancelled | 11/1/2022 | 11/1/2022 | 6.591 |  |  | Cancelled
PJM SOUTH | n6372 | Rebuild 1.34 miles of 115 kV Line 198 from Ni River DP to Chancellor with 768 ACSS. | Dominion | [5 empty] | Cancelled | 11/1/2022 | 11/1/2022 | 1.742 |  |  | Cancelled
PJM SOUTH | n6371 | Rebuild 7.46 miles of 115 kV Line 198 from Spotsylvania to Todds Tavern DP with 768 ACSS. | Dominion | [5 empty] | Cancelled | 11/1/2022 | 11/1/2022 | 9.698 |  |  | Cancelled
PJM WEST | n6330 | Perform a sag study on the AD2-071 Tap - Pipe Creek 138 kV line - replaced by s2902.1 | AEP |  |  |  | 12/1/2021 |  | Cancelled | 1/9/2024 | 1/9/2024 | 0.0328 |  |  | Cancelled
PJM WEST | n6329 | Perform a sag study on the Pipe Creek - 05GRNTTA 138 kV line - replaced by s2902.1 | AEP |  |  |  | 12/1/2021 |  | Cancelled | 1/9/2024 | 1/9/2024 | 0.02 |  |  | Cancelled
PJM SOUTH | n6314 | Shawboro – Elizabeth City 230 kV line #2021 | Dominion |  |  |  | 6/1/2020 |  | Cancelled | 1/9/2024 | 1/9/2024 | 15.42 |  |  | Cancelled
PJM SOUTH | s2100 | Interconnect the new Nimbus substation by cutting and extending 230kV Line #2152 (Buttermilk-Beaumeade). Terminate both ends into a four-breaker ring arrangement to create a Buttermilk-Nimbus line and a Nimbus-Beaumeade line. | Dominion |  |  | Customer Service |  |  | IS | 5/16/2019 | 5/16/2019 | 20 | 20 |  | Scope/Cost Change
PJM MA | s2034 | Convert Lincoln 115 kV to a six (6) breaker ring bus | ME |  |  | Operational Flexibility and Efficiency |  |  | EP | 7/31/2019 | 11/19/2019 | 6.9 | 6.9 |  | Scope/Cost Change
PJM SOUTH | n6237 | Modify protection and communication work to support interconnection of new AC1-105 generator | Dominion |  |  |  | 10/2/2019 |  | Cancelled |  |  | 0.18 |  |  | Cancelled
PJM SOUTH | n6236 | Build new structures to cut and loop the line into AC1-043 115 kV switching station | Dominion |  |  |  | 10/2/2019 |  | Cancelled | 1/9/2024 | 1/9/2024 | 1.43 |  |  | Cancelled
PJM SOUTH | n6235 | Build a three breaker ring bus at the new AC1-043 substation | Dominion |  |  |  | 10/2/2019 |  | Cancelled |  |  | 5.468 |  |  | Cancelled
PJM WEST | s1953 | Ayersville- Sand Ridge 69 kV Line - Conversion from 34.5 kV - Ayersville Substation: Install one (1) new 69 kV breaker. Install one (1) new 138 – 69 kV transformer. Install four (4) new 138 kV breakers and reconfigure the 138 kV yard to a four (4) breaker ring bus with a new 69 kV line exit to Weston Substation. Close in the N.O. switch A13404 at Ayersville to network Ayersville Substation to Richland Substation 138 kV K Bus. Remove all 34.5 kV equipment post conversion (ex: Richland 138 - 34.5 kV transformer #1 and circuit breakers). - Sand Ridge Substation: Build a new four (4) breaker, future six (6) breaker ring bus with 69 kV line exits for the new Ayersville line, the Midway and Bowling Green No.2 69 kV lines, and the Weston 69 kV line. - A new 69 kV tie line from Sand Ridge Substation to Weston Substation will be constructed using the same conductor as Ayersville – Sand Ridge 69 kV proposed line rebuild. Bowling Green No. 2-Midway 69 kV Line: - Rebuild 5.0 miles of 69 kV transmission line from Weston Substation to the Weston tap on the Bowling Green No2 - Midway 69 kV Line as double circuit to eliminate the three terminal line from Weston, Midway and Bowling Green No2 substations and extend both new lines and terminate into the new ring bus station (Sand Ridge). New Ayersville- Sand Ridge 69 kV Line: - Build new 5.6 miles 69 kV line to network Ayersville-Maroe and Weston-Malinta radial lines. - Rebuild 0.5 miles of 138 kV transmission line as double circuit 138 kV and 69 kV to network the Maroe radial line to Ayersville Substation; de-energize and retire the 34.5 kV line section from Richland Substation. - Convert the existing Richland-Maroe 34.5 kV Line to 69 kV (Approximately 17 miles) and re terminate line from Maroe Substation to Ayersville Substation; customers to upgrade existing substation equipment at Holgate Substation and Maroe Substation to 69 kV. - Convert the existing Weston-Malinta 34.5 kV Line to 69 kV (Approximately 13 miles) ; customers to upgrade existing substation equipment at Weston, McClure, and Malinta substations. - Remove all 34.5 kV equipment post conversion. - Install eight (8) SCADA and MOAB controlled switches on the new Ayersville- Sand Ridge 69 kV Line. | ATSI |  |  | Operational Flexibility and Efficiency^Infrastructure Resilience |  |  | UC | 3/25/2019 | 3/25/2019 | 50 | 99.3 |  | Scope/Cost Change
PJM WEST | s1941 | Rebuild the KU Wofford - Whitley City 69 kV line using 556.5 MCM ACSR/TW conductor (20.7 miles) | EKPC |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 3/25/2019 | 3/25/2019 | 13 |  |  | Scope/Cost Change
PJM MA | s1891 | Construct a 115 kV ring bus at the Titusville. | PENELEC |  |  | Operational Flexibility and Efficiency |  |  | UC | 3/25/2019 | 11/19/2019 | 9.3 | 9.3 |  | Scope/Cost Change
PJM WEST | n6187 | Reconductor the X1-027A to Beaver substation (On Beaver-Davis Besse 345 kV Line). | ATSI |  |  |  | 6/1/2022 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n6186 | Reconductor the existing Beaver-Lake Ave #2 345 kV line. Reconductor substation conductor, line drop and switches at both terminals. | ATSI |  |  |  | 6/1/2022 |  | Cancelled | [5 empty] | Cancelled
PJM WEST | n6185 | Build a new 138 kV line from Black River to Astor substation. | ATSI |  |  |  | 6/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 18.67 |  | 2/26/2025 | Cancelled
PJM SOUTH | n6179 | Rebuild 12.3 miles of 230 kV Line 2003 from Poe to Harrowgate with 2-636 ACSR. | Dominion | [5 empty] | Cancelled | 10/8/2024 | 10/8/2024 | 30.75 |  | 2/26/2025 | Cancelled
PJM SOUTH | n6130 | Rebuild 12.4 miles 2-636 ACSR between Chesterfield-Basin 230 kV, Ratings after the upgrade: 1047/1047/1204 | Dominion |  |  |  | 12/1/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 31 |  | 2/26/2025 | Cancelled
PJM MA | s1823 | Build a new Walnut Ave 69 kV Substation. Eliminate Clark substation. Transfer load from nearby heavily loaded Aldene, Warinanco, and Westfield to the new station | PSEG |  |  | Equipment Material Condition, Performance and Risk^Customer Service |  |  | UC | 1/25/2019 | 5/24/2019 | 146 | 146 |  | Scope/Cost Change
PJM MA | s0811 | Rebuild the BL England - Scull - Mill - Lewis 138 kV #1 circuit '1407' | AEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/24/2014 | 9/24/2014 | 11.46 |  |  | Scope/Cost Change
PJM MA | s0812 | Rebuild the BL England - Scull - Mill - Lewis 138 kV #2 circuit '1408' | AEC |  |  | Equipment Material Condition, Performance and Risk |  |  | EP | 9/24/2014 | 9/24/2014 | 9.55 |  |  | Scope/Cost Change
PJM WEST | s1756 | Replace New Castle #7 138/69 kV Transformer. Replace existing New Castle #7 138/69/4.2 kV transformer (125 MVA) with new 138/69 kV transformer (134 MVA). Replace existing 69 kV breaker (B32). Install new 69/4.2 kV transformer (15 MVA) and a 69 kV circuit breaker in existing 69 kV transformer position for generation station service. | ATSI |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 10/26/2018 | 10/26/2018 | 3.9 |  |  | Scope/Cost Change
PJM WEST | n5780 | Reconductor Stuart-Spurlock 345 kV line with twin bundle 1033 Curlew ACCR conductor | EKPC |  |  |  | 7/1/2022 |  | Cancelled | 10/8/2024 | 10/8/2024 | 17 |  | 2/26/2025 | Cancelled
PJM MA | s1671 | Build new 115kV station to supply 34kV & 13kV distribution station, Provide diverse overhead transmission supplies from Riverside and Windy Edge substations to new 115kV station | BGE |  |  | Operational Flexibility and Efficiency^Customer Service |  |  | UC | 5/25/2018 | 7/20/2018 | 45 | 45 |  | Scope/Cost Change
PJM MA | s1670 | Rebuild both Five Forks – Windy Edge 115kV (110511, 110512) circuits using steel monopole, double circuit construction with sufficient capacity to support future needs | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | IS | 5/25/2018 | 7/20/2018 | 60 | 60 | 11/18/2024 | Scope/Cost Change
PJM MA | n5667 | Install breaker, disconnect switches, CVT’s and installation of relays/controls, and install fiber interface for new AC1-048 & AC2-053 fiber or OPGW. Fiber Work - Install in-sub fiber runs. | ME |  |  |  | 10/2/2017 | 12/31/2020 | Cancelled | 9/13/2018 | 9/13/2018 | 1.18 |  |  | Cancelled
PJM WEST | n5629 | Install protection and controls at the new 138 kV switching station. | AEP |  |  |  | 6/1/2019 |  | Cancelled | 9/13/2018 | 9/13/2018 | 0.25 |  |  | Cancelled
PJM WEST | n5628 | Install 138 kV Revenue Metering at the new AC1-122/123 | AEP |  |  |  | 6/1/2019 |  | Cancelled | 9/13/2018 | 9/13/2018 | 0.25 |  |  | Cancelled
PJM MA | s1631 | Build a new Loch Raven 115/13 kV substation | BGE |  |  | Equipment Material Condition, Performance and Risk |  |  | UC | 3/23/2018 | 5/25/2018 | 130 | 130 |  | Scope/Cost Change
PJM SOUTH | n5609 | Rebuild 41.13 miles of 500 kV Line 576 from Midlothian to North Anna with 3-1351.5 125C ACSR with the following ratings: Rate A: 4816, Rate B: 4816 & Rate C: 5539 | Dominion |  |  |  | 12/1/2021 |  | Cancelled | 10/8/2024 | 10/8/2024 | 234.441 |  | 2/26/2025 | Cancelled
PJM WEST | n5967 | A sag study will be required on the 19.33 mile AEP section of line to mitigate the overload. Depending on the sag study results, cost for the upgrade is expected to be between $78,000 (no remediation required just sag study) or $39.0 million (complete line rebuild required) | AEP |  |  |  | 6/1/2020 |  | Cancelled | 9/13/2018 | 9/13/2018 | 0.078 |  |  | Cancelled
PJM WEST | n5252 | Mitigate the sag on the Wilton - Dumont 765 kV line L11215 to achieve an ALDR that exceeds 6166 MVA. | ComEd |  |  |  | 6/1/2020 |  | Cancelled | 10/12/2017 | 10/12/2017 | 9 |  |  | Cancelled
PJM WEST | n6639.4 | 1) Upgrade 345kV station conductor at TSS 111 Electric Junction and TSS 155 Nelson. 2) Upgrade 345kV L15502 circuit breaker line and bus motor operated disconnect (MOD) switches. | ComEd | [5 empty] | EP | [5 empty] | New Upgrade
PJM WEST | n6639.2 | Replace existing 345kV line conductor and possibly tower structures for approx. 27 miles, Sag mitigation on existing 345kV line conductor for up to 13 miles, Upgrade station 345kV conductor and motor operated switches, Upgrade 345kV relay scheme at one terminal substation. Tower work and cost will be identified during the Facility Study Phase. | ComEd | [5 empty] | EP | 11/3/2026 | 11/3/2026 | 146 |  |  | New Upgrade
PJM WEST | n4056.1 | AEPI0048a: Replace the 2 3000A 765kV CB's at Dumont station | AEP |  |  |  | 7/16/2026 |  | IS | [5 empty] | Scope/Cost Change
PJM WEST | n7165.2 | Reconductor All Dam 6 - Kittanning 138kV line | APS |  |  |  | 6/1/2028 |  | Cancelled | [5 empty] | Cancelled