## Oil Heat Rate Curves
No Load Cost = No Load Fuel * Fuel Cost
= $4380/hr
Fuel Cost = $14/mmBtu
VOM Cost = $0.15/mmBtu

## Gas Heat Rate Curves
Text here . . .
Change No Load Cost to $1008/hr
No Load Cost = No Load Fuel * Fuel Cost
Fuel Cost = $4/mmbtu
VOM Cost = $0.15/mmBtu
= $1007.76 $/hr
MW

## Heat Rate & Cost Curves
Heat Rate & Cost Curves
a= | 306.744 | (No Load Fuel) |  |  | Fuel Cost | 14 | $/mmBtu
b= | 9.6894 |  |  |  | VOM | 0.15 | $/mmBtu
c= | 0.0015639 |  |  |  | PF | 1.02
Oil |  |  |  | Incremental | No Load = | 4380.3043 | $/hr
Net Gen | Heat Input | Heat Rate | Total Cost | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh | $/MWH | Btu/Kwh |  | $/MWH
0 | 306.744
50 | 795.1238 | 15902.4755 | 229.5204 | 9767.5955 |  | 141.9143 | 141.9143
160 | 1897.0841 | 11856.7756 | 171.1288 | 10017.8211 |  | 144.5872 | 144.5872
310 | 3460.7498 | 11163.7089 | 161.1258 | 10424.4377 |  | 150.4559 | 150.4559
410 | 4542.2913 | 11078.7592 | 159.8997 | 10815.4152 |  | 156.0989 | 156.0989
525 | 5824.7317 | 11094.727 | 160.1302 | 11151.6558 |  | 160.9518 | 160.9518
550 | 6108.9968 | 11107.2669 | 160.3112 | 11370.6033 |  | 164.1119 | 164.1119
a= | 238.232 | (No Load Fuel) |  |  | Fuel Cost | 4 | $/mmBtu
b= | 10.7195 |  |  |  | VOM | 0.15 | $/mmBtu
c= | 0.00014832 |  |  |  | PF | 1.02
Gas |  |  |  | Incremental | No Load = | 1007.76 | $/hr
Net Gen | Heat Input | Heat Rate | Total Cost | Heat Rate |  | Incremental Cost
MW | MMBtu/Hr | Btu/Kwh | $/MWH | Btu/Kwh |  | $/MWH
0 | 247
50 | 774.5778 | 15491.556 | 65.5758 | 10551.556 |  | 45.4206 | 45.4206
160 | 1957.149 | 12232.1814 | 51.7788 | 10750.6474 |  | 45.5075 | 45.5075
310 | 3575.5306 | 11533.9698 | 48.8233 | 10789.2109 |  | 45.6707 | 45.6707
410 | 4658.1598 | 11361.3653 | 48.0927 | 10826.2911 |  | 45.8277 | 45.8277
525 | 5906.8505 | 11251.1438 | 47.6261 | 10858.1801 |  | 45.9627 | 45.9627
550 | 6178.8241 | 11234.2256 | 47.5545 | 10878.9451 |  | 46.0506 | 46.0506
no load check box checked
TRUE |  |  | = $1007.76 $/hr

## Oil Heat Input
Fitted Regression Line Equation
No Load Fuel = 306.744 mmBtu/hr
MW

## Oil Data
MONTH | DAY | HOUR |  |  |  |  | #6 Oil | Gas | Total
|  |  | Net Load | MFO Flw | MFO Ret | KTherms | 151137
11 | 4 | 9 | 41.7 | 82.6854 | 7.9113 | 0.5 | 678068658.3966 | 50000000 | 728068658.3966
6 | 22 | 4 | 43.7 | 75.1828 | 0 | 0.4 | 681774131.6129 | 40000000 | 721774131.6129
6 | 22 | 5 | 43.7 | 75.7049 | 0 | 0.4 | 686508674.1935 | 40000000 | 726508674.1935
6 | 22 | 3 | 43.8 | 74.7422 | 0 | 0.4 | 677779106.778 | 40000000 | 717779106.778
7 | 12 | 4 | 43.9 | 68.5447 | 0 | 0.3 | 621578383.7664 | 30000000 | 651578383.7664
7 | 12 | 3 | 44 | 68.619 | 0 | 0.3 | 622252620 | 30000000 | 652252620
7 | 12 | 2 | 44.2 | 68.7672 | 0 | 0.3 | 623596287.9335 | 30000000 | 653596287.9335
12 | 20 | 14 | 44.3 | 80.9276 | 2.575 | 0.5 | 710519240.4342 | 50000000 | 760519240.4342
1 | 30 | 19 | 44.3 | 81.9786 | 2.5224 | 0.4 | 720526553.6797 | 40000000 | 760526553.6797
7 | 12 | 1 | 44.3 | 68.841 | 0 | 0.3 | 624265731.032 | 30000000 | 654265731.032
6 | 22 | 2 | 44.4 | 75.2275 | 0 | 0.4 | 682179412.6066 | 40000000 | 722179412.6066
12 | 20 | 13 | 44.5 | 81.1006 | 2.5805 | 0.5 | 712037707.5621 | 50000000 | 762037707.5621
7 | 11 | 24 | 44.5 | 68.9882 | 0 | 0.3 | 625599863.787 | 30000000 | 655599863.787
9 | 13 | 12 | 44.6 | 83.8227 | 3.1631 | 0.4 | 731438766.383 | 40000000 | 771438766.383
10 | 15 | 1 | 44.6 | 78.0236 | 4.5865 | 0.1 | 665943922.5957 | 10000000 | 675943922.5957
1 | 29 | 23 | 44.6 | 82.2411 | 2.5305 | 0.4 | 722833604.4255 | 40000000 | 762833604.4255
9 | 13 | 11 | 44.7 | 83.9115 | 3.2192 | 0.4 | 731734692.5455 | 40000000 | 771734692.5455
10 | 15 | 2 | 44.9 | 79.3286 | 4.6539 | 0.1 | 677166391.2085 | 10000000 | 687166391.2085
1 | 29 | 24 | 45 | 82.5882 | 2.5412 | 0.4 | 725884339.7647 | 40000000 | 765884339.7647
9 | 13 | 10 | 45.1 | 84.2644 | 3.1798 | 0.4 | 735293048.9542 | 40000000 | 775293048.9542
7 | 14 | 3 | 45.2 | 74.8028 | 0 | 0.5 | 678328400.2817 | 50000000 | 728328400.2817
9 | 12 | 22 | 45.3 | 83.9086 | 3.1864 | 0.4 | 732006279.3904 | 40000000 | 772006279.3904
9 | 13 | 13 | 45.3 | 83.9086 | 3.1864 | 0.4 | 732006279.3904 | 40000000 | 772006279.3904
1 | 29 | 17 | 45.3 | 81.7843 | 2.496 | 0.4 | 719003536.2696 | 40000000 | 759003536.2696
1 | 30 | 15 | 45.4 | 83.4637 | 2.5518 | 0.4 | 733727306.9508 | 40000000 | 773727306.9508
7 | 13 | 6 | 45.4 | 66.452 | 0 | 0.5 | 602601270.4918 | 50000000 | 652601270.4918
9 | 13 | 18 | 45.5 | 84.0819 | 3.193 | 0.4 | 733518240 | 40000000 | 773518240
9 | 14 | 1 | 45.6 | 83.6355 | 3.1963 | 0.5 | 729440836.8224 | 50000000 | 779440836.8224
1 | 30 | 20 | 45.6 | 83.1028 | 2.557 | 0.4 | 730406983.6262 | 40000000 | 770406983.6262
9 | 8 | 1 | 45.7 | 79.9883 | 3.1462 | 0.4 | 696821282.8635 | 40000000 | 736821282.8635
9 | 13 | 17 | 45.7 | 84.2544 | 3.1995 | 0.4 | 735023143.6173 | 40000000 | 775023143.6173
7 | 14 | 2 | 45.7 | 75.7223 | 0 | 0.4 | 686666357.853 | 40000000 | 726666357.853
9 | 14 | 13 | 45.8 | 82.2051 | 3.1494 | 0.5 | 716894579.2028 | 50000000 | 766894579.2028
12 | 20 | 11 | 45.8 | 81.6713 | 2.6156 | 0.5 | 716894579.2028 | 50000000 | 766894579.2028
6 | 26 | 6 | 45.8 | 72.5967 | 0 | 0.4 | 658323178.7413 | 40000000 | 698323178.7413
9 | 14 | 15 | 45.9 | 83.3574 | 3.2061 | 0.5 | 726829973.2247 | 50000000 | 776829973.2247
9 | 14 | 17 | 45.9 | 82.8231 | 3.1526 | 0.5 | 722468993.3853 | 50000000 | 772468993.3853
9 | 13 | 14 | 45.9 | 84.4261 | 3.2061 | 0.4 | 736521039.5343 | 40000000 | 776521039.5343
9 | 7 | 24 | 46 | 79.6977 | 3.1023 | 0.4 | 694583474.2326 | 40000000 | 734583474.2326
9 | 13 | 15 | 46.1 | 84.597 | 3.2125 | 0.4 | 738011976.5854 | 40000000 | 778011976.5854
12 | 20 | 10 | 46.1 | 81.9199 | 2.57 | 0.5 | 719561677.1707 | 50000000 | 769561677.1707
1 | 10 | 18 | 46.1 | 80.849 | 2.4094 | 0.4 | 711307595.8537 | 40000000 | 751307595.8537
1 | 10 | 19 | 46.1 | 80.849 | 2.4094 | 0.4 | 711307595.8537 | 40000000 | 751307595.8537
9 | 14 | 16 | 46.2 | 83.0742 | 3.1622 | 0.5 | 724660185.7587 | 50000000 | 774660185.7587
9 | 14 | 18 | 46.2 | 82.5383 | 3.1622 | 0.5 | 719799956.478 | 50000000 | 769799956.478
1 | 30 | 4 | 46.2 | 83.6102 | 2.5726 | 0.4 | 734866667.2483 | 40000000 | 774866667.2483
9 | 14 | 14 | 46.3 | 83.1576 | 3.1654 | 0.5 | 725387197.8285 | 50000000 | 775387197.8285
9 | 13 | 16 | 46.4 | 84.8519 | 3.2222 | 0.4 | 740235440 | 40000000 | 780235440
1 | 24 | 17 | 46.4 | 84.3148 | 2.5241 | 0.5 | 741696431 | 50000000 | 791696431
1 | 30 | 1 | 46.4 | 83.7778 | 2.5778 | 0.4 | 736339464 | 40000000 | 776339464
9 | 13 | 24 | 46.5 | 84.3988 | 3.2254 | 0.5 | 736098343.6994 | 50000000 | 786098343.6994
1 | 30 | 8 | 46.5 | 82.7861 | 2.5803 | 0.4 | 727323661.4566 | 40000000 | 767323661.4566
1 | 22 | 18 | 46.5 | 83.8613 | 2.5803 | 0.2 | 737073308.3931 | 20000000 | 757073308.3931
1 | 22 | 19 | 46.5 | 84.3988 | 2.5803 | 0.2 | 741948131.8613 | 20000000 | 761948131.8613
12 | 20 | 9 | 46.6 | 82.3303 | 2.6367 | 0.5 | 722678494.2402 | 50000000 | 772678494.2402
1 | 30 | 3 | 46.6 | 83.9446 | 2.5829 | 0.4 | 737805457.9954 | 40000000 | 777805457.9954
1 | 30 | 21 | 46.6 | 83.9446 | 2.5829 | 0.4 | 737805457.9954 | 40000000 | 777805457.9954
12 | 18 | 19 | 46.7 | 82.4118 | 2.6393 | 0.5 | 723393978.5398 | 50000000 | 773393978.5398
12 | 18 | 22 | 46.7 | 82.4118 | 2.6393 | 0.5 | 723393978.5398 | 50000000 | 773393978.5398
1 | 21 | 18 | 46.7 | 86.7209 | 2.6393 | 0.5 | 762469953.0727 | 50000000 | 812469953.0727
1 | 21 | 19 | 46.7 | 86.7209 | 2.6393 | 0.5 | 762469953.0727 | 50000000 | 812469953.0727
1 | 18 | 21 | 46.7 | 85.6436 | 2.6393 | 0.3 | 752700959.4394 | 30000000 | 782700959.4394
11 | 7 | 19 | 46.8 | 84.1106 | 4.3673 | 0.5 | 723129950.9032 | 50000000 | 773129950.9032
1 | 24 | 16 | 46.8 | 84.1106 | 2.5341 | 0.5 | 739753627.9355 | 50000000 | 789753627.9355
1 | 7 | 9 | 46.8 | 83.5714 | 2.4802 | 0.4 | 735353242.8387 | 40000000 | 775353242.8387
1 | 7 | 10 | 46.8 | 83.5714 | 2.4802 | 0.4 | 735353242.8387 | 40000000 | 775353242.8387
1 | 20 | 22 | 46.8 | 86.2673 | 2.6959 | 0.4 | 757844100 | 40000000 | 797844100
7 | 16 | 4 | 46.8 | 74.4055 | 0 | 0.5 | 674725714.8387 | 50000000 | 724725714.8387
12 | 18 | 13 | 46.9 | 82.0345 | 2.7525 | 0.5 | 718947056.3199 | 50000000 | 768947056.3199
1 | 22 | 11 | 46.9 | 84.733 | 2.6985 | 0.3 | 743907097.0771 | 30000000 | 773907097.0771
1 | 6 | 19 | 46.9 | 84.733 | 2.5366 | 0.3 | 745375334.7687 | 30000000 | 775375334.7687
1 | 6 | 20 | 46.9 | 84.733 | 2.5366 | 0.3 | 745375334.7687 | 30000000 | 775375334.7687
9 | 7 | 23 | 47 | 81.0345 | 3.0793 | 0.4 | 706914653.5862 | 40000000 | 746914653.5862
9 | 11 | 20 | 47 | 85.8966 | 3.2414 | 0.4 | 749535287.5862 | 40000000 | 789535287.5862
12 | 18 | 14 | 47 | 82.1149 | 2.7552 | 0.5 | 719651854.5517 | 50000000 | 769651854.5517
12 | 18 | 20 | 47 | 82.1149 | 2.5931 | 0.5 | 721121531.5862 | 50000000 | 771121531.5862
1 | 2 | 18 | 47 | 83.1954 | 2.5931 | 0.5 | 730919378.4828 | 50000000 | 780919378.4828
1 | 10 | 20 | 47 | 81.0345 | 2.4851 | 0.4 | 712303469.3793 | 40000000 | 752303469.3793
1 | 5 | 17 | 47 | 82.6552 | 2.431 | 0.3 | 727490132.069 | 30000000 | 757490132.069
1 | 21 | 20 | 47 | 86.4368 | 2.6471 | 0.3 | 759823026.8276 | 30000000 | 789823026.8276
1 | 22 | 17 | 47 | 84.2759 | 2.5931 | 0.2 | 740717225.3793 | 20000000 | 760717225.3793
1 | 22 | 20 | 47 | 84.8161 | 2.5931 | 0.1 | 745616148.8276 | 10000000 | 755616148.8276
12 | 18 | 12 | 47.1 | 82.1952 | 2.7579 | 0.5 | 720355034.4179 | 50000000 | 770355034.4179
1 | 22 | 13 | 47.1 | 84.899 | 2.5956 | 0.2 | 746344698.6958 | 20000000 | 766344698.6958
1 | 22 | 22 | 47.1 | 84.899 | 2.5956 | 0.2 | 746344698.6958 | 20000000 | 766344698.6958
9 | 12 | 23 | 47.2 | 84.9817 | 3.2477 | 0.4 | 741181394.3119 | 40000000 | 781181394.3119
9 | 13 | 9 | 47.2 | 86.0642 | 3.2477 | 0.4 | 750998366.422 | 40000000 | 790998366.422
9 | 8 | 4 | 47.2 | 81.1927 | 3.1394 | 0.3 | 707803689.1376 | 30000000 | 737803689.1376
12 | 18 | 21 | 47.2 | 82.8165 | 2.6523 | 0.5 | 726946784.7523 | 50000000 | 776946784.7523
1 | 24 | 15 | 47.2 | 84.4404 | 2.544 | 0.5 | 742653940.1284 | 50000000 | 792653940.1284
1 | 21 | 21 | 47.2 | 86.6055 | 2.6523 | 0.4 | 761306187.1376 | 40000000 | 801306187.1376
12 | 11 | 18 | 47.2 | 87.1468 | 6.7119 | 0.1 | 729401027.7798 | 10000000 | 739401027.7798
9 | 14 | 19 | 47.3 | 83.9805 | 3.2509 | 0.5 | 732074388.2474 | 50000000 | 782074388.2474
9 | 8 | 2 | 47.3 | 81.2715 | 3.1425 | 0.4 | 708490783.7938 | 40000000 | 748490783.7938
12 | 18 | 18 | 47.3 | 82.3551 | 2.6007 | 0.5 | 723230536.5773 | 50000000 | 773230536.5773
1 | 2 | 19 | 47.3 | 84.5223 | 2.6007 | 0.5 | 742883540.2887 | 50000000 | 792883540.2887
1 | 22 | 14 | 47.3 | 85.0641 | 2.6007 | 0.2 | 747796791.2165 | 20000000 | 767796791.2165
1 | 22 | 21 | 47.3 | 85.0641 | 2.6007 | 0.2 | 747796791.2165 | 20000000 | 767796791.2165
12 | 4 | 4 | 47.3 | 81.2715 | 4.3345 | 0.1 | 697681631.7526 | 10000000 | 707681631.7526
12 | 4 | 5 | 47.3 | 81.2715 | 4.3345 | 0.1 | 697681631.7526 | 10000000 | 707681631.7526
12 | 4 | 3 | 47.3 | 81.2715 | 4.2803 | 0.1 | 698172956.8454 | 10000000 | 708172956.8454
9 | 14 | 20 | 47.4 | 83.5195 | 3.1998 | 0.5 | 728356525.2494 | 50000000 | 778356525.2494
9 | 14 | 21 | 47.4 | 83.5195 | 3.1998 | 0.5 | 728356525.2494 | 50000000 | 778356525.2494
9 | 8 | 5 | 47.4 | 81.3501 | 3.1455 | 0.4 | 709176306.151 | 40000000 | 749176306.151
9 | 10 | 16 | 47.4 | 85.1465 | 3.254 | 0.4 | 742618739.4508 | 40000000 | 782618739.4508
9 | 11 | 21 | 47.4 | 86.2311 | 3.254 | 0.4 | 752454749.2449 | 40000000 | 792454749.2449
9 | 8 | 6 | 47.4 | 81.3501 | 3.1455 | 0.3 | 709176306.151 | 30000000 | 739176306.151
12 | 18 | 15 | 47.4 | 82.4348 | 2.7117 | 0.5 | 722946719.8627 | 50000000 | 772946719.8627
11 | 7 | 18 | 47.4 | 84.6041 | 4.4471 | 0.5 | 726881123.7803 | 50000000 | 776881123.7803
12 | 18 | 23 | 47.4 | 82.9771 | 2.6574 | 0.5 | 728356525.2494 | 50000000 | 778356525.2494
1 | 10 | 17 | 47.4 | 81.8924 | 2.4405 | 0.4 | 720487717.4142 | 40000000 | 760487717.4142
12 | 20 | 8 | 47.4 | 82.9771 | 2.6574 | 0.4 | 728356525.2494 | 40000000 | 768356525.2494
1 | 7 | 15 | 47.4 | 83.5195 | 2.4947 | 0.4 | 734749931.6156 | 40000000 | 774749931.6156
1 | 30 | 16 | 47.4 | 85.1465 | 2.6032 | 0.4 | 748520345.3272 | 40000000 | 788520345.3272
1 | 22 | 16 | 47.4 | 85.1465 | 2.6574 | 0.2 | 748028544.8375 | 20000000 | 768028544.8375
1 | 18 | 23 | 47.4 | 85.6888 | 2.6032 | 0.2 | 753438350.2243 | 20000000 | 773438350.2243
9 | 8 | 3 | 47.5 | 81.4286 | 3.1486 | 0.4 | 709860261.6 | 40000000 | 749860261.6
9 | 9 | 7 | 47.5 | 83.0571 | 3.1486 | 0.4 | 724628505.6 | 40000000 | 764628505.6
1 | 8 | 9 | 47.5 | 84.1429 | 2.5514 | 0.4 | 739889024.4 | 40000000 | 779889024.4
1 | 8 | 7 | 47.5 | 84.1429 | 2.4971 | 0.4 | 740381299.2 | 40000000 | 780381299.2
1 | 30 | 12 | 47.5 | 84.6857 | 2.6057 | 0.4 | 744319497.6 | 40000000 | 784319497.6
1 | 8 | 8 | 47.5 | 84.6857 | 2.5514 | 0.4 | 744811772.4 | 40000000 | 784811772.4
1 | 22 | 12 | 47.5 | 85.2286 | 2.7143 | 0.2 | 748257696 | 20000000 | 768257696
1 | 22 | 15 | 47.5 | 85.2286 | 2.6057 | 0.2 | 749242245.6 | 20000000 | 769242245.6
1 | 18 | 22 | 47.5 | 86.3143 | 2.6057 | 0.2 | 759087741.6 | 20000000 | 779087741.6
9 | 13 | 23 | 47.6 | 84.7671 | 3.2603 | 0.5 | 739122041.0959 | 50000000 | 789122041.0959
9 | 9 | 6 | 47.6 | 83.6804 | 3.1516 | 0.4 | 730252576.6027 | 40000000 | 770252576.6027
9 | 10 | 20 | 47.6 | 86.9406 | 3.2059 | 0.4 | 759324710.2192 | 40000000 | 799324710.2192
1 | 2 | 21 | 47.6 | 84.7671 | 2.6082 | 0.5 | 745035017.4247 | 50000000 | 795035017.4247
1 | 2 | 20 | 47.6 | 85.3105 | 2.6626 | 0.5 | 749469749.6712 | 50000000 | 799469749.6712
1 | 27 | 9 | 47.6 | 86.9406 | 2.6626 | 0.5 | 764252190.4932 | 50000000 | 814252190.4932
1 | 7 | 18 | 47.6 | 84.2237 | 2.5539 | 0.4 | 740600285.1781 | 40000000 | 780600285.1781
6 | 21 | 1 | 47.6 | 83.6804 | 0 | 0.5 | 758831962.1918 | 50000000 | 808831962.1918
9 | 10 | 15 | 47.7 | 85.3922 | 3.209 | 0.4 | 745255685.3295 | 40000000 | 785255685.3295
9 | 13 | 8 | 47.7 | 86.48 | 3.2634 | 0.4 | 754626868.6659 | 40000000 | 794626868.6659
11 | 7 | 20 | 47.7 | 84.8483 | 4.4056 | 0.5 | 729472639.7104 | 50000000 | 779472639.7104
1 | 7 | 19 | 47.7 | 84.3044 | 2.5019 | 0.4 | 741803144.1003 | 40000000 | 781803144.1003
1 | 6 | 18 | 47.7 | 85.3922 | 2.5563 | 0.3 | 751174327.4367 | 30000000 | 781174327.4367
12 | 4 | 2 | 47.7 | 81.5849 | 4.3512 | 0.1 | 700372649.3501 | 10000000 | 710372649.3501
9 | 10 | 21 | 47.8 | 87.1071 | 3.2665 | 0.4 | 760284522.369 | 40000000 | 800284522.369
9 | 11 | 19 | 47.8 | 86.5626 | 3.2665 | 0.4 | 755347609.8861 | 40000000 | 795347609.8861
9 | 12 | 18 | 47.8 | 86.5626 | 3.2665 | 0.4 | 755347609.8861 | 40000000 | 795347609.8861
9 | 13 | 19 | 47.8 | 86.0182 | 3.2665 | 0.4 | 750410697.4032 | 40000000 | 790410697.4032
11 | 7 | 21 | 47.8 | 84.9294 | 4.4098 | 0.5 | 730169356.2232 | 50000000 | 780169356.2232
1 | 27 | 8 | 47.8 | 87.1071 | 2.6132 | 0.5 | 766208817.3485 | 50000000 | 816208817.3485
1 | 8 | 6 | 47.8 | 83.8405 | 2.5043 | 0.4 | 737574724.9476 | 40000000 | 777574724.9476
1 | 8 | 5 | 47.8 | 83.8405 | 2.4499 | 0.4 | 738068416.1959 | 40000000 | 778068416.1959
1 | 30 | 2 | 47.8 | 84.9294 | 2.6132 | 0.4 | 746461167.4169 | 40000000 | 786461167.4169
12 | 11 | 19 | 47.8 | 88.1959 | 6.7508 | 0.1 | 738562107.4442 | 10000000 | 748562107.4442
12 | 11 | 22 | 47.8 | 88.1959 | 6.7508 | 0.1 | 738562107.4442 | 10000000 | 748562107.4442
9 | 10 | 9 | 47.9 | 85.5552 | 3.1606 | 0.4 | 747171808.7099 | 40000000 | 787171808.7099
9 | 13 | 7 | 47.9 | 86.1001 | 3.2696 | 0.4 | 751125098.7031 | 40000000 | 791125098.7031
1 | 8 | 4 | 47.9 | 83.9204 | 2.5067 | 0.4 | 738276906.2253 | 40000000 | 778276906.2253
1 | 31 | 12 | 47.9 | 85.5552 | 2.6702 | 0.4 | 751619259.9522 | 40000000 | 791619259.9522
1 | 31 | 14 | 47.9 | 85.0102 | 2.6157 | 0.3 | 747171808.7099 | 30000000 | 777171808.7099
1 | 22 | 10 | 47.9 | 85.5552 | 2.6702 | 0.3 | 751619259.9522 | 30000000 | 781619259.9522
12 | 11 | 21 | 47.9 | 87.7349 | 6.7572 | 0.1 | 734323616.2321 | 10000000 | 744323616.2321
12 | 11 | 20 | 47.9 | 88.2799 | 6.8117 | 0.1 | 738771067.4744 | 10000000 | 748771067.4744
7 | 21 | 4 | 47.9 | 77.9261 | 0 | 0.5 | 706650586.2799 | 50000000 | 756650586.2799
9 | 10 | 22 | 48 | 86.1818 | 3.2727 | 0.4 | 751837876.3636 | 40000000 | 791837876.3636
12 | 18 | 17 | 48 | 82.9091 | 2.6182 | 0.5 | 728095627.6364 | 50000000 | 778095627.6364
1 | 7 | 20 | 48 | 84.5455 | 2.5091 | 0.4 | 743923793.4545 | 40000000 | 783923793.4545
1 | 27 | 11 | 48 | 87.2727 | 2.6727 | 0.4 | 767171412 | 40000000 | 807171412
1 | 27 | 7 | 48 | 87.2727 | 2.6182 | 0.4 | 767666042.1818 | 40000000 | 807666042.1818
9 | 9 | 14 | 48.1 | 83.5335 | 3.1666 | 0.5 | 728784329.5165 | 50000000 | 778784329.5165
9 | 13 | 22 | 48.1 | 85.1714 | 3.2758 | 0.5 | 742647074.9149 | 50000000 | 792647074.9149
11 | 6 | 18 | 48.1 | 85.7174 | 4.4224 | 0.5 | 737200996.3655 | 50000000 | 787200996.3655
1 | 30 | 17 | 48.1 | 85.1714 | 2.6207 | 0.4 | 748588251.5142 | 40000000 | 788588251.5142
1 | 30 | 22 | 48.1 | 85.7174 | 2.6207 | 0.4 | 753539232.0136 | 40000000 | 793539232.0136
1 | 31 | 11 | 48.1 | 86.2633 | 2.6753 | 0.4 | 757995114.4631 | 40000000 | 797995114.4631
1 | 21 | 10 | 48.1 | 87.3553 | 2.6753 | 0.4 | 767897075.462 | 40000000 | 807897075.462
1 | 27 | 10 | 48.1 | 87.3553 | 2.6753 | 0.4 | 767897075.462 | 40000000 | 807897075.462
1 | 31 | 13 | 48.1 | 84.6254 | 2.6207 | 0.3 | 743637271.0148 | 30000000 | 773637271.0148
7 | 21 | 1 | 48.1 | 78.0738 | 0 | 0.5 | 707990211.4188 | 50000000 | 757990211.4188
7 | 21 | 3 | 48.1 | 78.0738 | 0 | 0.5 | 707990211.4188 | 50000000 | 757990211.4188
9 | 10 | 10 | 48.2 | 86.3447 | 3.1696 | 0.4 | 754249712.5714 | 40000000 | 794249712.5714
9 | 10 | 12 | 48.2 | 86.3447 | 3.1696 | 0.4 | 754249712.5714 | 40000000 | 794249712.5714
9 | 11 | 18 | 48.2 | 86.8912 | 3.2789 | 0.4 | 758214231.4286 | 40000000 | 798214231.4286
9 | 11 | 22 | 48.2 | 86.8912 | 3.2789 | 0.4 | 758214231.4286 | 40000000 | 798214231.4286
9 | 12 | 24 | 48.2 | 85.7982 | 3.2789 | 0.4 | 748302934.2857 | 40000000 | 788302934.2857
12 | 18 | 16 | 48.2 | 83.0658 | 2.6778 | 0.5 | 728975904.8571 | 50000000 | 778975904.8571
11 | 6 | 19 | 48.2 | 85.7982 | 4.4265 | 0.5 | 737896072.2857 | 50000000 | 787896072.2857
1 | 7 | 17 | 48.2 | 84.7052 | 2.5138 | 0.4 | 745329545.1429 | 40000000 | 785329545.1429
1 | 31 | 15 | 48.2 | 85.2517 | 2.6231 | 0.4 | 749294064 | 40000000 | 789294064
1 | 18 | 24 | 48.2 | 85.7982 | 2.6231 | 0.3 | 754249712.5714 | 30000000 | 784249712.5714
6 | 21 | 2 | 48.2 | 84.1587 | 0 | 0.5 | 763169880 | 50000000 | 813169880
7 | 21 | 2 | 48.2 | 78.1474 | 0 | 0.5 | 708657745.7143 | 50000000 | 758657745.7143
7 | 22 | 2 | 48.2 | 76.5079 | 0 | 0.5 | 693790800 | 50000000 | 743790800
9 | 12 | 19 | 48.3 | 86.9728 | 3.282 | 0.4 | 758926828.7429 | 40000000 | 798926828.7429
1 | 20 | 24 | 48.3 | 87.5198 | 2.735 | 0.5 | 768847440.8834 | 50000000 | 818847440.8834
1 | 7 | 16 | 48.3 | 84.2378 | 2.5162 | 0.4 | 741069726.8901 | 40000000 | 781069726.8901
1 | 7 | 22 | 48.3 | 84.7848 | 2.5709 | 0.4 | 745534002.3533 | 40000000 | 785534002.3533
1 | 31 | 16 | 48.3 | 85.3318 | 2.6256 | 0.4 | 749998277.8165 | 40000000 | 789998277.8165
1 | 30 | 13 | 48.3 | 85.8788 | 2.6256 | 0.4 | 754958583.8867 | 40000000 | 794958583.8867
1 | 21 | 11 | 48.3 | 87.5198 | 2.6803 | 0.3 | 769343471.4904 | 30000000 | 799343471.4904
9 | 13 | 6 | 48.4 | 86.5068 | 3.2851 | 0.4 | 754672860.8145 | 40000000 | 794672860.8145
12 | 18 | 4 | 48.4 | 83.7692 | 2.7923 | 0.5 | 734316553.3846 | 50000000 | 784316553.3846
1 | 17 | 24 | 48.4 | 85.4118 | 2.5733 | 0.5 | 751197393.6923 | 50000000 | 801197393.6923
1 | 3 | 12 | 48.4 | 87.6018 | 2.6828 | 0.5 | 770064215.2127 | 50000000 | 820064215.2127
1 | 10 | 21 | 48.4 | 82.1267 | 2.4638 | 0.4 | 722400666.1086 | 40000000 | 762400666.1086
12 | 1 | 12 | 48.4 | 85.9593 | 0 | 0.2 | 779497625.9729 | 20000000 | 799497625.9729
9 | 10 | 11 | 48.5 | 86.5876 | 3.1785 | 0.4 | 756371520.6102 | 40000000 | 796371520.6102
9 | 12 | 12 | 48.5 | 87.1356 | 3.2333 | 0.4 | 760844151.1525 | 40000000 | 800844151.1525
9 | 12 | 13 | 48.5 | 87.1356 | 3.2881 | 0.4 | 760347192.2034 | 40000000 | 800347192.2034
9 | 13 | 1 | 48.5 | 86.5876 | 3.2881 | 0.4 | 755377602.7119 | 40000000 | 795377602.7119
10 | 14 | 11 | 48.5 | 87.6836 | 4.1102 | 0.1 | 757862397.4576 | 10000000 | 767862397.4576
12 | 18 | 8 | 48.5 | 83.2994 | 2.7949 | 0.5 | 730032696.3051 | 50000000 | 780032696.3051
1 | 3 | 14 | 48.5 | 87.1356 | 2.6305 | 0.5 | 766310699.5932 | 50000000 | 816310699.5932
1 | 3 | 13 | 48.5 | 87.6836 | 2.6305 | 0.5 | 771280289.0847 | 50000000 | 821280289.0847
1 | 8 | 3 | 48.5 | 83.8475 | 2.5209 | 0.4 | 737487080.5424 | 40000000 | 777487080.5424
1 | 7 | 21 | 48.5 | 84.9435 | 2.5757 | 0.4 | 746929300.5763 | 40000000 | 786929300.5763
1 | 21 | 17 | 48.5 | 87.1356 | 2.6853 | 0.4 | 765813740.6441 | 40000000 | 805813740.6441
1 | 27 | 13 | 48.5 | 87.6836 | 2.7401 | 0.4 | 770286371.1864 | 40000000 | 810286371.1864
1 | 21 | 9 | 48.5 | 87.6836 | 2.6853 | 0.3 | 770783330.1356 | 30000000 | 800783330.1356
6 | 21 | 6 | 48.5 | 86.0395 | 0 | 0.5 | 780225550.1695 | 50000000 | 830225550.1695
7 | 11 | 12 | 48.5 | 74.5311 | 0 | 0.2 | 675864170.8475 | 20000000 | 695864170.8475
9 | 10 | 17 | 48.6 | 87.2167 | 3.2363 | 0.4 | 761552390.8036 | 40000000 | 801552390.8036
9 | 11 | 23 | 48.6 | 87.7652 | 3.2912 | 0.4 | 766029184.7404 | 40000000 | 806029184.7404
9 | 12 | 17 | 48.6 | 87.2167 | 3.2912 | 0.4 | 761054969.2551 | 40000000 | 801054969.2551
12 | 18 | 3 | 48.6 | 83.9255 | 2.7975 | 0.5 | 735686470.2799 | 50000000 | 785686470.2799
12 | 18 | 6 | 48.6 | 83.9255 | 2.7975 | 0.5 | 735686470.2799 | 50000000 | 785686470.2799
1 | 3 | 10 | 48.6 | 87.2167 | 2.6878 | 0.5 | 766526606.2889 | 50000000 | 816526606.2889
1 | 21 | 14 | 48.6 | 87.7652 | 2.6878 | 0.4 | 771500821.7743 | 40000000 | 811500821.7743
12 | 1 | 18 | 48.6 | 86.6682 | 0 | 0.2 | 785926046.6817 | 20000000 | 805926046.6817
6 | 21 | 4 | 48.6 | 86.1196 | 0 | 0.5 | 780951831.1964 | 50000000 | 830951831.1964
9 | 10 | 23 | 48.7 | 86.7486 | 3.2943 | 0.4 | 756782319.3687 | 40000000 | 796782319.3687
9 | 11 | 17 | 48.7 | 87.2976 | 3.2943 | 0.4 | 761761150.4171 | 40000000 | 801761150.4171
9 | 13 | 5 | 48.7 | 87.2976 | 3.2393 | 0.4 | 762259033.522 | 40000000 | 802259033.522
1 | 7 | 14 | 48.7 | 82.9053 | 2.4707 | 0.4 | 729398748.602 | 40000000 | 769398748.602
1 | 21 | 12 | 48.7 | 87.8467 | 2.7452 | 0.4 | 771718812.5141 | 40000000 | 811718812.5141
1 | 22 | 2 | 48.7 | 86.1995 | 2.6354 | 0.2 | 757778085.5784 | 20000000 | 777778085.5784
12 | 11 | 24 | 48.7 | 83.4543 | 2.7452 | 0.1 | 731888164.1263 | 10000000 | 741888164.1263
12 | 11 | 17 | 48.7 | 88.9448 | 6.8081 | 0.1 | 744833124.8523 | 10000000 | 754833124.8523
9 | 8 | 24 | 48.8 | 84.0811 | 3.2423 | 0.4 | 733063467.4054 | 40000000 | 773063467.4054
9 | 9 | 5 | 48.8 | 84.6306 | 3.1874 | 0.4 | 738545247.2432 | 40000000 | 778545247.2432
9 | 9 | 23 | 48.8 | 85.7297 | 3.1874 | 0.4 | 748512119.6757 | 40000000 | 788512119.6757
12 | 18 | 5 | 48.8 | 83.5315 | 2.8027 | 0.5 | 732066780.1622 | 50000000 | 782066780.1622
12 | 18 | 2 | 48.8 | 83.5315 | 2.7477 | 0.5 | 732565123.7838 | 50000000 | 782565123.7838
11 | 6 | 17 | 48.8 | 85.7297 | 4.4514 | 0.5 | 737050216.3784 | 50000000 | 787050216.3784
12 | 18 | 24 | 48.8 | 84.0811 | 2.6928 | 0.5 | 738046903.6216 | 50000000 | 788046903.6216
1 | 8 | 2 | 48.8 | 83.5315 | 2.5279 | 0.4 | 734558498.2703 | 40000000 | 774558498.2703
1 | 18 | 6 | 48.8 | 85.7297 | 2.5829 | 0.4 | 753993899.5135 | 40000000 | 793993899.5135
1 | 12 | 9 | 48.8 | 90.1261 | 6.5396 | 0.4 | 757980648.4865 | 40000000 | 797980648.4865
1 | 31 | 10 | 48.8 | 86.2793 | 2.6928 | 0.4 | 757980648.4865 | 40000000 | 797980648.4865
1 | 21 | 15 | 48.8 | 87.9279 | 2.7477 | 0.4 | 772432613.5135 | 40000000 | 812432613.5135
1 | 27 | 14 | 48.8 | 87.9279 | 2.6928 | 0.4 | 772930957.1351 | 40000000 | 812930957.1351
12 | 1 | 13 | 48.8 | 86.2793 | 0 | 0.3 | 782399485.9459 | 30000000 | 812399485.9459
1 | 22 | 7 | 48.8 | 85.7297 | 2.6378 | 0.2 | 753495555.8919 | 20000000 | 773495555.8919
6 | 21 | 3 | 48.8 | 85.7297 | 0 | 0.5 | 777416049.7297 | 50000000 | 827416049.7297
7 | 11 | 5 | 48.8 | 74.7387 | 0 | 0.2 | 677747325.4054 | 20000000 | 697747325.4054
9 | 10 | 19 | 48.9 | 87.4589 | 3.3003 | 0.4 | 763168746.6142 | 40000000 | 803168746.6142
1 | 2 | 17 | 48.9 | 85.2587 | 2.6403 | 0.5 | 749202259.748 | 50000000 | 799202259.748
1 | 4 | 20 | 48.9 | 85.2587 | 2.5853 | 0.5 | 749701062.8504 | 50000000 | 799701062.8504
1 | 2 | 22 | 48.9 | 85.8088 | 2.6403 | 0.5 | 754190290.7717 | 50000000 | 804190290.7717
1 | 27 | 16 | 48.9 | 86.9089 | 2.6953 | 0.5 | 763667549.7165 | 50000000 | 813667549.7165
1 | 3 | 18 | 48.9 | 86.9089 | 2.6403 | 0.5 | 764166352.8189 | 50000000 | 814166352.8189
11 | 6 | 20 | 48.9 | 86.3588 | 4.4555 | 0.4 | 742717819.4173 | 40000000 | 782717819.4173
1 | 19 | 23 | 48.9 | 87.4589 | 2.6403 | 0.4 | 769154383.8425 | 40000000 | 809154383.8425
1 | 27 | 12 | 48.9 | 88.009 | 2.6953 | 0.4 | 773643611.7638 | 40000000 | 813643611.7638
12 | 12 | 3 | 48.9 | 84.1586 | 2.8053 | 0.1 | 737729788.3937 | 10000000 | 747729788.3937
6 | 21 | 5 | 48.9 | 86.3588 | 0 | 0.5 | 783120870.7087 | 50000000 | 833120870.7087
7 | 11 | 11 | 48.9 | 74.8076 | 0 | 0.2 | 678372219.2126 | 20000000 | 698372219.2126
9 | 8 | 23 | 49 | 84.236 | 3.1933 | 0.4 | 734913002.427 | 40000000 | 774913002.427
10 | 14 | 21 | 49 | 87.5393 | 4.0191 | 0.1 | 757379772.2022 | 10000000 | 767379772.2022
11 | 7 | 17 | 49 | 85.8876 | 4.4596 | 0.5 | 738407833.2809 | 50000000 | 788407833.2809
1 | 4 | 21 | 49 | 85.8876 | 2.6427 | 0.5 | 754883464.4494 | 50000000 | 804883464.4494
1 | 27 | 15 | 49 | 86.9888 | 2.6978 | 0.5 | 764369433.9101 | 50000000 | 814369433.9101
1 | 19 | 24 | 49 | 87.5393 | 2.6978 | 0.5 | 769362049.4157 | 50000000 | 819362049.4157
1 | 3 | 15 | 49 | 87.5393 | 2.6427 | 0.5 | 769861310.9663 | 50000000 | 819861310.9663
1 | 21 | 13 | 49 | 88.0899 | 2.6978 | 0.4 | 774354664.9213 | 40000000 | 814354664.9213
1 | 21 | 16 | 49 | 88.0899 | 2.6978 | 0.4 | 774354664.9213 | 40000000 | 814354664.9213
12 | 1 | 14 | 49 | 86.4382 | 0 | 0.3 | 783840634.382 | 30000000 | 813840634.382
12 | 1 | 17 | 49 | 86.9888 | 0 | 0.2 | 788833249.8876 | 20000000 | 808833249.8876
12 | 1 | 20 | 49 | 86.9888 | 0 | 0.2 | 788833249.8876 | 20000000 | 808833249.8876
7 | 11 | 4 | 49 | 75.427 | 0 | 0.2 | 683988324.2697 | 20000000 | 703988324.2697
7 | 11 | 13 | 49 | 74.8764 | 0 | 0.2 | 678995708.764 | 20000000 | 698995708.764
9 | 10 | 8 | 49.1 | 85.4153 | 3.1962 | 0.4 | 745580702.7879 | 40000000 | 785580702.7879
10 | 14 | 22 | 49.1 | 87.6195 | 3.9677 | 0.1 | 758573396 | 10000000 | 768573396
1 | 29 | 4 | 49.1 | 85.9663 | 2.7553 | 0.5 | 754575644.2424 | 50000000 | 804575644.2424
1 | 3 | 17 | 49.1 | 87.6195 | 2.6451 | 0.5 | 770566651.2727 | 50000000 | 820566651.2727
1 | 7 | 13 | 49.1 | 84.8642 | 2.5349 | 0.4 | 746580140.7273 | 40000000 | 786580140.7273
1 | 18 | 3 | 49.1 | 86.5174 | 2.59 | 0.4 | 761071990.8485 | 40000000 | 801071990.8485
1 | 19 | 1 | 49.1 | 86.5174 | 2.6451 | 0.3 | 760572271.8788 | 30000000 | 790572271.8788
1 | 22 | 4 | 49.1 | 85.9663 | 2.59 | 0.2 | 756074801.1515 | 20000000 | 776074801.1515
12 | 11 | 16 | 49.1 | 88.7217 | 6.7781 | 0.1 | 743082107.9394 | 10000000 | 753082107.9394
7 | 11 | 15 | 49.1 | 74.3939 | 0 | 0.3 | 674620609.0909 | 30000000 | 704620609.0909
7 | 11 | 16 | 49.1 | 74.3939 | 0 | 0.3 | 674620609.0909 | 30000000 | 704620609.0909
7 | 11 | 3 | 49.1 | 75.4961 | 0 | 0.2 | 684614988.4848 | 20000000 | 704614988.4848
9 | 8 | 22 | 49.2 | 84.9417 | 3.2543 | 0.4 | 740759712.9417 | 40000000 | 780759712.9417
9 | 12 | 15 | 49.2 | 87.6996 | 3.2543 | 0.4 | 765768481.1031 | 40000000 | 805768481.1031
9 | 12 | 16 | 49.2 | 87.6996 | 3.3094 | 0.4 | 765268305.7399 | 40000000 | 805268305.7399
11 | 6 | 21 | 49.2 | 86.5964 | 4.5229 | 0.5 | 744260940.4843 | 50000000 | 794260940.4843
1 | 3 | 16 | 49.2 | 87.6996 | 2.6475 | 0.5 | 771270410.0987 | 50000000 | 821270410.0987
1 | 3 | 11 | 49.2 | 88.2511 | 2.7027 | 0.5 | 775771988.3677 | 50000000 | 825771988.3677
1 | 21 | 7 | 49.2 | 88.8027 | 2.7578 | 0.5 | 780273566.6368 | 50000000 | 830273566.6368
12 | 2 | 21 | 49.2 | 84.9417 | 4.4677 | 0.4 | 729755854.9507 | 40000000 | 769755854.9507
1 | 18 | 2 | 49.2 | 86.5964 | 2.6475 | 0.4 | 761266902.8341 | 40000000 | 801266902.8341
1 | 31 | 8 | 49.2 | 86.5964 | 2.6475 | 0.4 | 761266902.8341 | 40000000 | 801266902.8341
1 | 27 | 6 | 49.2 | 88.2511 | 2.6475 | 0.4 | 776272163.7309 | 40000000 | 816272163.7309
1 | 21 | 8 | 49.2 | 88.8027 | 2.7578 | 0.4 | 780273566.6368 | 40000000 | 820273566.6368
1 | 22 | 6 | 49.2 | 86.0448 | 2.6475 | 0.3 | 756265149.2018 | 30000000 | 786265149.2018
1 | 19 | 6 | 49.2 | 86.5964 | 2.6475 | 0.3 | 761266902.8341 | 30000000 | 791266902.8341
1 | 22 | 5 | 49.2 | 86.0448 | 2.6475 | 0.2 | 756265149.2018 | 20000000 | 776265149.2018
9 | 10 | 7 | 49.3 | 86.6753 | 3.1468 | 0.4 | 757454301.4535 | 40000000 | 797454301.4535
9 | 11 | 16 | 49.3 | 87.7794 | 3.3124 | 0.4 | 765965023.9418 | 40000000 | 805965023.9418
9 | 7 | 20 | 49.3 | 87.2273 | 3.3124 | 0.3 | 760958716.5957 | 30000000 | 790958716.5957
1 | 2 | 16 | 49.3 | 84.467 | 2.6499 | 0.5 | 741934748.6809 | 50000000 | 791934748.6809
1 | 30 | 23 | 49.3 | 86.6753 | 2.6499 | 0.4 | 761959978.0649 | 40000000 | 801959978.0649
1 | 20 | 12 | 49.3 | 89.9877 | 2.8708 | 0.4 | 789995299.2027 | 40000000 | 829995299.2027
1 | 6 | 21 | 49.3 | 86.6753 | 2.5395 | 0.3 | 762961239.5342 | 30000000 | 792961239.5342
1 | 22 | 8 | 49.3 | 86.1232 | 2.6499 | 0.2 | 756953670.7189 | 20000000 | 776953670.7189
1 | 22 | 9 | 49.3 | 86.6753 | 2.7052 | 0.2 | 761459347.3303 | 20000000 | 781459347.3303
12 | 1 | 21 | 49.3 | 87.7794 | 0 | 0.2 | 796002868.0179 | 20000000 | 816002868.0179
12 | 12 | 1 | 49.3 | 84.467 | 2.7604 | 0.1 | 740933487.2116 | 10000000 | 750933487.2116
7 | 11 | 14 | 49.3 | 74.5297 | 0 | 0.3 | 675851491.7133 | 30000000 | 705851491.7133
7 | 11 | 1 | 49.3 | 75.6338 | 0 | 0.2 | 685864106.4054 | 20000000 | 705864106.4054
9 | 9 | 24 | 49.4 | 86.2013 | 3.1497 | 0.4 | 753130886.1342 | 40000000 | 793130886.1342
9 | 12 | 14 | 49.4 | 87.8591 | 3.2602 | 0.4 | 767161268.5772 | 40000000 | 807161268.5772
12 | 20 | 7 | 49.4 | 84.5436 | 2.5971 | 0.5 | 743109184.3893 | 50000000 | 793109184.3893
12 | 19 | 1 | 49.4 | 85.0962 | 2.7076 | 0.5 | 747117865.0872 | 50000000 | 797117865.0872
12 | 2 | 20 | 49.4 | 85.6488 | 4.5311 | 0.4 | 735592908.0805 | 40000000 | 775592908.0805
1 | 7 | 11 | 49.4 | 85.0962 | 2.5418 | 0.4 | 748621120.349 | 40000000 | 788621120.349
1 | 8 | 19 | 49.4 | 87.3065 | 2.6523 | 0.4 | 767662353.6644 | 40000000 | 807662353.6644
1 | 20 | 8 | 49.4 | 89.5168 | 2.7629 | 0.4 | 786703586.9799 | 40000000 | 826703586.9799
1 | 19 | 3 | 49.4 | 86.7539 | 2.6523 | 0.3 | 762651502.7919 | 30000000 | 792651502.7919
1 | 5 | 18 | 49.4 | 87.3065 | 2.5971 | 0.3 | 768163438.7517 | 30000000 | 798163438.7517
1 | 6 | 9 | 49.4 | 87.8591 | 2.7076 | 0.3 | 772172119.4497 | 30000000 | 802172119.4497
12 | 1 | 19 | 49.4 | 87.3065 | 0 | 0.2 | 791714437.8523 | 20000000 | 811714437.8523
12 | 12 | 2 | 49.4 | 84.5436 | 2.8181 | 0.1 | 741104844.0403 | 10000000 | 751104844.0403
12 | 11 | 14 | 49.4 | 88.9642 | 6.7966 | 0.1 | 745113524.7383 | 10000000 | 755113524.7383
6 | 11 | 3 | 49.4 | 85.6488 | 3.3707 | 0.5 | 746115694.9128 | 50000000 | 796115694.9128
10 | 13 | 9 | 49.5 | 87.3855 | 4.2587 | 0.5 | 753812252.1453 | 50000000 | 803812252.1453
9 | 9 | 2 | 49.5 | 85.1732 | 3.1525 | 0.4 | 743781483.6536 | 40000000 | 783781483.6536
9 | 12 | 10 | 49.5 | 87.9385 | 3.3184 | 0.4 | 767353789.6089 | 40000000 | 807353789.6089
9 | 13 | 2 | 49.5 | 87.9385 | 3.3184 | 0.4 | 767353789.6089 | 40000000 | 807353789.6089
12 | 19 | 2 | 49.5 | 85.1732 | 2.7101 | 0.5 | 747793791.0503 | 50000000 | 797793791.0503
12 | 19 | 9 | 49.5 | 85.1732 | 2.7101 | 0.5 | 747793791.0503 | 50000000 | 797793791.0503
11 | 7 | 22 | 49.5 | 87.3855 | 4.5352 | 0.5 | 751304560.0223 | 50000000 | 801304560.0223
1 | 4 | 22 | 49.5 | 86.2793 | 2.5994 | 0.5 | 758827636.3911 | 50000000 | 808827636.3911
1 | 3 | 19 | 49.5 | 86.8324 | 2.5994 | 0.5 | 763843020.6369 | 50000000 | 813843020.6369
1 | 18 | 1 | 49.5 | 86.2793 | 2.5994 | 0.4 | 758827636.3911 | 40000000 | 798827636.3911
1 | 18 | 5 | 49.5 | 86.8324 | 2.5994 | 0.4 | 763843020.6369 | 40000000 | 803843020.6369
1 | 19 | 2 | 49.5 | 86.8324 | 2.6547 | 0.3 | 763341482.2123 | 30000000 | 793341482.2123
1 | 19 | 4 | 49.5 | 86.8324 | 2.6547 | 0.3 | 763341482.2123 | 30000000 | 793341482.2123
12 | 1 | 15 | 49.5 | 87.3855 | 0 | 0.3 | 792430710.838 | 30000000 | 822430710.838
1 | 22 | 1 | 49.5 | 87.9385 | 2.7101 | 0.2 | 772870712.2793 | 20000000 | 792870712.2793
12 | 11 | 15 | 49.5 | 89.0447 | 6.9134 | 0.1 | 744784560.5028 | 10000000 | 754784560.5028
9 | 9 | 4 | 49.6 | 84.6964 | 3.2107 | 0.4 | 738930384 | 40000000 | 778930384
9 | 9 | 22 | 49.6 | 86.3571 | 3.2107 | 0.4 | 753990106.5 | 40000000 | 793990106.5
9 | 10 | 18 | 49.6 | 88.5714 | 3.3214 | 0.4 | 773065755 | 40000000 | 813065755
9 | 11 | 15 | 49.6 | 88.0179 | 3.3214 | 0.4 | 768045847.5 | 40000000 | 808045847.5
9 | 13 | 4 | 49.6 | 87.4643 | 3.2661 | 0.4 | 763527930.75 | 40000000 | 803527930.75
11 | 7 | 16 | 49.6 | 86.3571 | 4.4839 | 0.5 | 742444319.25 | 50000000 | 792444319.25
12 | 19 | 6 | 49.6 | 85.25 | 2.7125 | 0.5 | 748468208.25 | 50000000 | 798468208.25
12 | 19 | 10 | 49.6 | 85.8036 | 2.7679 | 0.5 | 752986125 | 50000000 | 802986125
1 | 10 | 22 | 49.6 | 83.5893 | 2.5464 | 0.4 | 734914458 | 40000000 | 774914458
1 | 10 | 11 | 49.6 | 83.5893 | 2.4911 | 0.4 | 735416448.75 | 40000000 | 775416448.75
1 | 8 | 10 | 49.6 | 86.9107 | 2.6018 | 0.4 | 764531912.25 | 40000000 | 804531912.25
1 | 18 | 4 | 49.6 | 86.9107 | 2.6018 | 0.4 | 764531912.25 | 40000000 | 804531912.25
1 | 8 | 18 | 49.6 | 87.4643 | 2.6571 | 0.4 | 769049829 | 40000000 | 809049829
1 | 8 | 20 | 49.6 | 88.0179 | 2.6571 | 0.4 | 774069736.5 | 40000000 | 814069736.5
1 | 19 | 5 | 49.6 | 86.9107 | 2.6571 | 0.3 | 764029921.5 | 30000000 | 794029921.5
1 | 20 | 14 | 49.6 | 90.2321 | 2.8232 | 0.3 | 792643394.25 | 30000000 | 822643394.25
12 | 1 | 16 | 49.6 | 87.4643 | 0 | 0.3 | 793145385 | 30000000 | 823145385
12 | 12 | 4 | 49.6 | 84.6964 | 2.8232 | 0.1 | 742444319.25 | 10000000 | 752444319.25
9 | 14 | 24 | 49.7 | 86.9889 | 3.3244 | 0.5 | 758687521.0033 | 50000000 | 808687521.0033
10 | 14 | 10 | 49.7 | 89.2051 | 4.1555 | 0.2 | 771248572.6756 | 20000000 | 791248572.6756
10 | 14 | 19 | 49.7 | 87.5429 | 4.0447 | 0.2 | 757180194.8027 | 20000000 | 777180194.8027
12 | 19 | 3 | 49.7 | 84.7726 | 2.7149 | 0.5 | 744116701.0635 | 50000000 | 794116701.0635
12 | 19 | 12 | 49.7 | 85.3266 | 2.7703 | 0.5 | 748638679.6656 | 50000000 | 798638679.6656
1 | 3 | 9 | 49.7 | 88.097 | 2.7149 | 0.5 | 774263225.0769 | 50000000 | 824263225.0769
12 | 19 | 4 | 49.7 | 85.3266 | 2.7149 | 0.4 | 749141121.7324 | 40000000 | 789141121.7324
1 | 27 | 5 | 49.7 | 88.6511 | 2.6595 | 0.4 | 779790087.8127 | 40000000 | 819790087.8127
1 | 20 | 7 | 49.7 | 89.7592 | 2.7703 | 0.4 | 788834045.0167 | 40000000 | 828834045.0167
12 | 11 | 12 | 49.7 | 89.7592 | 6.9259 | 0.1 | 751150890 | 10000000 | 761150890
12 | 11 | 13 | 49.7 | 89.7592 | 6.8705 | 0.1 | 751653332.0669 | 10000000 | 761653332.0669
6 | 11 | 2 | 49.7 | 85.3266 | 3.3798 | 0.5 | 743111816.9298 | 50000000 | 793111816.9298
7 | 14 | 23 | 49.7 | 79.2319 | 0 | 0.5 | 718492155.6522 | 50000000 | 768492155.6522
7 | 11 | 10 | 49.7 | 74.7993 | 0 | 0.2 | 678296790.301 | 20000000 | 698296790.301
9 | 9 | 1 | 49.8 | 84.8486 | 3.2165 | 0.4 | 740257581.3274 | 40000000 | 780257581.3274
9 | 9 | 3 | 49.8 | 84.8486 | 3.2165 | 0.4 | 740257581.3274 | 40000000 | 780257581.3274
1 | 1 | 15 | 49.8 | 84.294 | 2.6065 | 0.5 | 740760473.706 | 50000000 | 790760473.706
12 | 19 | 13 | 49.8 | 84.8486 | 2.7174 | 0.5 | 744783612.735 | 50000000 | 794783612.735
1 | 2 | 15 | 49.8 | 84.8486 | 2.6619 | 0.5 | 745286505.1136 | 50000000 | 795286505.1136
12 | 19 | 11 | 49.8 | 85.9577 | 2.7728 | 0.5 | 754338567.9287 | 50000000 | 804338567.9287
12 | 19 | 8 | 49.8 | 85.9577 | 2.7174 | 0.5 | 754841460.3074 | 50000000 | 804841460.3074
12 | 2 | 22 | 49.8 | 85.4031 | 4.5474 | 0.4 | 733217088.0267 | 40000000 | 773217088.0267
1 | 5 | 20 | 49.8 | 88.1759 | 2.6065 | 0.3 | 775962940.2094 | 30000000 | 805962940.2094
1 | 20 | 13 | 49.8 | 90.3942 | 2.8283 | 0.3 | 794067065.8396 | 30000000 | 824067065.8396
12 | 1 | 22 | 49.8 | 87.6214 | 0 | 0.2 | 794569958.2183 | 20000000 | 814569958.2183
6 | 11 | 4 | 49.8 | 85.9577 | 3.4383 | 0.5 | 748303859.3853 | 50000000 | 798303859.3853
7 | 15 | 4 | 49.8 | 80.412 | 0 | 0.5 | 729193948.9978 | 50000000 | 779193948.9978
7 | 15 | 5 | 49.8 | 80.412 | 0 | 0.5 | 729193948.9978 | 50000000 | 779193948.9978
7 | 11 | 2 | 49.8 | 75.9755 | 0 | 0.2 | 688962558.7082 | 20000000 | 708962558.7082
9 | 12 | 11 | 49.9 | 88.2547 | 3.2749 | 0.4 | 770616125.1591 | 40000000 | 810616125.1591
12 | 19 | 5 | 49.9 | 85.4794 | 2.7198 | 0.5 | 750482457.6174 | 50000000 | 800482457.6174
1 | 2 | 14 | 49.9 | 85.4794 | 2.6643 | 0.5 | 750985799.3059 | 50000000 | 800985799.3059
12 | 19 | 7 | 49.9 | 86.0345 | 2.7198 | 0.5 | 755515874.5028 | 50000000 | 805515874.5028
1 | 10 | 9 | 49.9 | 83.8142 | 2.5533 | 0.4 | 736892232.0267 | 40000000 | 776892232.0267
1 | 8 | 21 | 49.9 | 88.2547 | 2.6643 | 0.4 | 776152883.733 | 40000000 | 816152883.733
1 | 8 | 23 | 49.9 | 88.2547 | 2.6643 | 0.4 | 776152883.733 | 40000000 | 816152883.733
1 | 27 | 1 | 49.9 | 88.2547 | 2.6643 | 0.4 | 776152883.733 | 40000000 | 816152883.733
1 | 26 | 23 | 49.9 | 88.2547 | 2.6088 | 0.4 | 776656225.4216 | 40000000 | 816656225.4216
1 | 27 | 3 | 49.9 | 88.8098 | 2.6643 | 0.4 | 781186300.6185 | 40000000 | 821186300.6185
1 | 20 | 15 | 49.9 | 89.9199 | 2.7753 | 0.4 | 790246451.0122 | 40000000 | 830246451.0122
1 | 6 | 22 | 49.9 | 87.1446 | 2.6088 | 0.3 | 766589391.6507 | 30000000 | 796589391.6507
1 | 5 | 21 | 49.9 | 88.2547 | 2.6643 | 0.3 | 776152883.733 | 30000000 | 806152883.733
9 | 11 | 4 | 50 | 87.7778 | 3.2778 | 0.4 | 766264590 | 40000000 | 806264590
9 | 12 | 9 | 50 | 88.8889 | 3.3333 | 0.4 | 775836600 | 40000000 | 815836600
1 | 3 | 21 | 50 | 87.2222 | 2.6111 | 0.5 | 767272170 | 50000000 | 817272170
1 | 10 | 14 | 50 | 82.7778 | 2.5 | 0.4 | 727976550 | 40000000 | 767976550
1 | 7 | 12 | 50 | 85.5556 | 2.5556 | 0.4 | 752662260 | 40000000 | 792662260
1 | 20 | 3 | 50 | 88.8889 | 2.7222 | 0.4 | 781378290 | 40000000 | 821378290
1 | 20 | 4 | 50 | 88.8889 | 2.7222 | 0.4 | 781378290 | 40000000 | 821378290
12 | 2 | 8 | 50 | 86.6667 | 0 | 0.3 | 785912400 | 30000000 | 815912400
7 | 11 | 7 | 50 | 74.4444 | 0 | 0.2 | 675078600 | 20000000 | 695078600
7 | 11 | 9 | 50 | 74.4444 | 0 | 0.2 | 675078600 | 20000000 | 695078600
9 | 13 | 3 | 50.1 | 88.4118 | 3.3363 | 0.4 | 771483093.9623 | 40000000 | 811483093.9623
11 | 6 | 16 | 50.1 | 85.6315 | 4.4484 | 0.5 | 736186481.8202 | 50000000 | 786186481.8202
1 | 3 | 20 | 50.1 | 87.8557 | 2.669 | 0.5 | 772491568.5949 | 50000000 | 822491568.5949
1 | 20 | 1 | 50.1 | 88.9678 | 2.7246 | 0.5 | 782072077.6049 | 50000000 | 832072077.6049
1 | 10 | 12 | 50.1 | 83.4073 | 2.5022 | 0.4 | 733665295.2386 | 40000000 | 773665295.2386
1 | 6 | 23 | 50.1 | 86.1876 | 2.5578 | 0.4 | 758372923.7381 | 40000000 | 798372923.7381
1 | 8 | 11 | 50.1 | 87.2997 | 2.6134 | 0.4 | 767953432.7481 | 40000000 | 807953432.7481
1 | 8 | 22 | 50.1 | 88.4118 | 2.669 | 0.4 | 777533941.758 | 40000000 | 817533941.758
1 | 27 | 2 | 50.1 | 88.4118 | 2.669 | 0.4 | 777533941.758 | 40000000 | 817533941.758
1 | 9 | 19 | 50.1 | 88.9678 | 2.669 | 0.4 | 782576314.9212 | 40000000 | 822576314.9212
1 | 27 | 4 | 50.1 | 88.9678 | 2.669 | 0.4 | 782576314.9212 | 40000000 | 822576314.9212
1 | 21 | 1 | 50.1 | 89.5239 | 2.7802 | 0.4 | 786610213.4517 | 40000000 | 826610213.4517
1 | 6 | 11 | 50.1 | 88.4118 | 2.669 | 0.3 | 777533941.758 | 30000000 | 807533941.758
1 | 5 | 19 | 50.1 | 88.4118 | 2.6134 | 0.3 | 778038179.0744 | 30000000 | 808038179.0744
1 | 6 | 16 | 50.1 | 88.4118 | 2.6134 | 0.3 | 778038179.0744 | 30000000 | 808038179.0744
7 | 11 | 6 | 50.1 | 75.0666 | 0 | 0.2 | 680720377.0255 | 20000000 | 700720377.0255
7 | 11 | 8 | 50.1 | 74.5105 | 0 | 0.2 | 675678003.8624 | 20000000 | 695678003.8624
9 | 14 | 23 | 50.2 | 87.3769 | 3.2836 | 0.5 | 762576981.2461 | 50000000 | 812576981.2461
9 | 11 | 24 | 50.2 | 88.49 | 3.3392 | 0.4 | 772165970.4213 | 40000000 | 812165970.4213
9 | 15 | 24 | 50.2 | 86.8204 | 3.3949 | 0.4 | 756520777.5565 | 40000000 | 796520777.5565
10 | 14 | 13 | 50.2 | 88.49 | 4.1741 | 0.1 | 764595715.8093 | 10000000 | 774595715.8093
11 | 7 | 15 | 50.2 | 86.2639 | 4.508 | 0.5 | 741380268.3326 | 50000000 | 791380268.3326
1 | 5 | 8 | 50.2 | 85.7073 | 2.6157 | 0.5 | 753492675.7118 | 50000000 | 803492675.7118
1 | 3 | 22 | 50.2 | 87.3769 | 2.6157 | 0.5 | 768633184.9357 | 50000000 | 818633184.9357
1 | 7 | 8 | 50.2 | 86.2639 | 2.5601 | 0.4 | 759044195.7605 | 40000000 | 799044195.7605
1 | 31 | 5 | 50.2 | 87.3769 | 2.6714 | 0.4 | 768128501.2949 | 40000000 | 808128501.2949
1 | 31 | 7 | 50.2 | 87.3769 | 2.6714 | 0.4 | 768128501.2949 | 40000000 | 808128501.2949
1 | 20 | 2 | 50.2 | 89.0466 | 2.7271 | 0.4 | 782764326.878 | 40000000 | 822764326.878
1 | 6 | 17 | 50.2 | 87.9335 | 2.6157 | 0.3 | 773680021.3437 | 30000000 | 803680021.3437
1 | 6 | 10 | 50.2 | 89.0466 | 2.7271 | 0.3 | 782764326.878 | 30000000 | 812764326.878
1 | 6 | 14 | 50.2 | 89.0466 | 2.6714 | 0.3 | 783269010.5188 | 30000000 | 813269010.5188
1 | 6 | 15 | 50.2 | 89.0466 | 2.6714 | 0.3 | 783269010.5188 | 30000000 | 813269010.5188
9 | 15 | 1 | 50.3 | 88.0111 | 3.3979 | 0.5 | 767290915.6744 | 50000000 | 817290915.6744
10 | 13 | 8 | 50.3 | 86.897 | 4.2891 | 0.5 | 749106272.5116 | 50000000 | 799106272.5116
9 | 11 | 3 | 50.3 | 88.0111 | 3.3422 | 0.4 | 767796044.6512 | 40000000 | 807796044.6512
1 | 12 | 8 | 50.3 | 91.3533 | 6.6844 | 0.5 | 767796044.6512 | 50000000 | 817796044.6512
1 | 10 | 15 | 50.3 | 83.5548 | 2.5066 | 0.4 | 734962661.1628 | 40000000 | 774962661.1628
1 | 10 | 23 | 50.3 | 84.1118 | 2.5623 | 0.4 | 739508821.9535 | 40000000 | 779508821.9535
1 | 31 | 6 | 50.3 | 87.454 | 2.6738 | 0.4 | 768806302.6047 | 40000000 | 808806302.6047
1 | 9 | 20 | 50.3 | 89.1251 | 2.6738 | 0.4 | 783960171.907 | 40000000 | 823960171.907
1 | 6 | 13 | 50.3 | 88.5681 | 2.6738 | 0.3 | 778908882.1395 | 30000000 | 808908882.1395
7 | 15 | 2 | 50.3 | 80.7697 | 0 | 0.5 | 732437016.2791 | 50000000 | 782437016.2791
9 | 11 | 2 | 50.4 | 87.531 | 3.3451 | 0.4 | 763415724.4248 | 40000000 | 803415724.4248
11 | 8 | 6 | 50.4 | 87.531 | 4.5159 | 0.5 | 752798684.5487 | 50000000 | 802798684.5487
1 | 10 | 16 | 50.4 | 84.1858 | 2.5088 | 0.4 | 740664924.6903 | 40000000 | 780664924.6903
1 | 11 | 6 | 50.4 | 84.1858 | 2.5088 | 0.4 | 740664924.6903 | 40000000 | 780664924.6903
12 | 8 | 10 | 50.4 | 86.9735 | 4.2929 | 0.4 | 749765244.5841 | 40000000 | 789765244.5841
1 | 11 | 22 | 50.4 | 91.4336 | 6.6903 | 0.4 | 768471457.6991 | 40000000 | 808471457.6991
1 | 21 | 23 | 50.4 | 90.8761 | 2.7319 | 0.2 | 799311430.6726 | 20000000 | 819311430.6726
7 | 21 | 5 | 50.4 | 80.8407 | 0 | 0.5 | 733081324.7788 | 50000000 | 783081324.7788
9 | 10 | 6 | 50.5 | 87.0497 | 3.2365 | 0.4 | 760037077.5912 | 40000000 | 800037077.5912
9 | 10 | 24 | 50.5 | 88.7238 | 3.3481 | 0.4 | 774205545.0829 | 40000000 | 814205545.0829
10 | 14 | 17 | 50.5 | 88.1657 | 4.0735 | 0.1 | 762567161.0718 | 10000000 | 772567161.0718
11 | 8 | 5 | 50.5 | 87.6077 | 4.5199 | 0.5 | 753458860.5414 | 50000000 | 803458860.5414
1 | 3 | 8 | 50.5 | 88.1657 | 2.7343 | 0.5 | 774711561.779 | 50000000 | 824711561.779
1 | 21 | 6 | 50.5 | 89.2818 | 2.7901 | 0.4 | 784325879.0055 | 40000000 | 824325879.0055
12 | 8 | 9 | 50.5 | 88.1657 | 4.0735 | 0.1 | 762567161.0718 | 10000000 | 772567161.0718
10 | 14 | 18 | 50.6 | 88.2428 | 4.077 | 0.1 | 763233842.7417 | 10000000 | 773233842.7417
11 | 7 | 13 | 50.6 | 86.5673 | 4.5238 | 0.5 | 743988397.4702 | 50000000 | 793988397.4702
12 | 29 | 19 | 50.6 | 88.8013 | 2.7366 | 0.5 | 780453451.6689 | 50000000 | 830453451.6689
1 | 10 | 13 | 50.6 | 83.7748 | 2.5132 | 0.4 | 736897970.2649 | 40000000 | 776897970.2649
1 | 10 | 10 | 50.6 | 84.8918 | 2.5691 | 0.4 | 746520692.9007 | 40000000 | 786520692.9007
1 | 31 | 4 | 50.6 | 87.6843 | 2.7366 | 0.4 | 770324269.947 | 40000000 | 810324269.947
1 | 31 | 2 | 50.6 | 87.6843 | 2.6808 | 0.4 | 770830729.0331 | 40000000 | 810830729.0331
1 | 26 | 22 | 50.6 | 88.8013 | 2.6808 | 0.4 | 780959910.755 | 40000000 | 820959910.755
1 | 21 | 4 | 50.6 | 89.3598 | 2.7925 | 0.4 | 785011583.4437 | 40000000 | 825011583.4437
1 | 30 | 24 | 50.6 | 87.6843 | 2.7366 | 0.3 | 770324269.947 | 30000000 | 800324269.947
7 | 15 | 3 | 50.6 | 80.9823 | 0 | 0.5 | 734365674.8344 | 50000000 | 784365674.8344
7 | 15 | 6 | 50.6 | 81.5408 | 0 | 0.5 | 739430265.6954 | 50000000 | 789430265.6954
9 | 12 | 8 | 50.7 | 89.4377 | 3.3539 | 0.4 | 780626770.849 | 40000000 | 820626770.849
10 | 14 | 14 | 50.7 | 88.8787 | 4.1924 | 0.1 | 767954258.3352 | 10000000 | 777954258.3352
1 | 6 | 24 | 50.7 | 86.6428 | 2.5713 | 0.5 | 762378352.8291 | 50000000 | 812378352.8291
1 | 21 | 5 | 50.7 | 89.4377 | 2.7949 | 0.4 | 785695775.8545 | 40000000 | 825695775.8545
1 | 9 | 22 | 50.7 | 89.4377 | 2.6831 | 0.4 | 786709576.8556 | 40000000 | 826709576.8556
1 | 17 | 13 | 50.7 | 89.9967 | 2.8508 | 0.3 | 790257880.3594 | 30000000 | 820257880.3594
1 | 21 | 24 | 50.7 | 90.5557 | 2.739 | 0.2 | 796340686.366 | 20000000 | 816340686.366
9 | 12 | 6 | 50.8 | 88.9559 | 3.3568 | 0.4 | 776231642.3789 | 40000000 | 816231642.3789
1 | 2 | 24 | 50.8 | 87.2775 | 2.6855 | 0.5 | 767099505.4097 | 50000000 | 817099505.4097
1 | 3 | 23 | 50.8 | 87.837 | 2.6295 | 0.5 | 772680255.7797 | 50000000 | 822680255.7797
1 | 20 | 5 | 50.8 | 90.0749 | 2.7974 | 0.4 | 791451870.6608 | 40000000 | 831451870.6608
1 | 21 | 2 | 50.8 | 90.0749 | 2.7974 | 0.4 | 791451870.6608 | 40000000 | 831451870.6608
1 | 21 | 3 | 50.8 | 90.0749 | 2.7974 | 0.4 | 791451870.6608 | 40000000 | 831451870.6608
1 | 10 | 24 | 50.8 | 84.4802 | 2.5176 | 0.3 | 743254481.1013 | 30000000 | 773254481.1013
1 | 6 | 12 | 50.8 | 88.9559 | 2.6855 | 0.3 | 782319733.6916 | 30000000 | 812319733.6916
1 | 9 | 10 | 50.8 | 89.5154 | 2.6855 | 0.1 | 787393143.1189 | 10000000 | 797393143.1189
7 | 21 | 6 | 50.8 | 81.6828 | 0 | 0.5 | 740717776.3877 | 50000000 | 790717776.3877
6 | 1 | 3 | 50.8 | 86.1586 | 3.2449 | 0.3 | 751879277.1278 | 30000000 | 781879277.1278
9 | 10 | 1 | 50.9 | 87.3531 | 3.1917 | 0.4 | 763193965.0099 | 40000000 | 803193965.0099
9 | 10 | 5 | 50.9 | 87.9131 | 3.2477 | 0.4 | 767763988.7525 | 40000000 | 807763988.7525
9 | 12 | 7 | 50.9 | 89.033 | 3.3597 | 0.4 | 776904036.2376 | 40000000 | 816904036.2376
1 | 2 | 23 | 50.9 | 86.7932 | 2.6878 | 0.5 | 762686184.5941 | 50000000 | 812686184.5941
1 | 8 | 17 | 50.9 | 88.473 | 2.6318 | 0.4 | 778427377.4851 | 40000000 | 818427377.4851
1 | 9 | 18 | 50.9 | 89.593 | 2.6878 | 0.4 | 788075205.3861 | 40000000 | 828075205.3861
1 | 9 | 23 | 50.9 | 89.593 | 2.6878 | 0.4 | 788075205.3861 | 40000000 | 828075205.3861
9 | 14 | 3 | 51 | 87.4286 | 3.3626 | 0.5 | 762328384.6154 | 50000000 | 812328384.6154
9 | 10 | 4 | 51 | 87.989 | 3.1945 | 0.4 | 768935230.6154 | 40000000 | 808935230.6154
11 | 7 | 14 | 51 | 86.8681 | 4.5396 | 0.5 | 746573598 | 50000000 | 796573598
11 | 7 | 23 | 51 | 88.5495 | 4.5396 | 0.5 | 761820165.6923 | 50000000 | 811820165.6923
1 | 4 | 23 | 51 | 87.4286 | 2.6341 | 0.5 | 768935230.6154 | 50000000 | 818935230.6154
1 | 3 | 7 | 51 | 87.989 | 2.7462 | 0.5 | 773000982 | 50000000 | 823000982
1 | 31 | 3 | 51 | 87.4286 | 2.6901 | 0.4 | 768427011.6923 | 40000000 | 808427011.6923
1 | 11 | 23 | 51 | 91.9121 | 6.6692 | 0.4 | 773000982 | 40000000 | 813000982
1 | 31 | 1 | 51 | 87.989 | 2.6901 | 0.4 | 773509200.9231 | 40000000 | 813509200.9231
1 | 11 | 1 | 51 | 84.6264 | 2.578 | 0.3 | 744032503.3846 | 30000000 | 774032503.3846
1 | 17 | 10 | 51 | 90.2308 | 2.6901 | 0.3 | 793837957.8462 | 30000000 | 823837957.8462
6 | 1 | 4 | 51 | 90.7912 | 3.2505 | 0.3 | 793837957.8462 | 30000000 | 823837957.8462
10 | 14 | 16 | 51.1 | 89.1866 | 4.1508 | 0.1 | 771123204.9089 | 10000000 | 781123204.9089
1 | 7 | 2 | 51.1 | 86.382 | 2.5802 | 0.5 | 759932762.6213 | 50000000 | 809932762.6213
1 | 9 | 8 | 51.1 | 89.1866 | 2.6924 | 0.5 | 784348273.067 | 50000000 | 834348273.067
1 | 11 | 5 | 51.1 | 84.6992 | 2.5241 | 0.4 | 745181725.0604 | 40000000 | 785181725.0604
1 | 12 | 7 | 51.1 | 91.9912 | 6.675 | 0.4 | 773666487.247 | 40000000 | 813666487.247
1 | 9 | 21 | 51.1 | 89.7475 | 2.6924 | 0.4 | 789434837.7431 | 40000000 | 829434837.7431
1 | 17 | 16 | 51.1 | 89.7475 | 2.8046 | 0.3 | 788417524.8079 | 30000000 | 818417524.8079
12 | 13 | 9 | 51.1 | 88.6257 | 2.9168 | 0.1 | 777227082.5203 | 10000000 | 787227082.5203
11 | 6 | 15 | 51.2 | 86.4561 | 4.5474 | 0.5 | 742766763.7895 | 50000000 | 792766763.7895
11 | 8 | 4 | 51.2 | 88.1404 | 4.6035 | 0.5 | 757530462.3158 | 50000000 | 807530462.3158
1 | 7 | 1 | 51.2 | 87.0175 | 2.5825 | 0.5 | 765675951.1579 | 50000000 | 815675951.1579
1 | 3 | 6 | 51.2 | 88.7018 | 2.7509 | 0.5 | 779421463.5789 | 50000000 | 829421463.5789
12 | 2 | 23 | 51.2 | 86.4561 | 4.6035 | 0.4 | 742257670.7368 | 40000000 | 782257670.7368
12 | 22 | 11 | 51.2 | 87.5789 | 2.807 | 0.4 | 768730509.4737 | 40000000 | 808730509.4737
1 | 11 | 24 | 51.2 | 92.0702 | 6.7368 | 0.4 | 773821440 | 40000000 | 813821440
1 | 15 | 19 | 51.2 | 88.7018 | 2.6947 | 0.4 | 779930556.6316 | 40000000 | 819930556.6316
1 | 9 | 7 | 51.2 | 89.2632 | 2.6947 | 0.4 | 785021487.1579 | 40000000 | 825021487.1579
1 | 17 | 14 | 51.2 | 90.386 | 2.807 | 0.3 | 794185162.1053 | 30000000 | 824185162.1053
12 | 2 | 5 | 51.2 | 88.7018 | 0 | 0.2 | 804367023.1579 | 20000000 | 824367023.1579
9 | 10 | 3 | 51.3 | 87.6539 | 3.2589 | 0.4 | 765312079.2683 | 40000000 | 805312079.2683
9 | 16 | 10 | 51.3 | 87.092 | 3.3713 | 0.4 | 759197735.0931 | 40000000 | 799197735.0931
10 | 14 | 15 | 51.3 | 88.7777 | 4.1579 | 0.1 | 767350193.9934 | 10000000 | 777350193.9934
11 | 4 | 19 | 51.3 | 92.7108 | 8.8778 | 0.5 | 760216792.4556 | 50000000 | 810216792.4556
1 | 5 | 7 | 51.3 | 88.2158 | 2.6409 | 0.5 | 776012181.575 | 50000000 | 826012181.575
1 | 3 | 5 | 51.3 | 88.7777 | 2.7532 | 0.5 | 780088411.0252 | 50000000 | 830088411.0252
12 | 22 | 13 | 51.3 | 88.2158 | 2.7532 | 0.4 | 774993124.2125 | 40000000 | 814993124.2125
1 | 15 | 17 | 51.3 | 88.7777 | 2.697 | 0.4 | 780597939.7065 | 40000000 | 820597939.7065
1 | 5 | 23 | 51.3 | 89.9014 | 2.697 | 0.4 | 790788513.3319 | 40000000 | 830788513.3319
12 | 22 | 10 | 51.3 | 87.6539 | 2.8094 | 0.3 | 769388308.7185 | 30000000 | 799388308.7185
12 | 22 | 12 | 51.3 | 88.2158 | 2.8094 | 0.3 | 774483595.5312 | 30000000 | 804483595.5312
12 | 1 | 23 | 51.3 | 88.7777 | 0 | 0.2 | 805055316.4074 | 20000000 | 825055316.4074
12 | 6 | 18 | 51.3 | 85.4064 | 4.4389 | 0.1 | 734230829.7108 | 10000000 | 744230829.7108
9 | 10 | 2 | 51.4 | 87.7287 | 3.2617 | 0.4 | 765964961.7243 | 40000000 | 805964961.7243
9 | 11 | 10 | 51.4 | 91.6652 | 3.4304 | 0.4 | 800132506.6214 | 40000000 | 840132506.6214
9 | 11 | 11 | 51.4 | 90.5405 | 3.3742 | 0.4 | 790443202.8446 | 40000000 | 830443202.8446
10 | 13 | 21 | 51.4 | 89.9781 | 4.1053 | 0.4 | 778714045.6411 | 40000000 | 818714045.6411
12 | 22 | 15 | 51.4 | 88.291 | 2.8118 | 0.5 | 775144302.1444 | 50000000 | 825144302.1444
1 | 15 | 20 | 51.4 | 88.8534 | 2.7556 | 0.5 | 780753899.0678 | 50000000 | 830753899.0678
1 | 12 | 1 | 51.4 | 92.2276 | 6.6921 | 0.4 | 775654265.5011 | 40000000 | 815654265.5011
12 | 13 | 10 | 51.4 | 88.8534 | 2.9243 | 0.4 | 779224008.9978 | 40000000 | 819224008.9978
1 | 8 | 24 | 51.4 | 89.4158 | 2.6993 | 0.4 | 786363495.9912 | 40000000 | 826363495.9912
1 | 20 | 6 | 51.4 | 91.1028 | 2.8118 | 0.3 | 800642469.9781 | 30000000 | 830642469.9781
12 | 2 | 7 | 51.4 | 88.291 | 0 | 0.2 | 800642469.9781 | 20000000 | 820642469.9781
12 | 5 | 23 | 51.4 | 87.7287 | 4.5551 | 0.1 | 754235804.5208 | 10000000 | 764235804.5208
9 | 12 | 5 | 51.5 | 89.4918 | 3.377 | 0.4 | 780907535.4098 | 40000000 | 820907535.4098
11 | 7 | 12 | 51.5 | 87.8033 | 4.559 | 0.5 | 754877284.2295 | 50000000 | 804877284.2295
11 | 4 | 20 | 51.5 | 93.4317 | 8.8929 | 0.5 | 766616417.1148 | 50000000 | 816616417.1148
1 | 15 | 21 | 51.5 | 88.929 | 2.7579 | 0.4 | 781417932.4918 | 40000000 | 821417932.4918
1 | 8 | 16 | 51.5 | 88.929 | 2.7016 | 0.4 | 781928329.5738 | 40000000 | 821928329.5738
1 | 15 | 18 | 51.5 | 88.929 | 2.7016 | 0.4 | 781928329.5738 | 40000000 | 821928329.5738
1 | 9 | 4 | 51.5 | 89.4918 | 2.7016 | 0.4 | 787032300.3934 | 40000000 | 827032300.3934
1 | 9 | 6 | 51.5 | 89.4918 | 2.7016 | 0.4 | 787032300.3934 | 40000000 | 827032300.3934
1 | 9 | 11 | 51.5 | 89.4918 | 2.7016 | 0.3 | 787032300.3934 | 30000000 | 817032300.3934
1 | 17 | 15 | 51.5 | 90.6175 | 2.8142 | 0.2 | 796219447.8689 | 20000000 | 816219447.8689
12 | 2 | 2 | 51.5 | 88.929 | 0 | 0.2 | 806427389.5082 | 20000000 | 826427389.5082
12 | 2 | 4 | 51.5 | 88.929 | 0 | 0.2 | 806427389.5082 | 20000000 | 826427389.5082
12 | 2 | 6 | 51.5 | 89.4918 | 0 | 0.2 | 811531360.3279 | 20000000 | 831531360.3279
9 | 15 | 2 | 51.6 | 89.0044 | 3.3799 | 0.5 | 776461387.5983 | 50000000 | 826461387.5983
9 | 11 | 12 | 51.6 | 90.6943 | 3.4362 | 0.4 | 791275453.5459 | 40000000 | 831275453.5459
9 | 16 | 9 | 51.6 | 87.3144 | 3.3799 | 0.4 | 761136491.7904 | 40000000 | 801136491.7904
12 | 13 | 11 | 51.6 | 88.441 | 2.9856 | 0.5 | 774928898.0175 | 50000000 | 824928898.0175
1 | 3 | 1 | 51.6 | 88.441 | 2.7603 | 0.5 | 776972217.4585 | 50000000 | 826972217.4585
1 | 4 | 4 | 51.6 | 88.441 | 2.6476 | 0.5 | 777993877.179 | 50000000 | 827993877.179
1 | 5 | 6 | 51.6 | 88.441 | 2.6476 | 0.5 | 777993877.179 | 50000000 | 827993877.179
1 | 4 | 16 | 51.6 | 90.131 | 2.7603 | 0.4 | 792297113.2664 | 40000000 | 832297113.2664
12 | 22 | 14 | 51.6 | 88.441 | 2.8166 | 0.3 | 776461387.5983 | 30000000 | 806461387.5983
1 | 17 | 7 | 51.6 | 90.6943 | 2.5913 | 0.2 | 798937901.4498 | 20000000 | 818937901.4498
12 | 1 | 24 | 51.6 | 89.0044 | 0 | 0.2 | 807111179.214 | 20000000 | 827111179.214
9 | 11 | 9 | 51.7 | 91.8986 | 3.3828 | 0.4 | 802680860.6107 | 40000000 | 842680860.6107
9 | 12 | 4 | 51.7 | 89.6434 | 3.3828 | 0.4 | 782230392.8244 | 40000000 | 822230392.8244
9 | 16 | 1 | 51.7 | 87.3882 | 3.3828 | 0.4 | 761779925.0382 | 40000000 | 801779925.0382
11 | 7 | 5 | 51.7 | 89.0796 | 4.6231 | 0.5 | 765870018.5954 | 50000000 | 815870018.5954
11 | 7 | 8 | 51.7 | 89.6434 | 4.5104 | 0.5 | 772005158.9313 | 50000000 | 822005158.9313
1 | 3 | 24 | 51.7 | 88.5158 | 2.7062 | 0.5 | 778140299.2672 | 50000000 | 828140299.2672
1 | 4 | 1 | 51.7 | 88.5158 | 2.6498 | 0.5 | 778651560.9618 | 50000000 | 828651560.9618
1 | 4 | 2 | 51.7 | 88.5158 | 2.6498 | 0.5 | 778651560.9618 | 50000000 | 828651560.9618
1 | 4 | 6 | 51.7 | 88.5158 | 2.6498 | 0.5 | 778651560.9618 | 50000000 | 828651560.9618
1 | 3 | 4 | 51.7 | 89.0796 | 2.7626 | 0.5 | 782741654.5191 | 50000000 | 832741654.5191
12 | 16 | 12 | 51.7 | 89.6434 | 2.9881 | 0.5 | 785809224.687 | 50000000 | 835809224.687
1 | 24 | 22 | 51.7 | 90.771 | 2.7062 | 0.5 | 798590767.0534 | 50000000 | 848590767.0534
1 | 12 | 6 | 51.7 | 93.0262 | 6.7092 | 0.4 | 782741654.5191 | 40000000 | 822741654.5191
1 | 15 | 14 | 51.7 | 89.6434 | 2.7626 | 0.4 | 787854271.4656 | 40000000 | 827854271.4656
1 | 9 | 5 | 51.7 | 89.6434 | 2.7062 | 0.4 | 788365533.1603 | 40000000 | 828365533.1603
1 | 9 | 3 | 51.7 | 89.6434 | 2.6498 | 0.4 | 788876794.855 | 40000000 | 828876794.855
1 | 9 | 17 | 51.7 | 90.2072 | 2.7062 | 0.4 | 793478150.1069 | 40000000 | 833478150.1069
12 | 4 | 19 | 51.7 | 87.952 | 5.7507 | 0.2 | 745419550.8092 | 20000000 | 765419550.8092
9 | 14 | 7 | 51.8 | 88.0261 | 3.3856 | 0.5 | 767538882.3529 | 50000000 | 817538882.3529
1 | 7 | 7 | 51.8 | 87.4619 | 2.5956 | 0.5 | 769585652.7059 | 50000000 | 819585652.7059
12 | 13 | 12 | 51.8 | 88.5904 | 2.9342 | 0.5 | 776749348.9412 | 50000000 | 826749348.9412
1 | 28 | 24 | 51.8 | 89.719 | 2.8778 | 0.5 | 787494893.2941 | 50000000 | 837494893.2941
1 | 26 | 14 | 51.8 | 91.4118 | 2.7649 | 0.5 | 803869056.1176 | 50000000 | 853869056.1176
1 | 8 | 15 | 51.8 | 89.1547 | 2.6521 | 0.4 | 784424737.7647 | 40000000 | 824424737.7647
12 | 3 | 10 | 51.8 | 86.3333 | 4.3449 | 0.3 | 743489330.7059 | 30000000 | 773489330.7059
1 | 16 | 24 | 51.8 | 90.2832 | 2.7649 | 0.3 | 793635204.3529 | 30000000 | 823635204.3529
1 | 9 | 12 | 51.8 | 90.2832 | 2.7085 | 0.3 | 794146896.9412 | 30000000 | 824146896.9412
12 | 2 | 3 | 51.8 | 89.719 | 0 | 0.2 | 813591215.2941 | 20000000 | 833591215.2941
12 | 6 | 19 | 51.8 | 86.3333 | 4.4577 | 0.1 | 742465945.5294 | 10000000 | 752465945.5294
12 | 7 | 11 | 51.8 | 86.8976 | 4.3449 | 0.1 | 748606256.5882 | 10000000 | 758606256.5882
9 | 14 | 6 | 51.9 | 88.6649 | 3.3885 | 0.5 | 773305041.5452 | 50000000 | 823305041.5452
10 | 12 | 14 | 51.9 | 87.5354 | 4.2921 | 0.5 | 754868629.9587 | 50000000 | 804868629.9587
10 | 12 | 17 | 51.9 | 87.5354 | 4.2921 | 0.5 | 754868629.9587 | 50000000 | 804868629.9587
9 | 11 | 14 | 51.9 | 90.9238 | 3.3885 | 0.4 | 793789943.3079 | 40000000 | 833789943.3079
9 | 2 | 11 | 51.9 | 93.7476 | 3.6144 | 0.1 | 817347580.3351 | 10000000 | 827347580.3351
9 | 2 | 13 | 51.9 | 93.7476 | 3.6144 | 0.1 | 817347580.3351 | 10000000 | 827347580.3351
11 | 7 | 6 | 51.9 | 89.2296 | 4.6309 | 0.5 | 767159571.0163 | 50000000 | 817159571.0163
11 | 7 | 7 | 51.9 | 89.2296 | 4.518 | 0.5 | 768183816.1045 | 50000000 | 818183816.1045
1 | 26 | 17 | 51.9 | 92.6181 | 2.7672 | 0.5 | 814786967.6148 | 50000000 | 864786967.6148
1 | 12 | 2 | 51.9 | 92.6181 | 6.7769 | 0.4 | 778426266.9859 | 40000000 | 818426266.9859
1 | 4 | 12 | 51.9 | 90.9238 | 2.7672 | 0.4 | 799423291.2927 | 40000000 | 839423291.2927
1 | 11 | 4 | 51.9 | 85.2764 | 2.5978 | 0.3 | 749747404.518 | 30000000 | 779747404.518
12 | 2 | 1 | 51.9 | 89.7943 | 0 | 0.2 | 814274845.0707 | 20000000 | 834274845.0707
12 | 7 | 12 | 51.9 | 87.5354 | 4.405 | 0.1 | 753844384.8705 | 10000000 | 763844384.8705
12 | 8 | 8 | 51.9 | 89.2296 | 4.1226 | 0.1 | 771768673.9129 | 10000000 | 781768673.9129
12 | 12 | 21 | 51.9 | 88.6649 | 2.8802 | 0.1 | 777914144.4418 | 10000000 | 787914144.4418
9 | 16 | 2 | 52 | 85.913 | 3.3913 | 0.4 | 748325285.2174 | 40000000 | 788325285.2174
11 | 4 | 22 | 52 | 93.8261 | 8.9304 | 0.5 | 769852450.9565 | 50000000 | 819852450.9565
12 | 28 | 24 | 52 | 89.8696 | 2.7696 | 0.5 | 789841962 | 50000000 | 839841962
1 | 4 | 11 | 52 | 91 | 2.8261 | 0.5 | 799580441.7391 | 50000000 | 849580441.7391
1 | 26 | 15 | 52 | 92.6957 | 2.7696 | 0.5 | 815469540.2609 | 50000000 | 865469540.2609
1 | 8 | 12 | 52 | 89.3043 | 2.6565 | 0.4 | 785741549.4783 | 40000000 | 825741549.4783
1 | 15 | 23 | 52 | 89.8696 | 2.7696 | 0.4 | 789841962 | 40000000 | 829841962
1 | 9 | 2 | 52 | 89.8696 | 2.713 | 0.4 | 790354513.5652 | 40000000 | 830354513.5652
1 | 15 | 16 | 52 | 89.8696 | 2.713 | 0.4 | 790354513.5652 | 40000000 | 830354513.5652
1 | 9 | 24 | 52 | 90.4348 | 2.713 | 0.4 | 795480029.2174 | 40000000 | 835480029.2174
12 | 8 | 7 | 52 | 89.3043 | 4.1261 | 0.1 | 772415208.7826 | 10000000 | 782415208.7826
12 | 12 | 19 | 52 | 88.7391 | 2.9391 | 0.1 | 778053276 | 10000000 | 788053276
9 | 12 | 1 | 52.1 | 89.9446 | 3.3941 | 0.4 | 784858871.7264 | 40000000 | 824858871.7264
10 | 14 | 9 | 52.1 | 91.076 | 4.2427 | 0.1 | 787423770 | 10000000 | 797423770
11 | 6 | 23 | 52.1 | 88.8132 | 4.6387 | 0.5 | 763313726.228 | 50000000 | 813313726.228
11 | 8 | 3 | 52.1 | 88.8132 | 4.6387 | 0.5 | 763313726.228 | 50000000 | 813313726.228
11 | 7 | 4 | 52.1 | 89.3789 | 4.6387 | 0.5 | 768443522.7752 | 50000000 | 818443522.7752
1 | 4 | 5 | 52.1 | 88.8132 | 2.6587 | 0.5 | 781268014.1433 | 50000000 | 831268014.1433
12 | 14 | 14 | 52.1 | 89.9446 | 2.885 | 0.5 | 789475688.6189 | 50000000 | 839475688.6189
1 | 15 | 15 | 52.1 | 89.9446 | 2.7719 | 0.5 | 790501647.9283 | 50000000 | 840501647.9283
1 | 29 | 1 | 52.1 | 91.076 | 2.885 | 0.5 | 799735281.7134 | 50000000 | 849735281.7134
1 | 26 | 10 | 52.1 | 91.076 | 2.7153 | 0.5 | 801274220.6775 | 50000000 | 851274220.6775
12 | 3 | 9 | 52.1 | 85.9848 | 4.5255 | 0.4 | 738690702.8013 | 40000000 | 778690702.8013
12 | 3 | 4 | 52.1 | 87.1162 | 4.6387 | 0.4 | 747924336.5863 | 40000000 | 787924336.5863
12 | 3 | 6 | 52.1 | 87.6819 | 4.6387 | 0.4 | 753054133.1336 | 40000000 | 793054133.1336
1 | 12 | 5 | 52.1 | 92.7731 | 6.7317 | 0.4 | 780242054.8339 | 40000000 | 820242054.8339
1 | 5 | 24 | 52.1 | 90.5103 | 2.7153 | 0.4 | 796144424.1303 | 40000000 | 836144424.1303
1 | 9 | 16 | 52.1 | 90.5103 | 2.7153 | 0.4 | 796144424.1303 | 40000000 | 836144424.1303
12 | 3 | 11 | 52.1 | 87.1162 | 4.3558 | 0.2 | 750489234.8599 | 20000000 | 770489234.8599
12 | 13 | 8 | 52.1 | 89.3789 | 2.9982 | 0.2 | 783319932.7622 | 20000000 | 803319932.7622
12 | 3 | 13 | 52.1 | 86.5505 | 4.3558 | 0.1 | 745359438.3127 | 10000000 | 755359438.3127
12 | 3 | 18 | 52.1 | 87.1162 | 4.5821 | 0.1 | 748437316.241 | 10000000 | 758437316.241
12 | 7 | 13 | 52.1 | 87.6819 | 4.3558 | 0.1 | 755619031.4072 | 10000000 | 765619031.4072
12 | 12 | 20 | 52.1 | 88.8132 | 2.9416 | 0.1 | 778703115.8697 | 10000000 | 788703115.8697
9 | 14 | 5 | 52.2 | 88.321 | 3.397 | 0.5 | 770110223.4273 | 50000000 | 820110223.4273
10 | 12 | 15 | 52.2 | 87.7549 | 4.1896 | 0.5 | 757788459.8525 | 50000000 | 807788459.8525
10 | 12 | 16 | 52.2 | 87.7549 | 4.3028 | 0.5 | 756761646.2213 | 50000000 | 806761646.2213
10 | 13 | 22 | 52.2 | 91.1518 | 4.1896 | 0.4 | 788592868.7896 | 40000000 | 828592868.7896
9 | 2 | 10 | 52.2 | 93.9826 | 3.68 | 0.1 | 818883870.9111 | 10000000 | 828883870.9111
9 | 2 | 12 | 52.2 | 93.9826 | 3.5102 | 0.1 | 820424091.3579 | 10000000 | 830424091.3579
9 | 2 | 14 | 52.2 | 93.9826 | 3.6234 | 0.1 | 819397277.7267 | 10000000 | 829397277.7267
11 | 7 | 11 | 52.2 | 90.0195 | 4.6425 | 0.5 | 774217477.9523 | 50000000 | 824217477.9523
1 | 4 | 3 | 52.2 | 88.8872 | 2.661 | 0.5 | 781918580.1866 | 50000000 | 831918580.1866
1 | 15 | 22 | 52.2 | 89.4534 | 2.7742 | 0.5 | 786025834.7115 | 50000000 | 836025834.7115
12 | 14 | 13 | 52.2 | 90.0195 | 2.944 | 0.5 | 789619682.4208 | 50000000 | 839619682.4208
1 | 4 | 10 | 52.2 | 90.0195 | 2.7742 | 0.5 | 791159902.8677 | 50000000 | 841159902.8677
12 | 2 | 24 | 52.2 | 87.7549 | 4.6425 | 0.4 | 753681205.3275 | 40000000 | 793681205.3275
1 | 8 | 13 | 52.2 | 89.4534 | 2.7176 | 0.4 | 786539241.5271 | 40000000 | 826539241.5271
1 | 4 | 13 | 52.2 | 90.5857 | 2.7742 | 0.4 | 796293971.0239 | 40000000 | 836293971.0239
1 | 6 | 2 | 52.2 | 90.5857 | 2.661 | 0.4 | 797320784.6551 | 40000000 | 837320784.6551
1 | 16 | 13 | 52.2 | 90.0195 | 2.7742 | 0.3 | 791159902.8677 | 30000000 | 821159902.8677
1 | 17 | 8 | 52.2 | 91.1518 | 2.6043 | 0.3 | 802968259.6269 | 30000000 | 832968259.6269
12 | 7 | 15 | 52.2 | 88.321 | 4.4161 | 0.2 | 760868900.7462 | 20000000 | 780868900.7462
12 | 4 | 21 | 52.2 | 87.7549 | 5.0954 | 0.1 | 749573950.8026 | 10000000 | 759573950.8026
12 | 4 | 23 | 52.2 | 87.7549 | 5.0954 | 0.1 | 749573950.8026 | 10000000 | 759573950.8026
12 | 6 | 20 | 52.2 | 87.1887 | 4.4161 | 0.1 | 750600764.4338 | 10000000 | 760600764.4338
12 | 7 | 9 | 52.2 | 87.7549 | 4.3594 | 0.1 | 756248239.4056 | 10000000 | 766248239.4056
12 | 7 | 8 | 52.2 | 87.7549 | 4.3028 | 0.1 | 756761646.2213 | 10000000 | 766761646.2213
12 | 12 | 18 | 52.2 | 88.8872 | 2.8874 | 0.1 | 779864952.9241 | 10000000 | 789864952.9241
9 | 12 | 3 | 52.3 | 90.0943 | 3.3998 | 0.4 | 786164567.909 | 40000000 | 826164567.909
11 | 7 | 24 | 52.3 | 88.3944 | 4.5897 | 0.5 | 759959082.312 | 50000000 | 809959082.312
11 | 8 | 2 | 52.3 | 88.961 | 4.5897 | 0.5 | 765097412.8212 | 50000000 | 815097412.8212
11 | 7 | 9 | 52.3 | 90.0943 | 4.5897 | 0.5 | 775374073.8397 | 50000000 | 825374073.8397
1 | 3 | 3 | 52.3 | 89.5276 | 2.7765 | 0.5 | 786678400.9599 | 50000000 | 836678400.9599
1 | 26 | 11 | 52.3 | 91.2275 | 2.7765 | 0.5 | 802093392.4875 | 50000000 | 852093392.4875
1 | 26 | 16 | 52.3 | 91.7941 | 2.7765 | 0.5 | 807231722.9967 | 50000000 | 857231722.9967
12 | 3 | 8 | 52.3 | 86.1278 | 4.5897 | 0.4 | 739405760.2752 | 40000000 | 779405760.2752
12 | 3 | 7 | 52.3 | 87.8277 | 4.6464 | 0.4 | 754306918.7519 | 40000000 | 794306918.7519
1 | 4 | 14 | 52.3 | 90.6609 | 2.7765 | 0.4 | 796955061.9783 | 40000000 | 836955061.9783
12 | 6 | 17 | 52.3 | 86.1278 | 4.4764 | 0.1 | 740433426.377 | 10000000 | 750433426.377
12 | 3 | 17 | 52.3 | 87.2611 | 4.6464 | 0.1 | 749168588.2427 | 10000000 | 759168588.2427
12 | 4 | 22 | 52.3 | 87.8277 | 5.0997 | 0.1 | 750196254.3445 | 10000000 | 760196254.3445
9 | 14 | 4 | 52.4 | 88.4675 | 3.4026 | 0.5 | 771387545.4545 | 50000000 | 821387545.4545
9 | 15 | 3 | 52.4 | 89.6017 | 3.4026 | 0.5 | 781672712.7273 | 50000000 | 831672712.7273
10 | 13 | 23 | 52.4 | 91.303 | 4.2532 | 0.4 | 789386588.1818 | 40000000 | 829386588.1818
1 | 5 | 4 | 52.4 | 88.4675 | 2.6654 | 0.5 | 778072904.1818 | 50000000 | 828072904.1818
1 | 26 | 12 | 52.4 | 91.303 | 2.7221 | 0.5 | 803271564 | 50000000 | 853271564
12 | 3 | 3 | 52.4 | 87.9004 | 4.6502 | 0.4 | 754931277.8182 | 40000000 | 794931277.8182
12 | 3 | 5 | 52.4 | 87.9004 | 4.6502 | 0.4 | 754931277.8182 | 40000000 | 794931277.8182
1 | 12 | 4 | 52.4 | 93.0043 | 6.7485 | 0.4 | 782186971.0909 | 40000000 | 822186971.0909
1 | 8 | 14 | 52.4 | 89.6017 | 2.7221 | 0.4 | 787843813.0909 | 40000000 | 827843813.0909
1 | 11 | 2 | 52.4 | 85.632 | 2.6087 | 0.3 | 752874244.3636 | 30000000 | 782874244.3636
1 | 17 | 6 | 52.4 | 91.303 | 2.6654 | 0.3 | 803785822.3636 | 30000000 | 833785822.3636
12 | 3 | 16 | 52.4 | 87.3333 | 4.5935 | 0.1 | 750302952.5455 | 10000000 | 760302952.5455
12 | 6 | 21 | 52.4 | 87.3333 | 4.3667 | 0.1 | 752359986 | 10000000 | 762359986
9 | 11 | 8 | 52.5 | 92.5135 | 3.4622 | 0.4 | 807537245.3514 | 40000000 | 847537245.3514
9 | 2 | 15 | 52.5 | 94.2162 | 3.6892 | 0.1 | 820918997.027 | 10000000 | 830918997.027
12 | 3 | 1 | 52.5 | 87.4054 | 4.6541 | 0.5 | 750407459.3514 | 50000000 | 800407459.3514
11 | 7 | 10 | 52.5 | 90.2432 | 4.7108 | 0.5 | 775626914.4324 | 50000000 | 825626914.4324
12 | 16 | 20 | 52.5 | 88.5405 | 2.9514 | 0.5 | 776141597.1892 | 50000000 | 826141597.1892
1 | 5 | 3 | 52.5 | 88.5405 | 2.6676 | 0.5 | 778715010.973 | 50000000 | 828715010.973
1 | 26 | 8 | 52.5 | 91.3784 | 2.7811 | 0.5 | 803419783.2973 | 50000000 | 853419783.2973
12 | 3 | 2 | 52.5 | 87.4054 | 4.6541 | 0.4 | 750407459.3514 | 40000000 | 790407459.3514
1 | 11 | 3 | 52.5 | 85.7027 | 2.6108 | 0.3 | 753495555.8919 | 30000000 | 783495555.8919
1 | 17 | 9 | 52.5 | 91.9459 | 2.6108 | 0.3 | 810110659.1351 | 30000000 | 840110659.1351
12 | 3 | 20 | 52.5 | 86.8378 | 4.5973 | 0.1 | 745775314.5405 | 10000000 | 755775314.5405
12 | 7 | 10 | 52.5 | 86.8378 | 4.3703 | 0.1 | 747834045.5676 | 10000000 | 757834045.5676
12 | 3 | 15 | 52.5 | 87.4054 | 4.5973 | 0.1 | 750922142.1081 | 10000000 | 760922142.1081
12 | 6 | 22 | 52.5 | 87.4054 | 4.3703 | 0.1 | 752980873.1351 | 10000000 | 762980873.1351
12 | 7 | 16 | 52.5 | 88.5405 | 4.427 | 0.1 | 762759845.5135 | 10000000 | 772759845.5135
12 | 12 | 22 | 52.5 | 89.1081 | 2.9514 | 0.1 | 781288424.7568 | 10000000 | 791288424.7568
9 | 12 | 2 | 52.6 | 90.3175 | 3.3514 | 0.4 | 788627643.1231 | 40000000 | 828627643.1231
9 | 7 | 21 | 52.6 | 92.5896 | 3.465 | 0.3 | 808201679.987 | 30000000 | 838201679.987
10 | 14 | 1 | 52.6 | 91.4536 | 4.3739 | 0.3 | 789657855.5896 | 30000000 | 819657855.5896
11 | 7 | 3 | 52.6 | 89.7495 | 4.6579 | 0.5 | 771629137.4255 | 50000000 | 821629137.4255
1 | 5 | 5 | 52.6 | 89.1814 | 2.6698 | 0.5 | 784506793.257 | 50000000 | 834506793.257
1 | 26 | 9 | 52.6 | 91.4536 | 2.7834 | 0.5 | 804080830.121 | 50000000 | 854080830.121
1 | 26 | 13 | 52.6 | 92.5896 | 2.7834 | 0.5 | 814382954.7862 | 50000000 | 864382954.7862
1 | 12 | 3 | 52.6 | 93.1577 | 6.7596 | 0.4 | 783476580.7905 | 40000000 | 823476580.7905
1 | 9 | 1 | 52.6 | 90.3175 | 2.7266 | 0.4 | 794293811.689 | 40000000 | 834293811.689
1 | 4 | 15 | 52.6 | 90.8855 | 2.7834 | 0.4 | 798929767.7883 | 40000000 | 838929767.7883
1 | 16 | 23 | 52.6 | 90.8855 | 2.6698 | 0.3 | 799959980.2549 | 30000000 | 829959980.2549
12 | 3 | 12 | 52.6 | 86.9093 | 4.3171 | 0.1 | 748964463.162 | 10000000 | 758964463.162
1 | 5 | 2 | 52.7 | 88.6861 | 2.672 | 0.5 | 779995068.5243 | 50000000 | 829995068.5243
12 | 16 | 13 | 52.7 | 90.3916 | 3.0131 | 0.5 | 792367759.6311 | 50000000 | 842367759.6311
1 | 26 | 7 | 52.7 | 90.9601 | 2.7857 | 0.5 | 799585162.7767 | 50000000 | 849585162.7767
1 | 16 | 2 | 52.7 | 90.9601 | 2.7857 | 0.3 | 799585162.7767 | 30000000 | 829585162.7767
1 | 16 | 22 | 52.7 | 90.3916 | 2.7857 | 0.2 | 794429874.8155 | 20000000 | 814429874.8155
12 | 3 | 14 | 52.7 | 86.9806 | 4.4912 | 0.1 | 748032283.165 | 10000000 | 758032283.165
9 | 16 | 3 | 52.8 | 85.9138 | 3.4138 | 0.4 | 748128150 | 40000000 | 788128150
9 | 16 | 8 | 52.8 | 88.1897 | 3.4138 | 0.4 | 768766167.931 | 40000000 | 808766167.931
11 | 7 | 2 | 52.8 | 89.3276 | 4.6655 | 0.5 | 767734267.0345 | 50000000 | 817734267.0345
12 | 13 | 19 | 52.8 | 87.6207 | 2.8448 | 0.5 | 768766167.931 | 50000000 | 818766167.931
12 | 13 | 21 | 52.8 | 88.1897 | 2.9017 | 0.5 | 773409721.9655 | 50000000 | 823409721.9655
12 | 16 | 22 | 52.8 | 89.3276 | 2.9586 | 0.5 | 783212780.4828 | 50000000 | 833212780.4828
12 | 16 | 23 | 52.8 | 89.3276 | 2.9586 | 0.5 | 783212780.4828 | 50000000 | 833212780.4828
1 | 25 | 6 | 52.8 | 91.0345 | 2.731 | 0.5 | 800755095.7241 | 50000000 | 850755095.7241
1 | 17 | 1 | 52.8 | 91.0345 | 2.7879 | 0.4 | 800239145.2759 | 40000000 | 840239145.2759
1 | 10 | 5 | 52.8 | 92.7414 | 2.7879 | 0.4 | 815717658.7241 | 40000000 | 855717658.7241
1 | 16 | 1 | 52.8 | 90.4655 | 2.7879 | 0.3 | 795079640.7931 | 30000000 | 825079640.7931
1 | 16 | 10 | 52.8 | 90.4655 | 2.731 | 0.3 | 795595591.2414 | 30000000 | 825595591.2414
1 | 16 | 11 | 52.8 | 90.4655 | 2.731 | 0.3 | 795595591.2414 | 30000000 | 825595591.2414
12 | 3 | 19 | 52.8 | 87.6207 | 4.6086 | 0.1 | 752771704.0345 | 10000000 | 762771704.0345
12 | 3 | 21 | 52.8 | 87.6207 | 4.6086 | 0.1 | 752771704.0345 | 10000000 | 762771704.0345
12 | 6 | 23 | 52.8 | 87.6207 | 4.4379 | 0.1 | 754319555.3793 | 10000000 | 764319555.3793
12 | 13 | 18 | 52.9 | 88.2616 | 2.9041 | 0.5 | 774040417.8278 | 50000000 | 824040417.8278
11 | 4 | 23 | 52.9 | 94.5253 | 8.997 | 0.5 | 775589531.4058 | 50000000 | 825589531.4058
12 | 17 | 12 | 52.9 | 89.4004 | 2.961 | 0.5 | 783851470.4887 | 50000000 | 833851470.4887
1 | 16 | 18 | 52.9 | 91.1087 | 2.7902 | 0.5 | 800891719.8471 | 50000000 | 850891719.8471
1 | 16 | 14 | 52.9 | 90.5393 | 2.7902 | 0.4 | 795728007.9203 | 40000000 | 835728007.9203
1 | 9 | 14 | 52.9 | 91.1087 | 2.7333 | 0.4 | 801408091.0398 | 40000000 | 841408091.0398
1 | 6 | 1 | 52.9 | 91.1087 | 2.6763 | 0.4 | 801924462.2325 | 40000000 | 841924462.2325
1 | 16 | 3 | 52.9 | 90.5393 | 2.7902 | 0.3 | 795728007.9203 | 30000000 | 825728007.9203
12 | 5 | 17 | 52.9 | 89.4004 | 4.6124 | 0.2 | 768876705.901 | 20000000 | 788876705.901
12 | 12 | 11 | 52.9 | 88.831 | 2.961 | 0.1 | 778687758.5619 | 10000000 | 788687758.5619
12 | 12 | 9 | 52.9 | 89.4004 | 2.961 | 0.1 | 783851470.4887 | 10000000 | 793851470.4887
9 | 11 | 7 | 53 | 92.8925 | 3.4763 | 0.4 | 810845129.6129 | 40000000 | 850845129.6129
9 | 16 | 6 | 53 | 86.6237 | 3.4194 | 0.4 | 754514907.0968 | 40000000 | 794514907.0968
9 | 2 | 16 | 53 | 94.6022 | 3.7043 | 0.1 | 824281696.4516 | 10000000 | 834281696.4516
1 | 5 | 1 | 53 | 88.9032 | 2.6785 | 0.5 | 781904831.8065 | 50000000 | 831904831.8065
12 | 13 | 15 | 53 | 89.4731 | 2.9634 | 0.5 | 784488786.9677 | 50000000 | 834488786.9677
1 | 29 | 2 | 53 | 91.7527 | 2.9065 | 0.5 | 805677219.2903 | 50000000 | 855677219.2903
12 | 23 | 24 | 53 | 90.6129 | 2.9634 | 0.4 | 794824607.6129 | 40000000 | 834824607.6129
1 | 16 | 5 | 53 | 91.1828 | 2.7925 | 0.3 | 801542891.0323 | 30000000 | 831542891.0323
12 | 7 | 14 | 53 | 88.9032 | 4.4452 | 0.1 | 765884309.8065 | 10000000 | 775884309.8065
12 | 12 | 13 | 53 | 88.9032 | 2.9634 | 0.1 | 779320876.6452 | 10000000 | 789320876.6452
12 | 12 | 23 | 53 | 89.4731 | 3.0204 | 0.1 | 783971995.9355 | 10000000 | 793971995.9355
12 | 12 | 10 | 53 | 89.4731 | 2.9065 | 0.1 | 785005578 | 10000000 | 795005578
11 | 6 | 24 | 53.1 | 89.5456 | 4.6769 | 0.5 | 769608435.2481 | 50000000 | 819608435.2481
12 | 13 | 20 | 53.1 | 87.8346 | 2.9088 | 0.5 | 770125645.218 | 50000000 | 820125645.218
12 | 13 | 16 | 53.1 | 89.5456 | 2.9658 | 0.5 | 785124734.3459 | 50000000 | 835124734.3459
12 | 16 | 14 | 53.1 | 90.116 | 3.0229 | 0.5 | 789779624.0752 | 50000000 | 839779624.0752
1 | 10 | 1 | 53.1 | 90.6864 | 2.7377 | 0.4 | 797537773.6241 | 40000000 | 837537773.6241
1 | 17 | 5 | 53.1 | 91.2567 | 2.7377 | 0.4 | 802709873.3233 | 40000000 | 842709873.3233
1 | 17 | 2 | 53.1 | 91.2567 | 2.7947 | 0.3 | 802192663.3534 | 30000000 | 832192663.3534
12 | 12 | 17 | 53.1 | 88.9753 | 2.9658 | 0.1 | 779952634.6466 | 10000000 | 789952634.6466
9 | 16 | 5 | 53.2 | 86.1931 | 3.4249 | 0.4 | 750560612.4464 | 40000000 | 790560612.4464
10 | 14 | 8 | 53.2 | 91.9013 | 4.2811 | 0.1 | 794558993.176 | 10000000 | 804558993.176
11 | 4 | 17 | 53.2 | 94.1845 | 8.9618 | 0.5 | 772818616.8155 | 50000000 | 822818616.8155
1 | 4 | 24 | 53.2 | 89.0472 | 2.7399 | 0.5 | 782653548.9785 | 50000000 | 832653548.9785
12 | 13 | 14 | 53.2 | 89.618 | 3.0253 | 0.5 | 785241689.0215 | 50000000 | 835241689.0215
12 | 13 | 17 | 53.2 | 89.618 | 3.0253 | 0.5 | 785241689.0215 | 50000000 | 835241689.0215
12 | 16 | 11 | 53.2 | 89.618 | 3.0253 | 0.5 | 785241689.0215 | 50000000 | 835241689.0215
12 | 17 | 9 | 53.2 | 90.1888 | 2.9682 | 0.5 | 790935597.1159 | 50000000 | 840935597.1159
1 | 25 | 4 | 53.2 | 91.3305 | 2.7399 | 0.5 | 803358669.3219 | 50000000 | 853358669.3219
1 | 25 | 5 | 53.2 | 91.3305 | 2.7399 | 0.5 | 803358669.3219 | 50000000 | 853358669.3219
1 | 9 | 15 | 53.2 | 91.3305 | 2.7399 | 0.4 | 803358669.3219 | 40000000 | 843358669.3219
1 | 9 | 13 | 53.2 | 91.9013 | 2.7399 | 0.4 | 808534949.4077 | 40000000 | 848534949.4077
1 | 17 | 4 | 53.2 | 91.3305 | 2.7399 | 0.3 | 803358669.3219 | 30000000 | 833358669.3219
12 | 7 | 7 | 53.2 | 87.9056 | 4.3382 | 0.1 | 757807404.5665 | 10000000 | 767807404.5665
12 | 6 | 1 | 53.2 | 88.4764 | 4.6236 | 0.1 | 760395544.6094 | 10000000 | 770395544.6094
12 | 6 | 24 | 53.2 | 88.4764 | 4.3953 | 0.1 | 762466056.6438 | 10000000 | 772466056.6438
12 | 12 | 14 | 53.2 | 89.618 | 2.9112 | 0.1 | 786276945.0386 | 10000000 | 796276945.0386
9 | 15 | 5 | 53.3 | 90.2615 | 3.4277 | 0.5 | 787428629.7106 | 50000000 | 837428629.7106
9 | 11 | 6 | 53.3 | 93.1179 | 3.4277 | 0.4 | 813330887.2669 | 40000000 | 853330887.2669
9 | 11 | 13 | 53.3 | 92.5466 | 3.4277 | 0.4 | 808150435.7556 | 40000000 | 848150435.7556
11 | 5 | 16 | 53.3 | 90.2615 | 4.5702 | 0.5 | 777067726.6881 | 50000000 | 827067726.6881
12 | 13 | 22 | 53.3 | 89.119 | 2.9135 | 0.5 | 781730133.0482 | 50000000 | 831730133.0482
11 | 5 | 17 | 53.3 | 90.8328 | 4.6273 | 0.5 | 781730133.0482 | 50000000 | 831730133.0482
12 | 13 | 23 | 53.3 | 90.2615 | 2.9706 | 0.5 | 791572990.9196 | 50000000 | 841572990.9196
1 | 3 | 2 | 53.3 | 90.2615 | 2.7992 | 0.5 | 793127126.373 | 50000000 | 843127126.373
1 | 15 | 24 | 53.3 | 90.8328 | 2.7992 | 0.4 | 798307577.8842 | 40000000 | 838307577.8842
1 | 10 | 4 | 53.3 | 91.9753 | 2.7421 | 0.4 | 809186526.0579 | 40000000 | 849186526.0579
1 | 16 | 4 | 53.3 | 90.8328 | 2.7992 | 0.3 | 798307577.8842 | 30000000 | 828307577.8842
1 | 16 | 6 | 53.3 | 90.8328 | 2.7992 | 0.3 | 798307577.8842 | 30000000 | 828307577.8842
12 | 6 | 9 | 53.3 | 85.6913 | 2.7992 | 0.2 | 751683514.283 | 20000000 | 771683514.283
12 | 6 | 12 | 53.3 | 85.6913 | 2.1708 | 0.1 | 757382010.9453 | 10000000 | 767382010.9453
12 | 8 | 6 | 53.3 | 90.2615 | 4.1703 | 0.1 | 780694042.746 | 10000000 | 790694042.746
9 | 15 | 6 | 53.4 | 89.7623 | 3.4304 | 0.5 | 782876714.6467 | 50000000 | 832876714.6467
9 | 16 | 7 | 53.4 | 88.0471 | 3.4304 | 0.4 | 767322872.6338 | 40000000 | 807322872.6338
11 | 4 | 16 | 53.4 | 93.7645 | 8.9762 | 0.5 | 768878256.8351 | 50000000 | 818878256.8351
11 | 7 | 1 | 53.4 | 89.7623 | 4.631 | 0.5 | 771989025.2377 | 50000000 | 821989025.2377
11 | 4 | 18 | 53.4 | 94.9079 | 9.0334 | 0.5 | 778729023.4433 | 50000000 | 828729023.4433
12 | 16 | 10 | 53.4 | 89.1906 | 2.973 | 0.5 | 781839791.8458 | 50000000 | 831839791.8458
12 | 16 | 16 | 53.4 | 89.7623 | 3.0302 | 0.5 | 786505944.4497 | 50000000 | 836505944.4497
12 | 13 | 13 | 53.4 | 89.7623 | 2.973 | 0.5 | 787024405.8501 | 50000000 | 837024405.8501
11 | 5 | 18 | 53.4 | 91.4775 | 4.631 | 0.5 | 787542867.2505 | 50000000 | 837542867.2505
12 | 17 | 7 | 53.4 | 90.334 | 2.973 | 0.5 | 792209019.8544 | 50000000 | 842209019.8544
12 | 17 | 8 | 53.4 | 90.334 | 2.973 | 0.5 | 792209019.8544 | 50000000 | 842209019.8544
11 | 5 | 13 | 53.4 | 92.0493 | 4.5739 | 0.5 | 793245942.6552 | 50000000 | 843245942.6552
11 | 4 | 12 | 53.4 | 96.6231 | 9.0906 | 0.5 | 793764404.0557 | 50000000 | 843764404.0557
1 | 10 | 2 | 53.4 | 90.9058 | 2.7443 | 0.4 | 799467479.4604 | 40000000 | 839467479.4604
1 | 16 | 12 | 53.4 | 91.4775 | 2.8015 | 0.4 | 804133632.0642 | 40000000 | 844133632.0642
12 | 25 | 3 | 53.4 | 93.7645 | 6.7465 | 0.3 | 789098251.4518 | 30000000 | 819098251.4518
1 | 17 | 3 | 53.4 | 91.4775 | 2.7443 | 0.3 | 804652093.4647 | 30000000 | 834652093.4647
12 | 5 | 15 | 53.4 | 88.0471 | 4.631 | 0.2 | 756435183.2248 | 20000000 | 776435183.2248
12 | 6 | 14 | 53.4 | 88.0471 | 4.5739 | 0.1 | 756953644.6253 | 10000000 | 766953644.6253
12 | 6 | 16 | 53.4 | 88.0471 | 4.5739 | 0.1 | 756953644.6253 | 10000000 | 766953644.6253
12 | 12 | 12 | 53.4 | 88.6188 | 2.973 | 0.1 | 776655177.8415 | 10000000 | 786655177.8415
12 | 12 | 15 | 53.4 | 89.1906 | 2.973 | 0.1 | 781839791.8458 | 10000000 | 791839791.8458
9 | 15 | 7 | 53.5 | 89.8342 | 3.4332 | 0.5 | 783503906.631 | 50000000 | 833503906.631
1 | 10 | 3 | 53.5 | 90.9786 | 2.7465 | 0.4 | 800107962.9305 | 40000000 | 840107962.9305
1 | 16 | 8 | 53.5 | 90.9786 | 2.8037 | 0.3 | 799589086.1711 | 30000000 | 829589086.1711
1 | 16 | 9 | 53.5 | 90.9786 | 2.8037 | 0.3 | 799589086.1711 | 30000000 | 829589086.1711
12 | 5 | 16 | 53.5 | 88.6898 | 4.6348 | 0.2 | 762229959.4973 | 20000000 | 782229959.4973
1 | 16 | 7 | 53.5 | 90.9786 | 2.8037 | 0.2 | 799589086.1711 | 20000000 | 819589086.1711
12 | 12 | 6 | 53.5 | 90.4064 | 2.9182 | 0.1 | 793362565.0588 | 10000000 | 803362565.0588
9 | 16 | 4 | 53.6 | 86.4701 | 3.3786 | 0.4 | 753491575.8462 | 40000000 | 793491575.8462
1 | 16 | 15 | 53.6 | 91.6239 | 2.806 | 0.5 | 805420698.9231 | 50000000 | 855420698.9231
1 | 16 | 16 | 53.6 | 91.6239 | 2.806 | 0.5 | 805420698.9231 | 50000000 | 855420698.9231
1 | 16 | 17 | 53.6 | 91.6239 | 2.806 | 0.5 | 805420698.9231 | 50000000 | 855420698.9231
12 | 25 | 5 | 53.6 | 93.9145 | 6.7573 | 0.4 | 790361253.2308 | 40000000 | 830361253.2308
12 | 23 | 23 | 53.6 | 92.7692 | 3.035 | 0.3 | 813729358.6154 | 30000000 | 843729358.6154
12 | 5 | 14 | 53.6 | 88.188 | 4.9248 | 0.2 | 755049449.5385 | 20000000 | 775049449.5385
12 | 6 | 11 | 53.6 | 83.6068 | 0 | 0.2 | 758165196.9231 | 20000000 | 778165196.9231
12 | 7 | 23 | 53.6 | 89.906 | 3.8368 | 0.1 | 780494719.8462 | 10000000 | 790494719.8462
12 | 8 | 5 | 53.6 | 90.4786 | 4.1803 | 0.1 | 782571884.7692 | 10000000 | 792571884.7692
12 | 12 | 8 | 53.6 | 89.906 | 3.035 | 0.1 | 787764797.0769 | 10000000 | 797764797.0769
12 | 12 | 7 | 53.6 | 89.906 | 2.9778 | 0.1 | 788284088.3077 | 10000000 | 798284088.3077
12 | 12 | 24 | 53.6 | 89.906 | 2.9778 | 0.1 | 788284088.3077 | 10000000 | 798284088.3077
9 | 15 | 4 | 53.7 | 90.5507 | 3.4386 | 0.5 | 789951322.6041 | 50000000 | 839951322.6041
10 | 13 | 18 | 53.7 | 91.6969 | 4.1837 | 0.4 | 793589256.3266 | 40000000 | 833589256.3266
11 | 4 | 15 | 53.7 | 93.9893 | 8.9978 | 0.5 | 770722244.3565 | 50000000 | 820722244.3565
11 | 4 | 14 | 53.7 | 93.9893 | 8.9978 | 0.4 | 770722244.3565 | 40000000 | 810722244.3565
1 | 6 | 3 | 53.7 | 92.27 | 2.6936 | 0.4 | 812298629.7567 | 40000000 | 852298629.7567
12 | 25 | 7 | 53.7 | 93.9893 | 6.7626 | 0.3 | 790990732.2391 | 30000000 | 820990732.2391
12 | 6 | 10 | 53.7 | 83.6734 | 0 | 0.2 | 758769033.5539 | 20000000 | 778769033.5539
12 | 5 | 13 | 53.7 | 88.8314 | 5.1006 | 0.1 | 759288738.3714 | 10000000 | 769288738.3714
12 | 4 | 24 | 53.7 | 89.4045 | 5.158 | 0.1 | 763966081.7289 | 10000000 | 773966081.7289
12 | 12 | 16 | 53.7 | 89.9776 | 3.0375 | 0.1 | 788392208.1515 | 10000000 | 798392208.1515
12 | 13 | 7 | 53.7 | 90.5507 | 2.9801 | 0.1 | 794108961.1441 | 10000000 | 804108961.1441
10 | 14 | 7 | 53.8 | 92.3433 | 4.3017 | 0.2 | 798380396.8657 | 20000000 | 818380396.8657
11 | 4 | 13 | 53.8 | 95.2111 | 9.0049 | 0.5 | 781736636.1493 | 50000000 | 831736636.1493
11 | 5 | 14 | 53.8 | 92.3433 | 4.6458 | 0.5 | 795259691.7313 | 50000000 | 845259691.7313
12 | 6 | 13 | 53.8 | 87.7548 | 4.5885 | 0.1 | 754170407.4627 | 10000000 | 764170407.4627
12 | 6 | 15 | 53.8 | 88.3284 | 4.5885 | 0.1 | 759371582.6866 | 10000000 | 769371582.6866
12 | 5 | 9 | 53.8 | 89.4755 | 5.162 | 0.1 | 764572757.9104 | 10000000 | 774572757.9104
12 | 8 | 3 | 53.8 | 90.6226 | 4.187 | 0.1 | 783817106.2388 | 10000000 | 793817106.2388
11 | 5 | 3 | 53.9 | 95.8605 | 9.1268 | 0.5 | 786519845.1949 | 50000000 | 836519845.1949
12 | 17 | 6 | 53.9 | 90.1203 | 2.9849 | 0.5 | 790163550.6326 | 50000000 | 840163550.6326
11 | 5 | 12 | 53.9 | 91.8424 | 4.5921 | 0.5 | 791204609.3291 | 50000000 | 841204609.3291
11 | 5 | 19 | 53.9 | 91.8424 | 4.5921 | 0.5 | 791204609.3291 | 50000000 | 841204609.3291
11 | 5 | 20 | 53.9 | 91.8424 | 4.5347 | 0.5 | 791725138.6773 | 50000000 | 841725138.6773
1 | 26 | 6 | 53.9 | 91.8424 | 2.7553 | 0.5 | 807861548.4728 | 50000000 | 857861548.4728
1 | 6 | 4 | 53.9 | 92.4164 | 2.6979 | 0.4 | 813587371.3035 | 40000000 | 853587371.3035
12 | 5 | 11 | 53.9 | 88.9723 | 5.1661 | 0.1 | 759972848.4345 | 10000000 | 769972848.4345
12 | 5 | 10 | 53.9 | 89.5463 | 5.1661 | 0.1 | 765178141.9169 | 10000000 | 775178141.9169
12 | 5 | 8 | 53.9 | 89.5463 | 5.1087 | 0.1 | 765698671.2652 | 10000000 | 775698671.2652
12 | 8 | 4 | 53.9 | 90.6944 | 4.1903 | 0.1 | 784437727.8019 | 10000000 | 794437727.8019
10 | 14 | 6 | 54 | 92.4894 | 4.3085 | 0.2 | 799643357.234 | 20000000 | 819643357.234
11 | 5 | 15 | 54 | 91.3404 | 4.6532 | 0.5 | 786098909.4894 | 50000000 | 836098909.4894
1 | 29 | 3 | 54 | 92.4894 | 2.9872 | 0.5 | 811624984.0851 | 50000000 | 861624984.0851
12 | 25 | 4 | 54 | 94.2128 | 6.7787 | 0.4 | 792871133.3617 | 40000000 | 832871133.3617
12 | 25 | 8 | 54 | 94.2128 | 6.7787 | 0.4 | 792871133.3617 | 40000000 | 832871133.3617
12 | 25 | 10 | 54 | 94.7872 | 7.0085 | 0.4 | 795996775.1489 | 40000000 | 835996775.1489
1 | 6 | 5 | 54 | 92.4894 | 2.7 | 0.4 | 814229685.5745 | 40000000 | 854229685.5745
12 | 13 | 5 | 54 | 90.766 | 3.0447 | 0.1 | 795475834.8511 | 10000000 | 805475834.8511
10 | 13 | 15 | 54.1 | 92.5622 | 4.3119 | 0.4 | 800272824.1977 | 40000000 | 840272824.1977
12 | 16 | 24 | 54.1 | 90.2625 | 3.0471 | 0.5 | 790888517.4644 | 50000000 | 840888517.4644
11 | 4 | 11 | 54.1 | 97.7365 | 9.1987 | 0.5 | 802879576.068 | 50000000 | 852879576.068
12 | 25 | 6 | 54.1 | 94.2869 | 6.7841 | 0.4 | 793495269.3348 | 40000000 | 833495269.3348
1 | 6 | 6 | 54.1 | 93.712 | 2.7596 | 0.4 | 824776291.779 | 40000000 | 864776291.779
12 | 8 | 1 | 54.1 | 90.8374 | 4.1394 | 0.1 | 786196364.0978 | 10000000 | 796196364.0978
12 | 13 | 6 | 54.1 | 90.8374 | 2.9896 | 0.1 | 796623371.5792 | 10000000 | 806623371.5792
7 | 14 | 8 | 54.1 | 89.1126 | 0 | 0.5 | 808093079.8087 | 50000000 | 858093079.8087
10 | 13 | 16 | 54.2 | 92.0594 | 4.2002 | 0.4 | 796726878.0764 | 40000000 | 836726878.0764
9 | 2 | 9 | 54.2 | 95.5117 | 3.6824 | 0.1 | 832728289.0701 | 10000000 | 842728289.0701
12 | 5 | 1 | 54.2 | 89.1826 | 5.1783 | 0.1 | 761768986.242 | 10000000 | 771768986.242
12 | 7 | 6 | 54.2 | 89.1826 | 4.3728 | 0.1 | 769073620.3567 | 10000000 | 779073620.3567
12 | 8 | 2 | 54.2 | 90.9087 | 4.2002 | 0.1 | 786291686.4841 | 10000000 | 796291686.4841
12 | 13 | 2 | 54.2 | 90.3333 | 3.0495 | 0.1 | 791509282.2803 | 10000000 | 801509282.2803
12 | 13 | 4 | 54.2 | 90.9087 | 2.9919 | 0.1 | 797248637.6561 | 10000000 | 807248637.6561
10 | 13 | 17 | 54.3 | 92.1315 | 4.2035 | 0.4 | 797350409.6946 | 40000000 | 837350409.6946
9 | 2 | 8 | 54.3 | 94.4348 | 3.6853 | 0.1 | 822936637.6416 | 10000000 | 832936637.6416
11 | 5 | 21 | 54.3 | 92.7073 | 4.549 | 0.5 | 799439081.3637 | 50000000 | 849439081.3637
12 | 7 | 24 | 54.3 | 90.404 | 4.0308 | 0.1 | 783251875.9279 | 10000000 | 793251875.9279
12 | 17 | 1 | 54.4 | 90.4746 | 2.9966 | 0.5 | 793269441.7627 | 50000000 | 843269441.7627
1 | 26 | 5 | 54.4 | 92.2034 | 2.7661 | 0.5 | 811037005.0169 | 50000000 | 861037005.0169
12 | 5 | 2 | 54.4 | 89.322 | 5.1864 | 0.1 | 762960069.1525 | 10000000 | 772960069.1525
12 | 5 | 12 | 54.4 | 89.322 | 5.1288 | 0.1 | 763482644.5424 | 10000000 | 773482644.5424
10 | 14 | 2 | 54.5 | 92.8519 | 4.3831 | 0.2 | 802254388 | 20000000 | 822254388
12 | 17 | 3 | 54.5 | 90.545 | 2.9989 | 0.5 | 793886676 | 50000000 | 843886676
12 | 5 | 4 | 54.5 | 89.3915 | 5.2481 | 0.1 | 763030738 | 10000000 | 773030738
12 | 5 | 3 | 54.5 | 89.3915 | 5.1905 | 0.1 | 763553720 | 10000000 | 773553720
12 | 5 | 5 | 54.5 | 89.9683 | 5.2481 | 0.1 | 768260558 | 10000000 | 778260558
12 | 13 | 1 | 54.5 | 91.1217 | 2.9989 | 0.1 | 799116496 | 10000000 | 809116496
12 | 13 | 3 | 54.5 | 91.1217 | 2.9989 | 0.1 | 799116496 | 10000000 | 809116496
11 | 5 | 11 | 54.6 | 91.7696 | 4.6173 | 0.5 | 790315503.2981 | 50000000 | 840315503.2981
12 | 17 | 2 | 54.6 | 90.6152 | 3.0013 | 0.5 | 794502605.3023 | 50000000 | 844502605.3023
12 | 17 | 4 | 54.6 | 90.6152 | 3.0013 | 0.5 | 794502605.3023 | 50000000 | 844502605.3023
12 | 13 | 24 | 54.6 | 91.1924 | 3.0013 | 0.5 | 799736482.8076 | 50000000 | 849736482.8076
1 | 6 | 7 | 54.6 | 94.6554 | 2.8281 | 0.4 | 832709911.0909 | 40000000 | 872709911.0909
12 | 5 | 6 | 54.6 | 90.0381 | 5.1945 | 0.1 | 769379993.277 | 10000000 | 779379993.277
7 | 14 | 7 | 54.6 | 89.4609 | 0 | 0.5 | 811251013.3192 | 50000000 | 861251013.3192
12 | 21 | 10 | 54.7 | 92.9958 | 3.0036 | 0.5 | 816068939.5692 | 50000000 | 866068939.5692
12 | 5 | 7 | 54.7 | 89.5301 | 5.1985 | 0.1 | 764737260.4435 | 10000000 | 774737260.4435
12 | 6 | 5 | 54.7 | 89.5301 | 4.6209 | 0.1 | 769975186.8849 | 10000000 | 779975186.8849
12 | 15 | 24 | 54.8 | 90.1772 | 3.0637 | 0.5 | 789964402.1013 | 50000000 | 839964402.1013
12 | 16 | 9 | 54.8 | 90.1772 | 3.0637 | 0.5 | 789964402.1013 | 50000000 | 839964402.1013
12 | 6 | 6 | 54.8 | 89.5992 | 4.6823 | 0.1 | 770044928.1266 | 10000000 | 780044928.1266
12 | 7 | 2 | 54.8 | 89.5992 | 4.3932 | 0.1 | 772665911.5443 | 10000000 | 782665911.5443
10 | 14 | 3 | 54.9 | 93.1391 | 4.3388 | 0.3 | 805260802.666 | 30000000 | 835260802.666
12 | 6 | 8 | 54.9 | 89.0896 | 4.628 | 0.2 | 765915812.3077 | 20000000 | 785915812.3077
12 | 6 | 2 | 54.9 | 89.6681 | 4.6859 | 0.1 | 770637211.1507 | 10000000 | 780637211.1507
12 | 7 | 1 | 54.9 | 89.6681 | 4.3966 | 0.1 | 773260210.5079 | 10000000 | 783260210.5079
7 | 14 | 5 | 54.9 | 89.6681 | 0 | 0.5 | 813129800.7376 | 50000000 | 863129800.7376
7 | 14 | 6 | 54.9 | 89.6681 | 0 | 0.5 | 813129800.7376 | 50000000 | 863129800.7376
10 | 14 | 4 | 55 | 93.2105 | 4.4 | 0.3 | 805353390.9474 | 30000000 | 835353390.9474
11 | 5 | 2 | 55 | 96.6842 | 9.2053 | 0.5 | 793278340.1053 | 50000000 | 843278340.1053
12 | 7 | 3 | 55 | 89.7368 | 4.4 | 0.1 | 773853258.3158 | 10000000 | 783853258.3158
12 | 7 | 5 | 55 | 89.7368 | 4.4 | 0.1 | 773853258.3158 | 10000000 | 783853258.3158
10 | 14 | 5 | 55.1 | 93.2818 | 4.3454 | 0.3 | 806494684.8265 | 30000000 | 836494684.8265
12 | 6 | 3 | 55.1 | 89.8055 | 4.6931 | 0.1 | 771818040.3975 | 10000000 | 781818040.3975
12 | 14 | 6 | 55.2 | 91.6134 | 3.0731 | 0.5 | 802903246.9412 | 50000000 | 852903246.9412
12 | 6 | 7 | 55.2 | 89.2941 | 4.6966 | 0.1 | 767148550.9412 | 10000000 | 777148550.9412
12 | 6 | 4 | 55.2 | 89.8739 | 4.6966 | 0.1 | 772406594.4706 | 10000000 | 782406594.4706
12 | 7 | 4 | 55.2 | 89.8739 | 4.4067 | 0.1 | 775035616.2353 | 10000000 | 785035616.2353
11 | 5 | 1 | 55.3 | 96.9056 | 9.1683 | 0.5 | 795620692.3316 | 50000000 | 845620692.3316
11 | 5 | 22 | 55.3 | 95.745 | 4.7582 | 0.5 | 825088125.3809 | 50000000 | 875088125.3809
12 | 16 | 1 | 55.4 | 91.7526 | 3.1358 | 0.5 | 803596379.5472 | 50000000 | 853596379.5472
12 | 16 | 7 | 55.5 | 90.6597 | 3.0801 | 0.5 | 794190909.3927 | 50000000 | 844190909.3927
12 | 16 | 2 | 55.5 | 91.2408 | 3.1382 | 0.5 | 798933920.7958 | 50000000 | 848933920.7958
11 | 6 | 11 | 55.5 | 92.9843 | 4.5911 | 0.5 | 801568927.1309 | 50000000 | 851568927.1309
12 | 21 | 2 | 55.5 | 93.5654 | 2.9639 | 0.5 | 821594975.2775 | 50000000 | 871594975.2775
12 | 14 | 4 | 55.6 | 91.8912 | 3.0243 | 0.5 | 805865013.4895 | 50000000 | 855865013.4895
12 | 16 | 8 | 55.7 | 90.7962 | 3.0847 | 0.5 | 795387126.4138 | 50000000 | 845387126.4138
12 | 16 | 3 | 55.7 | 91.3783 | 3.1429 | 0.5 | 800137281.7806 | 50000000 | 850137281.7806
12 | 14 | 5 | 55.7 | 91.9603 | 3.0847 | 0.5 | 805943027.2288 | 50000000 | 855943027.2288
12 | 14 | 2 | 55.8 | 92.0292 | 3.0288 | 0.5 | 807075366.3132 | 50000000 | 857075366.3132
12 | 14 | 3 | 55.8 | 92.0292 | 3.0288 | 0.5 | 807075366.3132 | 50000000 | 857075366.3132
11 | 6 | 4 | 55.8 | 95.524 | 4.7762 | 0.5 | 822921086.8559 | 50000000 | 872921086.8559
11 | 6 | 13 | 55.8 | 93.1942 | 4.5432 | 0.4 | 803906222.2046 | 40000000 | 843906222.2046
11 | 6 | 10 | 55.9 | 93.8467 | 4.6632 | 0.5 | 808735820.5839 | 50000000 | 858735820.5839
11 | 6 | 12 | 55.9 | 93.8467 | 4.4883 | 0.5 | 810321577.0949 | 50000000 | 860321577.0949
12 | 16 | 4 | 56.1 | 91.6514 | 3.1523 | 0.5 | 802528977.3902 | 50000000 | 852528977.3902
11 | 6 | 5 | 56.1 | 95.154 | 4.7869 | 0.5 | 819468903.0343 | 50000000 | 869468903.0343
11 | 5 | 23 | 56.2 | 95.2245 | 4.7904 | 0.5 | 820076274.711 | 50000000 | 870076274.711
12 | 16 | 6 | 56.3 | 91.2025 | 3.0985 | 0.5 | 798945965.215 | 50000000 | 848945965.215
12 | 16 | 5 | 56.3 | 91.7871 | 3.0985 | 0.5 | 804247531.0093 | 50000000 | 854247531.0093
12 | 14 | 1 | 56.3 | 92.3718 | 3.0401 | 0.5 | 810079253.3832 | 50000000 | 860079253.3832
11 | 6 | 6 | 56.3 | 95.2949 | 4.794 | 0.5 | 820682384.972 | 50000000 | 870682384.972
11 | 6 | 7 | 56.4 | 95.3651 | 4.739 | 0.5 | 821817785.0539 | 50000000 | 871817785.0539
11 | 6 | 8 | 56.5 | 94.2642 | 4.7425 | 0.5 | 811803029.5026 | 50000000 | 861803029.5026
11 | 6 | 9 | 56.7 | 94.4023 | 4.7494 | 0.5 | 812991711.6298 | 50000000 | 862991711.6298
6 | 6 | 3 | 56.7 | 93.2296 | 3.049 | 0.5 | 817777143.5491 | 50000000 | 867777143.5491
6 | 6 | 4 | 56.7 | 93.2296 | 3.049 | 0.5 | 817777143.5491 | 50000000 | 867777143.5491
11 | 6 | 2 | 56.8 | 95.6446 | 4.8116 | 0.5 | 823694151.8678 | 50000000 | 873694151.8678
11 | 6 | 3 | 56.8 | 95.6446 | 4.8116 | 0.5 | 823694151.8678 | 50000000 | 873694151.8678
6 | 7 | 4 | 56.9 | 95.1269 | 3.0535 | 0.5 | 834942552.9659 | 50000000 | 884942552.9659
7 | 10 | 5 | 57.2 | 80.6214 | 0 | 0.4 | 731092584.4444 | 40000000 | 771092584.4444
11 | 5 | 24 | 57.3 | 95.9908 | 4.829 | 0.5 | 826674965.3525 | 50000000 | 876674965.3525
11 | 6 | 1 | 57.5 | 96.1282 | 4.8359 | 0.5 | 827858730.4615 | 50000000 | 877858730.4615
6 | 6 | 6 | 57.6 | 93.8361 | 3.0689 | 0.5 | 823097057.3115 | 50000000 | 873097057.3115
6 | 25 | 5 | 57.8 | 85.6953 | 0 | 0.5 | 777103801.8405 | 50000000 | 827103801.8405
6 | 16 | 2 | 57.9 | 94.6272 | 0 | 0.5 | 858100000.8172 | 50000000 | 908100000.8172
10 | 12 | 6 | 58.2 | 98.3829 | 4.5043 | 0.5 | 851311934.7617 | 50000000 | 901311934.7617
6 | 7 | 3 | 58.2 | 96.0122 | 3.2004 | 0.5 | 841637935.5031 | 50000000 | 891637935.5031
10 | 12 | 5 | 58.3 | 97.8586 | 4.5074 | 0.5 | 846528945.8026 | 50000000 | 896528945.8026
6 | 16 | 5 | 58.3 | 96.6724 | 0 | 0.5 | 876646875.2594 | 50000000 | 926646875.2594
6 | 7 | 2 | 58.6 | 95.6856 | 3.2093 | 0.5 | 838595140.7221 | 50000000 | 888595140.7221
7 | 13 | 23 | 59 | 96.5455 | 0 | 0.4 | 875495421.8182 | 40000000 | 915495421.8182
7 | 13 | 20 | 59.1 | 96.0151 | 0 | 0.4 | 870686378.6276 | 40000000 | 910686378.6276
7 | 13 | 22 | 59.4 | 96.8089 | 0 | 0.4 | 877883978.0282 | 40000000 | 917883978.0282
6 | 5 | 6 | 60.1 | 92.4615 | 3.1821 | 0.5 | 809605427.2867 | 50000000 | 859605427.2867
6 | 5 | 5 | 60.3 | 82.3639 | 2.7054 | 0.5 | 722361024.3769 | 50000000 | 772361024.3769
7 | 22 | 5 | 61.6 | 93.9764 | 0 | 0.5 | 852198470.0787 | 50000000 | 902198470.0787
7 | 22 | 6 | 62.1 | 94.8834 | 0 | 0.5 | 860423977.1988 | 50000000 | 910423977.1988
7 | 11 | 18 | 62.6 | 89.6901 | 0 | 0.3 | 813329182.1053 | 30000000 | 843329182.1053
7 | 11 | 21 | 62.6 | 90.3002 | 0 | 0.3 | 818862033.6842 | 30000000 | 848862033.6842
7 | 20 | 5 | 62.8 | 97.1323 | 0 | 0.5 | 880817026.6926 | 50000000 | 930817026.6926
7 | 11 | 20 | 62.8 | 89.8016 | 0 | 0.3 | 814340269.9611 | 30000000 | 844340269.9611
7 | 28 | 5 | 62.8 | 96.5214 | 0 | 0.3 | 875277296.965 | 30000000 | 905277296.965
7 | 13 | 4 | 63 | 85.0194 | 0 | 0.5 | 770974781.9417 | 50000000 | 820974781.9417
7 | 11 | 19 | 63.2 | 90.6357 | 0 | 0.3 | 821904094.8837 | 30000000 | 851904094.8837
7 | 28 | 4 | 63.4 | 96.265 | 0 | 0.3 | 872952110.5996 | 30000000 | 902952110.5996
7 | 10 | 22 | 66 | 92.1509 | 0 | 0.2 | 835645027.9245 | 20000000 | 855645027.9245
7 | 10 | 23 | 66.6 | 93.0901 | 0 | 0.2 | 844161110.2064 | 20000000 | 864161110.2064
9 | 8 | 13 | 67.5 | 111.1395 | 3.893 | 0.4 | 972534961.6744 | 40000000 | 1012534961.6744
9 | 8 | 14 | 67.8 | 110.6939 | 3.8994 | 0.4 | 968435423.5325 | 40000000 | 1008435423.5325
9 | 8 | 15 | 67.9 | 112.013 | 3.9645 | 0.5 | 979807303.9351 | 50000000 | 1029807303.9351
9 | 8 | 12 | 68.2 | 111.5656 | 3.971 | 0.4 | 975691862.3179 | 40000000 | 1015691862.3179
9 | 8 | 11 | 68.3 | 111.626 | 3.9731 | 0.4 | 976220258.7091 | 40000000 | 1016220258.7091
9 | 8 | 10 | 68.7 | 111.8666 | 3.9817 | 0.4 | 978324122.1693 | 40000000 | 1018324122.1693
9 | 8 | 9 | 69.3 | 112.2242 | 4.1212 | 0.4 | 980301131.226 | 40000000 | 1020301131.226
12 | 5 | 19 | 80 | 124 | 5.7333 | 0.1 | 1072468152 | 10000000 | 1082468152
12 | 5 | 21 | 80.6 | 124.9768 | 5.2798 | 0.1 | 1085438864.6866 | 10000000 | 1095438864.6866
12 | 5 | 20 | 80.7 | 125.0282 | 5.2819 | 0.1 | 1085885160.7407 | 10000000 | 1095885160.7407
1 | 4 | 18 | 86.5 | 133.3399 | 3.966 | 0.5 | 1173191105.7391 | 50000000 | 1223191105.7391
6 | 27 | 6 | 107.9 | 153.2049 | 0 | 0.4 | 1389295449.4929 | 40000000 | 1429295449.4929
6 | 27 | 5 | 107.9 | 154.664 | 0 | 0.3 | 1402526834.7262 | 30000000 | 1432526834.7262
10 | 12 | 8 | 111.4 | 166.2906 | 6.9165 | 0.5 | 1445239476.5707 | 50000000 | 1495239476.5707
6 | 26 | 1 | 112 | 165.0526 | 0 | 0.2 | 1496733574.7368 | 20000000 | 1516733574.7368
6 | 26 | 2 | 112.2 | 165.1301 | 0 | 0.3 | 1497436002.7332 | 30000000 | 1527436002.7332
6 | 26 | 3 | 112.2 | 165.1301 | 0 | 0.3 | 1497436002.7332 | 30000000 | 1527436002.7332
6 | 25 | 24 | 112.4 | 164.4698 | 0 | 0.3 | 1491448477.3228 | 30000000 | 1521448477.3228
7 | 9 | 20 | 112.8 | 139.5236 | 0 | 0.5 | 1265230339.1623 | 50000000 | 1315230339.1623
12 | 16 | 18 | 120 | 166.5 | 4.2 | 0.5 | 1471772106 | 50000000 | 1521772106
1 | 19 | 19 | 122.1 | 176.2579 | 4.0675 | 0.5 | 1561460214.2702 | 50000000 | 1611460214.2702
7 | 16 | 1 | 129.3 | 167.2575 | 0 | 0.5 | 1516728087.8559 | 50000000 | 1566728087.8559
7 | 20 | 1 | 130.6 | 173.0106 | 0 | 0.5 | 1568897738.7573 | 50000000 | 1618897738.7573
7 | 20 | 2 | 132 | 174.2093 | 0 | 0.5 | 1579768279.5349 | 50000000 | 1629768279.5349
12 | 7 | 19 | 134.7 | 181.9645 | 6.3996 | 0.1 | 1592061239.7355 | 10000000 | 1602061239.7355
12 | 7 | 18 | 135 | 182.8286 | 6.6343 | 0.1 | 1597768545.6 | 10000000 | 1607768545.6
6 | 30 | 15 | 157.7 | 210.5857 | 0 | 0.4 | 1909637782.5797 | 40000000 | 1949637782.5797
6 | 23 | 5 | 157.8 | 211.4105 | 0 | 0.4 | 1917117066.4307 | 40000000 | 1957117066.4307
6 | 30 | 17 | 157.8 | 211.4105 | 0 | 0.4 | 1917117066.4307 | 40000000 | 1957117066.4307
6 | 5 | 20 | 157.9 | 210.6397 | 4.7075 | 0.5 | 1867438843.8494 | 50000000 | 1917438843.8494
1 | 10 | 7 | 158 | 217.0505 | 4.9475 | 0.5 | 1923396941.4546 | 50000000 | 1973396941.4546
6 | 30 | 16 | 158.2 | 211.5187 | 0 | 0.4 | 1918097815.6408 | 40000000 | 1958097815.6408
6 | 30 | 18 | 159 | 211.7337 | 0 | 0.4 | 1920047485.9297 | 40000000 | 1960047485.9297
6 | 3 | 5 | 159.7 | 215.9189 | 5.0381 | 0.4 | 1912313226.6189 | 40000000 | 1952313226.6189
6 | 3 | 6 | 159.8 | 215.9459 | 4.9588 | 0.4 | 1913278230.5946 | 40000000 | 1953278230.5946
6 | 23 | 2 | 160 | 213.6 | 0 | 0.4 | 1936971792 | 40000000 | 1976971792
6 | 3 | 3 | 160.1 | 214.4268 | 4.9606 | 0.4 | 1899485284.1559 | 40000000 | 1939485284.1559
6 | 3 | 4 | 160.2 | 215.2537 | 5.0413 | 0.4 | 1906253083.5105 | 40000000 | 1946253083.5105
6 | 23 | 1 | 161 | 216.2687 | 0 | 0.4 | 1961171758.209 | 40000000 | 2001171758.209
6 | 30 | 10 | 161.4 | 213.9712 | 0 | 0.4 | 1940337929.6723 | 40000000 | 1980337929.6723
7 | 25 | 8 | 161.5 | 209.1886 | 0 | 0.3 | 1896968115.7816 | 30000000 | 1926968115.7816
6 | 7 | 6 | 162.8 | 223.1677 | 4.8968 | 0.5 | 1979327712.6746 | 50000000 | 2029327712.6746
7 | 30 | 2 | 164 | 211.4314 | 0 | 0.3 | 1917306201.1765 | 30000000 | 1947306201.1765
6 | 9 | 5 | 164.7 | 222.0674 | 4.3448 | 0.3 | 1974356603.2262 | 30000000 | 2004356603.2262
7 | 31 | 4 | 165.1 | 211.7079 | 0 | 0.4 | 1919814242.2526 | 40000000 | 1959814242.2526
7 | 9 | 18 | 165.6 | 190.0856 | 0 | 0.5 | 1723738067.8599 | 50000000 | 1773738067.8599
7 | 23 | 4 | 165.8 | 214.2993 | 0 | 0.3 | 1943313377.1429 | 30000000 | 1973313377.1429
7 | 23 | 6 | 166.1 | 214.3746 | 0 | 0.4 | 1943995812.5764 | 40000000 | 1983995812.5764
7 | 23 | 3 | 166.1 | 214.3746 | 0 | 0.3 | 1943995812.5764 | 30000000 | 1973995812.5764
7 | 9 | 17 | 166.3 | 191.0475 | 0 | 0.5 | 1732460793.4174 | 50000000 | 1782460793.4174
7 | 23 | 5 | 166.3 | 214.4246 | 0 | 0.3 | 1944449666.8735 | 30000000 | 1974449666.8735
7 | 29 | 6 | 168.6 | 214.185 | 0 | 0.3 | 1942277091.9463 | 30000000 | 1972277091.9463
7 | 19 | 5 | 171.5 | 213.26 | 0 | 0.4 | 1933889025.9574 | 40000000 | 1973889025.9574
7 | 1 | 17 | 194.8 | 256.3595 | 0 | 0.4 | 2324723935.707 | 40000000 | 2364723935.707
7 | 1 | 18 | 196.2 | 256.6715 | 0 | 0.4 | 2327553311.0754 | 40000000 | 2367553311.0754
9 | 9 | 18 | 199.7 | 264.9337 | 5.4986 | 0.5 | 2352614052.9312 | 50000000 | 2402614052.9312
7 | 5 | 11 | 202 | 262.9339 | 0 | 0.4 | 2384342308.2645 | 40000000 | 2424342308.2645
7 | 5 | 17 | 202.2 | 267.1511 | 0 | 0.5 | 2422585082.0809 | 50000000 | 2472585082.0809
7 | 5 | 16 | 203.4 | 266.576 | 0 | 0.5 | 2417369874.3303 | 50000000 | 2467369874.3303
7 | 5 | 15 | 205.2 | 266.9608 | 0 | 0.5 | 2420859703.6542 | 50000000 | 2470859703.6542
7 | 4 | 7 | 205.4 | 260.3073 | 0 | 0.5 | 2360523442.0049 | 50000000 | 2410523442.0049
7 | 4 | 6 | 205.8 | 260.3897 | 0 | 0.5 | 2361271518.454 | 50000000 | 2411271518.454
7 | 5 | 14 | 206 | 267.1301 | 0 | 0.5 | 2422394345.8537 | 50000000 | 2472394345.8537
7 | 5 | 12 | 206.1 | 266.3137 | 0 | 0.5 | 2414991162.7631 | 50000000 | 2464991162.7631
7 | 5 | 13 | 206.6 | 267.2563 | 0 | 0.5 | 2423538793.1387 | 50000000 | 2473538793.1387
7 | 3 | 1 | 207.3 | 266.5645 | 0 | 0.4 | 2417265499.0214 | 40000000 | 2457265499.0214
7 | 3 | 3 | 207.4 | 265.747 | 0 | 0.5 | 2409851974.4382 | 50000000 | 2459851974.4382
7 | 4 | 5 | 207.5 | 263.2525 | 0 | 0.5 | 2387231814.5455 | 50000000 | 2437231814.5455
7 | 3 | 2 | 207.6 | 267.4653 | 0 | 0.4 | 2425433879.5153 | 40000000 | 2465433879.5153
7 | 10 | 17 | 208.9 | 233.3234 | 0 | 0.4 | 2115828131.4745 | 40000000 | 2155828131.4745
7 | 10 | 16 | 209.1 | 234.1987 | 0 | 0.4 | 2123765474.7411 | 40000000 | 2163765474.7411
7 | 10 | 15 | 209.2 | 234.2167 | 0 | 0.4 | 2123928503.5955 | 40000000 | 2163928503.5955
7 | 5 | 5 | 210.1 | 263.7801 | 0 | 0.4 | 2392015869.2843 | 40000000 | 2432015869.2843
7 | 10 | 13 | 210.3 | 235.2537 | 0 | 0.4 | 2133332267.1994 | 40000000 | 2173332267.1994
7 | 10 | 14 | 210.4 | 235.2716 | 0 | 0.4 | 2133494315.6549 | 40000000 | 2173494315.655
6 | 30 | 21 | 213.1 | 277.0047 | 0 | 0.4 | 2511939934.3264 | 40000000 | 2551939934.3264
7 | 1 | 2 | 214.4 | 274.7421 | 0 | 0.4 | 2491422153.9623 | 40000000 | 2531422153.9623
7 | 10 | 18 | 218.3 | 245.091 | 0 | 0.4 | 2222538921.9512 | 40000000 | 2262538921.9512
7 | 24 | 9 | 221.8 | 273.6494 | 0 | 0.4 | 2481512514.5455 | 40000000 | 2521512514.5455
6 | 26 | 19 | 224 | 290.1818 | 0 | 0.5 | 2631432567.2727 | 50000000 | 2681432567.2727
6 | 26 | 21 | 225 | 290.3774 | 0 | 0.5 | 2633205769.8113 | 50000000 | 2683205769.8113
6 | 26 | 20 | 225.3 | 290.4357 | 0 | 0.5 | 2633735123.905 | 50000000 | 2683735123.905
6 | 27 | 1 | 225.3 | 287.8881 | 0 | 0.4 | 2610632184.2216 | 40000000 | 2650632184.2216
6 | 26 | 24 | 226 | 292.2707 | 0 | 0.4 | 2650374795.7895 | 40000000 | 2690374795.7895
6 | 26 | 23 | 226.3 | 292.329 | 0 | 0.5 | 2650903251.9114 | 50000000 | 2700903251.9114
7 | 12 | 16 | 228.4 | 255.2906 | 0 | 0.4 | 2315031424.7392 | 40000000 | 2355031424.7392
7 | 12 | 15 | 228.5 | 254.4562 | 0 | 0.4 | 2307465149.8324 | 40000000 | 2347465149.8324
7 | 12 | 17 | 228.6 | 254.4728 | 0 | 0.4 | 2307615534.2815 | 40000000 | 2347615534.2815
7 | 12 | 18 | 229.9 | 254.6873 | 0 | 0.4 | 2309560391.3375 | 40000000 | 2349560391.3375
7 | 12 | 19 | 230.7 | 254.8182 | 0 | 0.4 | 2310747941.8027 | 40000000 | 2350747941.8027
7 | 12 | 21 | 230.7 | 255.6705 | 0 | 0.4 | 2318476195.7887 | 40000000 | 2358476195.7887
7 | 12 | 20 | 230.9 | 254.8509 | 0 | 0.4 | 2311043733.4884 | 40000000 | 2351043733.4884
7 | 12 | 22 | 230.9 | 255.7032 | 0 | 0.4 | 2318772976.7442 | 40000000 | 2358772976.7442
8 | 23 | 11 | 248.9 | 318.7712 | 12.5785 | 0.1 | 2776622419.7757 | 10000000 | 2786622419.7757
6 | 28 | 1 | 260.4 | 321.5992 | 0 | 0.5 | 2916332307.0839 | 50000000 | 2966332307.0839
6 | 17 | 9 | 260.6 | 335.503 | 0 | 0.5 | 3042414960.3593 | 50000000 | 3092414960.3593
6 | 28 | 2 | 260.6 | 321.6321 | 0 | 0.5 | 2916630362.515 | 50000000 | 2966630362.515
6 | 17 | 10 | 261.4 | 335.6397 | 0 | 0.5 | 3043654472.4486 | 50000000 | 3093654472.4486
7 | 19 | 22 | 264.3 | 320.4952 | 0 | 0.4 | 2906321299.6188 | 40000000 | 2946321299.6188
7 | 19 | 21 | 265.2 | 319.7693 | 0 | 0.4 | 2899738648.0734 | 40000000 | 2939738648.0734
7 | 21 | 22 | 265.8 | 319.864 | 0 | 0.5 | 2900596789.9542 | 50000000 | 2950596789.9542
7 | 22 | 23 | 266 | 317.2876 | 0 | 0.4 | 2877233594.1177 | 40000000 | 2917233594.1177
7 | 21 | 21 | 266.2 | 319.9268 | 0 | 0.5 | 2901167016.1724 | 50000000 | 2951167016.1724
7 | 21 | 20 | 267.1 | 320.0677 | 0 | 0.5 | 2902444593.9954 | 50000000 | 2952444593.9954
7 | 21 | 12 | 267.6 | 321.0156 | 0 | 0.5 | 2911040126.684 | 50000000 | 2961040126.684
7 | 19 | 20 | 267.9 | 321.9324 | 0 | 0.4 | 2919354241.8318 | 40000000 | 2959354241.8318
7 | 21 | 11 | 268.4 | 321.1401 | 0 | 0.5 | 2912168876.4981 | 50000000 | 2962168876.4981
7 | 21 | 10 | 268.8 | 322.0725 | 0 | 0.5 | 2920624638.342 | 50000000 | 2970624638.342
7 | 21 | 13 | 268.8 | 322.0725 | 0 | 0.5 | 2920624638.342 | 50000000 | 2970624638.342
7 | 21 | 9 | 269.5 | 322.1809 | 0 | 0.5 | 2921607616.4782 | 50000000 | 2971607616.4782
6 | 6 | 18 | 271.4 | 344.2614 | 5.1421 | 0.5 | 3075208126.8555 | 50000000 | 3125208126.8555
7 | 20 | 22 | 273.4 | 333.2444 | 0 | 0.5 | 3021933678.8003 | 50000000 | 3071933678.8003
7 | 20 | 21 | 273.8 | 333.3066 | 0 | 0.5 | 3022497256.0612 | 50000000 | 3072497256.0612
7 | 20 | 20 | 274.2 | 332.4959 | 0 | 0.5 | 3015145630.3119 | 50000000 | 3065145630.3119
7 | 20 | 19 | 274.3 | 331.6386 | 0 | 0.5 | 3007371439.6437 | 50000000 | 3057371439.6437
7 | 18 | 4 | 279.1 | 325.3688 | 0 | 0.5 | 2950516311.9524 | 50000000 | 3000516311.9524
7 | 3 | 22 | 284 | 350.6173 | 0 | 0.5 | 3179474666.6667 | 50000000 | 3229474666.6667
7 | 3 | 17 | 284.3 | 350.663 | 0 | 0.5 | 3179888925.0694 | 50000000 | 3229888925.0694
7 | 3 | 18 | 284.4 | 351.5549 | 0 | 0.5 | 3187976908.0395 | 50000000 | 3237976908.0395
7 | 3 | 21 | 284.5 | 350.6934 | 0 | 0.5 | 3180164671.8028 | 50000000 | 3230164671.8028
7 | 3 | 23 | 284.8 | 350.7389 | 0 | 0.5 | 3180577655.1724 | 50000000 | 3230577655.1724
7 | 3 | 20 | 285 | 350.7692 | 0 | 0.5 | 3180852553.8461 | 50000000 | 3230852553.8461
7 | 3 | 16 | 285.1 | 350.7844 | 0 | 0.5 | 3180989876.3457 | 50000000 | 3230989876.3457
7 | 3 | 12 | 285.3 | 352.5687 | 0 | 0.5 | 3197170589.4005 | 50000000 | 3247170589.4005
7 | 3 | 13 | 285.4 | 353.461 | 0 | 0.5 | 3205261847.4616 | 50000000 | 3255261847.4616
7 | 3 | 19 | 285.6 | 350.86 | 0 | 0.5 | 3181675223.5872 | 50000000 | 3231675223.5872
7 | 4 | 23 | 285.8 | 356.1535 | 0 | 0.5 | 3229678005.0829 | 50000000 | 3279678005.0829
7 | 3 | 15 | 285.9 | 351.7824 | 0 | 0.5 | 3190040636.0785 | 50000000 | 3240040636.0785
7 | 4 | 11 | 286.2 | 356.2146 | 0 | 0.5 | 3230232289.9571 | 50000000 | 3280232289.9571
7 | 3 | 14 | 286.4 | 353.6127 | 0 | 0.5 | 3206638167.3529 | 50000000 | 3256638167.3529
7 | 4 | 13 | 286.9 | 356.3212 | 0 | 0.5 | 3231199024.4968 | 50000000 | 3281199024.4968
7 | 4 | 17 | 287.1 | 355.4739 | 0 | 0.5 | 3223515177.6521 | 50000000 | 3273515177.6521
7 | 4 | 24 | 287.1 | 356.3516 | 0 | 0.5 | 3231474474.387 | 50000000 | 3281474474.387
7 | 4 | 16 | 287.2 | 355.489 | 0 | 0.5 | 3223652437.4083 | 50000000 | 3273652437.4083
7 | 4 | 15 | 287.4 | 356.3971 | 0 | 0.5 | 3231887018.2285 | 50000000 | 3281887018.2285
7 | 4 | 18 | 287.6 | 355.5495 | 0 | 0.5 | 3224200638.4615 | 50000000 | 3274200638.4615
7 | 4 | 22 | 287.6 | 356.4274 | 0 | 0.5 | 3232161627.6923 | 50000000 | 3282161627.6923
7 | 4 | 12 | 287.8 | 356.4576 | 0 | 0.5 | 3232435902.0622 | 50000000 | 3282435902.0622
7 | 4 | 21 | 287.8 | 355.5796 | 0 | 0.5 | 3224474237.2788 | 50000000 | 3274474237.2788
7 | 4 | 14 | 288.1 | 356.5029 | 0 | 0.5 | 3232846686.6565 | 50000000 | 3282846686.6565
7 | 4 | 20 | 288.3 | 355.6549 | 0 | 0.5 | 3225156775.9062 | 50000000 | 3275156775.9062
7 | 4 | 19 | 288.4 | 356.5481 | 0 | 0.5 | 3233256720.7308 | 50000000 | 3283256720.7308
6 | 6 | 15 | 290.9 | 366.592 | 5.3626 | 0.5 | 3275707711.8713 | 50000000 | 3325707711.8713
7 | 2 | 3 | 294.6 | 364.5081 | 0 | 0.3 | 3305439364.5188 | 30000000 | 3335439364.5188
7 | 20 | 12 | 300.8 | 357.4648 | 0 | 0.5 | 3241569346.4789 | 50000000 | 3291569346.4789
6 | 10 | 20 | 302.4 | 380.6495 | 5.4757 | 0.5 | 3402158844.785 | 50000000 | 3452158844.785
7 | 21 | 15 | 303 | 359.5364 | 0 | 0.5 | 3260355564.4898 | 50000000 | 3310355564.4898
7 | 21 | 16 | 303.7 | 358.7495 | 0 | 0.5 | 3253219307.78 | 50000000 | 3303219307.78
7 | 2 | 20 | 304.1 | 377.3633 | 0 | 0.4 | 3422013120.4708 | 40000000 | 3462013120.4708
7 | 2 | 22 | 304.1 | 378.247 | 0 | 0.4 | 3430027202.7201 | 40000000 | 3470027202.7201
7 | 20 | 13 | 304.4 | 362.381 | 0 | 0.5 | 3286150200 | 50000000 | 3336150200
7 | 2 | 23 | 305 | 377.4928 | 0 | 0.4 | 3423187338.2609 | 40000000 | 3463187338.2609
7 | 23 | 23 | 305.1 | 365.1298 | 0 | 0.4 | 3311077513.144 | 40000000 | 3351077513.144
7 | 24 | 20 | 305.4 | 365.1714 | 0 | 0.4 | 3311454551.9514 | 40000000 | 3351454551.9514
6 | 24 | 11 | 305.5 | 380.2171 | 0 | 0.4 | 3447892099.2764 | 40000000 | 3487892099.2764
7 | 2 | 18 | 305.5 | 377.5644 | 0 | 0.4 | 3423837038.1187 | 40000000 | 3463837038.1187
7 | 2 | 21 | 305.8 | 378.4916 | 0 | 0.4 | 3432245220.7288 | 40000000 | 3472245220.7288
7 | 2 | 19 | 306.2 | 378.5488 | 0 | 0.4 | 3432763941.6291 | 40000000 | 3472763941.6291
7 | 23 | 24 | 306.2 | 366.1664 | 0 | 0.4 | 3320477270.6413 | 40000000 | 3360477270.6413
7 | 24 | 11 | 306.2 | 367.9353 | 0 | 0.4 | 3336518223.6395 | 40000000 | 3376518223.6395
6 | 5 | 17 | 306.5 | 383.0144 | 5.1304 | 0.5 | 3426735089.4545 | 50000000 | 3476735089.4545
6 | 24 | 10 | 306.6 | 380.3751 | 0 | 0.4 | 3449324836.584 | 40000000 | 3489324836.584
6 | 21 | 20 | 306.7 | 375.0816 | 0 | 0.5 | 3401322709.4779 | 50000000 | 3451322709.4779
6 | 24 | 9 | 306.8 | 380.4037 | 0 | 0.4 | 3449584357.7855 | 40000000 | 3489584357.7855
6 | 24 | 8 | 307.1 | 380.4466 | 0 | 0.4 | 3449973078.8246 | 40000000 | 3489973078.8246
6 | 24 | 7 | 307.2 | 377.8065 | 0 | 0.4 | 3426032020.6452 | 40000000 | 3466032020.6452
6 | 21 | 16 | 307.6 | 376.9781 | 0 | 0.5 | 3418520670.5178 | 50000000 | 3468520670.5178
6 | 21 | 17 | 307.9 | 377.0204 | 0 | 0.5 | 3418904005.7143 | 50000000 | 3468904005.7143
6 | 4 | 22 | 308.7 | 386.8709 | 4.0723 | 0.5 | 3471302133.2194 | 50000000 | 3521302133.2194
7 | 1 | 10 | 308.7 | 385.1004 | 0 | 0.4 | 3492174902.7531 | 40000000 | 3532174902.7531
7 | 1 | 9 | 309.3 | 386.0716 | 0 | 0.4 | 3500981948.0561 | 40000000 | 3540981948.0561
7 | 1 | 8 | 309.4 | 385.2003 | 0 | 0.4 | 3493081458.443 | 40000000 | 3533081458.443
6 | 4 | 20 | 310.6 | 387.1426 | 4.7839 | 0.5 | 3467312804.8237 | 50000000 | 3517312804.8237
8 | 23 | 14 | 310.8 | 392.4869 | 15.2388 | 0.1 | 3420968933.9247 | 10000000 | 3430968933.9247
6 | 29 | 20 | 311.1 | 388.0997 | 0 | 0.3 | 3519373340.9171 | 30000000 | 3549373340.9171
6 | 4 | 21 | 311.3 | 387.242 | 4.9624 | 0.5 | 3466595424.4816 | 50000000 | 3516595424.4816
8 | 23 | 15 | 311.7 | 392.6162 | 15.2438 | 0.1 | 3422095607.8738 | 10000000 | 3432095607.8738
7 | 20 | 14 | 312.2 | 369.6405 | 0 | 0.5 | 3351981784.293 | 50000000 | 3401981784.293
7 | 20 | 11 | 312.7 | 370.5943 | 0 | 0.5 | 3360630396.0646 | 50000000 | 3410630396.0646
8 | 23 | 13 | 313 | 391.915 | 15.1623 | 0.1 | 3416476289.5581 | 10000000 | 3426476289.5581
8 | 23 | 16 | 313.1 | 393.7026 | 15.2515 | 0.1 | 3431877746.4673 | 10000000 | 3441877746.4673
7 | 19 | 8 | 313.1 | 370.648 | 0 | 0.5 | 3361117380.5608 | 50000000 | 3411117380.5608
7 | 19 | 1 | 313.1 | 368.8745 | 0 | 0.4 | 3345035479.2183 | 40000000 | 3385035479.2183
6 | 20 | 17 | 313.2 | 394.6036 | 0 | 0.5 | 3578352475.3114 | 50000000 | 3628352475.3114
6 | 28 | 6 | 313.5 | 387.5516 | 0 | 0.5 | 3514403411.2871 | 50000000 | 3564403411.2871
7 | 20 | 15 | 313.5 | 370.7016 | 0 | 0.5 | 3361603262.9703 | 50000000 | 3411603262.9703
6 | 28 | 4 | 314.3 | 387.6633 | 0 | 0.5 | 3515415906.2997 | 50000000 | 3565415906.2997
7 | 18 | 1 | 314.4 | 368.1603 | 0 | 0.5 | 3338558331.6027 | 50000000 | 3388558331.6027
7 | 20 | 9 | 314.4 | 371.7088 | 0 | 0.5 | 3370737207.088 | 50000000 | 3420737207.088
6 | 28 | 5 | 314.6 | 387.705 | 0 | 0.5 | 3515794414.1117 | 50000000 | 3565794414.1117
7 | 20 | 16 | 338 | 399.6984 | 0 | 0.5 | 3624553140 | 50000000 | 3674553140
7 | 22 | 20 | 358.8 | 421.9589 | 0 | 0.5 | 3826415924.2327 | 50000000 | 3876415924.2327
7 | 1 | 20 | 361.3 | 451.0623 | 0 | 0.4 | 4090332147.7349 | 40000000 | 4130332147.7349
6 | 2 | 5 | 361.4 | 448.3737 | 5.9423 | 0.5 | 4012065180.6457 | 50000000 | 4062065180.6457
7 | 25 | 17 | 362.7 | 429.6198 | 0 | 0.5 | 3895887010.0273 | 50000000 | 3945887010.0273
7 | 25 | 16 | 363.6 | 429.7255 | 0 | 0.5 | 3896845108.4837 | 50000000 | 3946845108.4837
7 | 25 | 20 | 363.7 | 429.7372 | 0 | 0.5 | 3896951300.1684 | 50000000 | 3946951300.1684
7 | 1 | 21 | 375.5 | 468.1324 | 0 | 0.4 | 4245127326.065 | 40000000 | 4285127326.065
6 | 30 | 4 | 377.4 | 462.0302 | 0 | 0.4 | 4189791381.1883 | 40000000 | 4229791381.1883
6 | 2 | 3 | 392.1 | 484.567 | 6.1705 | 0.5 | 4338204548.6841 | 50000000 | 4388204548.6841
6 | 4 | 14 | 393.2 | 488.3232 | 5.7183 | 0.5 | 4376367350.1773 | 50000000 | 4426367350.1773
6 | 4 | 15 | 393.8 | 488.3919 | 5.8099 | 0.5 | 4376159919.6349 | 50000000 | 4426159919.6349
7 | 30 | 22 | 399.6 | 471.7753 | 0 | 0.5 | 4278161759.6178 | 50000000 | 4328161759.6178
7 | 27 | 24 | 400.1 | 466.3742 | 0 | 0.5 | 4229184148.3436 | 50000000 | 4279184148.3436
7 | 25 | 14 | 400.6 | 478.2469 | 0 | 0.4 | 4336848429.941 | 40000000 | 4376848429.941
7 | 30 | 23 | 401.1 | 472.8452 | 0 | 0.5 | 4287863935.2528 | 50000000 | 4337863935.2528
6 | 9 | 21 | 403.4 | 505.8421 | 5.0038 | 0.3 | 4541711843.4235 | 30000000 | 4571711843.4235
7 | 23 | 10 | 403.8 | 477.6814 | 0 | 0.5 | 4331719916.4038 | 50000000 | 4381719916.4038
6 | 10 | 15 | 404.9 | 505.1011 | 5.9156 | 0.5 | 4526724363.8638 | 50000000 | 4576724363.8638
7 | 23 | 9 | 405.3 | 482.3916 | 0 | 0.5 | 4374433572.8273 | 50000000 | 4424433572.8273
7 | 26 | 17 | 405.6 | 478.7828 | 0 | 0.5 | 4341707443.5189 | 50000000 | 4391707443.5189
7 | 22 | 12 | 405.7 | 476.9729 | 0 | 0.5 | 4325294753.1882 | 50000000 | 4375294753.1882
7 | 26 | 20 | 405.8 | 476.9834 | 0 | 0.5 | 4325390413.2436 | 50000000 | 4375390413.2436
7 | 31 | 20 | 406.2 | 485.2187 | 0 | 0.3 | 4400070246.1049 | 30000000 | 4430070246.1049
7 | 26 | 18 | 406.4 | 478.8674 | 0 | 0.5 | 4342474784.5161 | 50000000 | 4392474784.5161
7 | 26 | 16 | 406.6 | 478.8885 | 0 | 0.5 | 4342666190.2194 | 50000000 | 4392666190.2194
6 | 5 | 13 | 407.3 | 506.2795 | 5.9187 | 0.5 | 4537381087.1831 | 50000000 | 4587381087.1831
6 | 5 | 12 | 407.5 | 507.2123 | 6.0101 | 0.5 | 4545012128.1788 | 50000000 | 4595012128.1788
7 | 26 | 19 | 407.5 | 478.9832 | 0 | 0.5 | 4343525398.6592 | 50000000 | 4393525398.6592
7 | 26 | 14 | 407.6 | 478.9937 | 0 | 0.5 | 4343620652.9759 | 50000000 | 4393620652.9759
7 | 26 | 15 | 407.6 | 478.9937 | 0 | 0.5 | 4343620652.9759 | 50000000 | 4393620652.9759
7 | 26 | 12 | 407.7 | 479.0042 | 0 | 0.5 | 4343715864.7398 | 50000000 | 4393715864.7398
7 | 26 | 13 | 407.7 | 479.0042 | 0 | 0.5 | 4343715864.7398 | 50000000 | 4393715864.7398
7 | 22 | 15 | 408.1 | 484.5106 | 0 | 0.5 | 4393648715.9652 | 50000000 | 4443648715.9652
7 | 22 | 17 | 408.3 | 483.621 | 0 | 0.5 | 4385581739.9197 | 50000000 | 4435581739.9197
7 | 26 | 11 | 408.4 | 478.1668 | 0 | 0.5 | 4336121878.2337 | 50000000 | 4386121878.2337
6 | 10 | 22 | 408.5 | 508.2341 | 5.7381 | 0.5 | 4556744155.806 | 50000000 | 4606744155.806
7 | 17 | 14 | 408.5 | 486.3746 | 0 | 0.5 | 4410551711.4381 | 50000000 | 4460551711.4381
7 | 22 | 16 | 408.5 | 484.553 | 0 | 0.5 | 4394032791.1706 | 50000000 | 4444032791.1706
7 | 22 | 13 | 408.7 | 484.5741 | 0 | 0.5 | 4394224571.9813 | 50000000 | 4444224571.9813
6 | 10 | 9 | 408.8 | 508.2674 | 5.9207 | 0.5 | 4555390412.8877 | 50000000 | 4605390412.8877
7 | 22 | 18 | 408.9 | 483.6843 | 0 | 0.5 | 4386156001.1094 | 50000000 | 4436156001.1094
7 | 22 | 14 | 409.2 | 483.7159 | 0 | 0.5 | 4386442556.4203 | 50000000 | 4436442556.4203
7 | 27 | 9 | 409.8 | 487.4233 | 0 | 0.4 | 4420061710.6714 | 40000000 | 4460061710.6714
7 | 17 | 15 | 410.6 | 488.419 | 0 | 0.5 | 4429090916.0053 | 50000000 | 4479090916.0053
7 | 28 | 10 | 411.7 | 485.8005 | 0 | 0.4 | 4405346094.182 | 40000000 | 4445346094.182
7 | 29 | 21 | 412 | 490.3894 | 0 | 0.5 | 4446958788.3186 | 50000000 | 4496958788.3186
7 | 18 | 22 | 412.4 | 493.1662 | 0 | 0.4 | 4472139821.061 | 40000000 | 4512139821.061
7 | 19 | 17 | 412.5 | 481.326 | 0 | 0.5 | 4364769759.116 | 50000000 | 4414769759.116
7 | 28 | 9 | 413.5 | 490.5469 | 0 | 0.4 | 4448386826.5932 | 40000000 | 4488386826.5932
6 | 8 | 5 | 413.6 | 509.7055 | 5.1974 | 0.2 | 4574990559.3333 | 20000000 | 4594990559.3333
7 | 18 | 12 | 413.9 | 495.1481 | 0 | 0.5 | 4490111452.0687 | 50000000 | 4540111452.0687
6 | 8 | 4 | 414.2 | 510.6825 | 5.198 | 0.3 | 4583844654.5865 | 30000000 | 4613844654.5865
7 | 17 | 16 | 415.8 | 497.172 | 0 | 0.5 | 4508465121.5884 | 50000000 | 4558465121.5884
7 | 29 | 22 | 416.2 | 496.3016 | 0 | 0.5 | 4500572295.5195 | 50000000 | 4550572295.5195
11 | 8 | 15 | 417.4 | 520.153 | 8.3955 | 0.5 | 4640730379.7604 | 50000000 | 4690730379.7604
7 | 28 | 11 | 418.4 | 494.7051 | 0 | 0.5 | 4486094329.0052 | 50000000 | 4536094329.0052
7 | 31 | 21 | 419 | 504.8083 | 0 | 0.3 | 4577712530.5882 | 30000000 | 4607712530.5882
11 | 8 | 10 | 420.4 | 519.5647 | 8.6746 | 0.5 | 4632863782.4414 | 50000000 | 4682863782.4414
7 | 27 | 23 | 421.2 | 495.9055 | 0 | 0.5 | 4496979846.817 | 50000000 | 4546979846.817
7 | 18 | 13 | 422.8 | 507.0311 | 0 | 0.5 | 4597869697.2342 | 50000000 | 4647869697.2342
6 | 9 | 20 | 423.3 | 533.5791 | 5.1165 | 0.3 | 4792215068.0734 | 30000000 | 4822215068.0734
11 | 8 | 11 | 423.6 | 520.8197 | 8.4062 | 0.5 | 4646677985.1458 | 50000000 | 4696677985.1458
7 | 18 | 14 | 423.6 | 507.1139 | 0 | 0.5 | 4598620331.2338 | 50000000 | 4648620331.2338
6 | 9 | 18 | 424 | 534.569 | 5.1172 | 0.3 | 4801184713.8621 | 30000000 | 4831184713.8621
6 | 9 | 17 | 424.2 | 534.5907 | 5.1174 | 0.2 | 4801379863.3468 | 20000000 | 4821379863.3468
6 | 9 | 19 | 424.3 | 534.6016 | 5.1176 | 0.3 | 4801477375.0429 | 30000000 | 4831477375.0429
6 | 9 | 16 | 424.4 | 535.5263 | 5.1177 | 0.3 | 4809861994.9768 | 30000000 | 4839861994.9768
6 | 9 | 14 | 425.2 | 502.7085 | 5.2099 | 0.3 | 4511426974.3749 | 30000000 | 4541426974.3749
6 | 9 | 15 | 425.8 | 535.678 | 5.1191 | 0.3 | 4811224524.067 | 30000000 | 4841224524.067
11 | 8 | 12 | 426.1 | 521.0835 | 8.4105 | 0.5 | 4649031448.9457 | 50000000 | 4699031448.9457
11 | 8 | 14 | 426.3 | 520.1902 | 8.5022 | 0.5 | 4640099269.7924 | 50000000 | 4690099269.7924
11 | 8 | 13 | 427.2 | 520.2842 | 8.4123 | 0.5 | 4641767162.5069 | 50000000 | 4691767162.5069
7 | 31 | 22 | 429.4 | 518.683 | 0 | 0.3 | 4703531550.3962 | 30000000 | 4733531550.3962
7 | 26 | 9 | 438.5 | 521.4347 | 0 | 0.5 | 4728484500.3762 | 50000000 | 4778484500.3762
6 | 28 | 14 | 453.6 | 570.6759 | 0 | 0.5 | 5175014164.5705 | 50000000 | 5225014164.5705
6 | 28 | 13 | 453.9 | 571.6254 | 0 | 0.5 | 5183625159.0929 | 50000000 | 5233625159.0929
6 | 28 | 11 | 454.3 | 570.7471 | 0 | 0.5 | 5175660422.5491 | 50000000 | 5225660422.5491
7 | 24 | 16 | 454.3 | 555.1228 | 0 | 0.4 | 5033975676.6822 | 40000000 | 5073975676.6822
6 | 28 | 12 | 455.3 | 569.9293 | 0 | 0.5 | 5168244601.0903 | 50000000 | 5218244601.0903
6 | 28 | 10 | 456.2 | 575.5365 | 0 | 0.5 | 5219091393.5187 | 50000000 | 5269091393.5187
6 | 28 | 9 | 456.4 | 570.0403 | 0 | 0.5 | 5169250759.3876 | 50000000 | 5219250759.3876
6 | 28 | 16 | 456.4 | 577.3956 | 0 | 0.5 | 5235950769.1861 | 50000000 | 5285950769.1861
6 | 30 | 1 | 456.8 | 574.6779 | 0 | 0.4 | 5211305978.2609 | 40000000 | 5251305978.2609
6 | 28 | 15 | 457.3 | 574.7285 | 0 | 0.5 | 5211764787.3517 | 50000000 | 5261764787.3517
6 | 29 | 13 | 458.8 | 573.9599 | 0 | 0.5 | 5204794678.5565 | 50000000 | 5254794678.5565
6 | 28 | 17 | 459.5 | 580.4695 | 0 | 0.5 | 5263824852.4324 | 50000000 | 5313824852.4324
6 | 29 | 16 | 461.8 | 581.6214 | 0 | 0.4 | 5274270477.226 | 40000000 | 5314270477.226
6 | 29 | 17 | 461.8 | 579.7808 | 0 | 0.4 | 5257579747.8677 | 40000000 | 5297579747.8677
6 | 29 | 15 | 462.4 | 578.9204 | 0 | 0.4 | 5249777387.9618 | 40000000 | 5289777387.9618
6 | 29 | 14 | 463.2 | 579 | 0 | 0.4 | 5250499380 | 40000000 | 5290499380
11 | 17 | 7 | 465.6 | 550.6899 | 8.8405 | 0.3 | 4913609267.6202 | 30000000 | 4943609267.6202
11 | 17 | 9 | 471.7 | 558.6285 | 8.8496 | 0.4 | 4985516315.5239 | 40000000 | 5025516315.5239
11 | 17 | 10 | 471.8 | 551.263 | 0.82966 | 0.5 | 4991450562 | 50000000 | 5041450562
11 | 17 | 11 | 472 | 550.3594 | 0 | 0.5 | 4990779891.5625 | 50000000 | 5040779891.5625
7 | 27 | 11 | 472 | 570.6406 | 0 | 0.4 | 5174694728.4375 | 40000000 | 5214694728.4375
7 | 27 | 12 | 472.2 | 569.7376 | 0 | 0.4 | 5166505921.7337 | 40000000 | 5206505921.7337
11 | 17 | 8 | 473.3 | 559.6982 | 8.9441 | 0.3 | 4994359529.6704 | 30000000 | 5024359529.6704
7 | 6 | 13 | 477.3 | 632.0327 | 36.907 | 0.5 | 5396730343.843 | 50000000 | 5446730343.843
7 | 6 | 17 | 478.4 | 611.8426 | 37.0059 | 0.5 | 5212745917.1667 | 50000000 | 5262745917.1667
7 | 6 | 18 | 479.7 | 549.2043 | 36.9213 | 0.5 | 4645495380.7389 | 50000000 | 4695495380.7389
7 | 18 | 16 | 492.2 | 598.3717 | 0 | 0.5 | 5426165898.0609 | 50000000 | 5476165898.0609
7 | 29 | 18 | 492.8 | 604.9009 | 0 | 0.5 | 5485374447.5676 | 50000000 | 5535374447.5676
7 | 27 | 19 | 496.5 | 604.3141 | 0 | 0.5 | 5480052960.2796 | 50000000 | 5530052960.2796
7 | 27 | 18 | 497.6 | 604.4137 | 0 | 0.5 | 5480956316.25 | 50000000 | 5530956316.25
7 | 23 | 18 | 497.8 | 609.9855 | 0 | 0.5 | 5531482678.7728 | 50000000 | 5581482678.7728
7 | 23 | 17 | 499 | 616.5751 | 0 | 0.5 | 5591239008.3117 | 50000000 | 5641239008.3117
7 | 27 | 17 | 499.3 | 607.3443 | 0 | 0.5 | 5507532047.7953 | 50000000 | 5557532047.7953
7 | 31 | 18 | 503.5 | 616.9844 | 0 | 0.3 | 5594949918.7121 | 30000000 | 5624949918.7121
7 | 31 | 17 | 504.8 | 618.0279 | 0 | 0.3 | 5604412964.6696 | 30000000 | 5634412964.6696
7 | 31 | 15 | 504.9 | 618.9635 | 0 | 0.3 | 5612897004.4118 | 30000000 | 5642897004.4118
7 | 31 | 16 | 505 | 618.0459 | 0 | 0.3 | 5604575933.3945 | 30000000 | 5634575933.3945
7 | 23 | 21 | 505.8 | 616.2642 | 0 | 0.5 | 5588419337.7428 | 50000000 | 5638419337.7428
7 | 23 | 19 | 506 | 618.1355 | 0 | 0.5 | 5605388986.1538 | 50000000 | 5655388986.1538
7 | 23 | 20 | 506.4 | 618.1713 | 0 | 0.5 | 5605713373.9678 | 50000000 | 5655713373.9678
7 | 23 | 12 | 506.9 | 621.9234 | 0 | 0.5 | 5639738090.6528 | 50000000 | 5689738090.6528
7 | 27 | 15 | 507.3 | 615.4709 | 0 | 0.5 | 5581225134.2664 | 50000000 | 5631225134.2664
7 | 23 | 13 | 507.5 | 622.9041 | 0 | 0.5 | 5648631504.6575 | 50000000 | 5698631504.6575
7 | 31 | 14 | 507.7 | 621.0681 | 0 | 0.3 | 5631982192.7698 | 30000000 | 5661982192.7698
7 | 23 | 16 | 508 | 624.8029 | 0 | 0.5 | 5665850332.5548 | 50000000 | 5715850332.5548
7 | 27 | 16 | 508.1 | 616.4687 | 0 | 0.5 | 5590273886.2069 | 50000000 | 5640273886.2069
7 | 29 | 14 | 508.2 | 620.1857 | 0 | 0.5 | 5623980356.2131 | 50000000 | 5673980356.2131
7 | 23 | 15 | 509 | 625.8197 | 0 | 0.5 | 5675070467.2131 | 50000000 | 5725070467.2131
7 | 23 | 14 | 509.9 | 625.9002 | 0 | 0.5 | 5675800382.1604 | 50000000 | 5725800382.1604
7 | 31 | 13 | 510 | 622.2 | 0 | 0.3 | 5642246484 | 30000000 | 5672246484
7 | 31 | 11 | 513.1 | 625.2566 | 0 | 0.3 | 5669963987.8286 | 30000000 | 5699963987.8286
7 | 2 | 13 | 514.6 | 641.1623 | 0 | 0.4 | 5814200602.7624 | 40000000 | 5854200602.7624
7 | 2 | 14 | 514.8 | 641.1802 | 0 | 0.4 | 5814363522.5234 | 40000000 | 5854363522.5234
7 | 2 | 15 | 514.9 | 640.2613 | 0 | 0.4 | 5806030401.5498 | 40000000 | 5846030401.5498
7 | 2 | 12 | 515.9 | 642.2069 | 0 | 0.4 | 5823673198.4458 | 40000000 | 5863673198.4458
7 | 2 | 11 | 516 | 644.0719 | 0 | 0.4 | 5840586069.9281 | 40000000 | 5880586069.9281
7 | 17 | 18 | 516.7 | 625.5718 | 0 | 0.5 | 5672822365.1446 | 50000000 | 5722822365.1446
7 | 19 | 12 | 517.4 | 631.202 | 0 | 0.5 | 5723878685.0377 | 50000000 | 5773878685.0377
7 | 19 | 15 | 517.6 | 628.4347 | 0 | 0.5 | 5698784298.6801 | 50000000 | 5748784298.6801
6 | 2 | 18 | 518.2 | 653.5521 | 6.7769 | 0.5 | 5865100183.6381 | 50000000 | 5915100183.6381
6 | 2 | 15 | 518.3 | 653.5612 | 6.777 | 0.5 | 5865181274.2149 | 50000000 | 5915181274.2149
7 | 19 | 13 | 518.9 | 630.4045 | 0 | 0.5 | 5716647099.8068 | 50000000 | 5766647099.8068
7 | 19 | 14 | 519.1 | 630.4219 | 0 | 0.5 | 5716804736.8235 | 50000000 | 5766804736.8235
7 | 19 | 11 | 519.2 | 632.2876 | 0 | 0.5 | 5733722639.7425 | 50000000 | 5783722639.7425
6 | 8 | 12 | 521.7 | 598.1392 | 5.5727 | 0.4 | 5373523337.3901 | 40000000 | 5413523337.3901
6 | 1 | 12 | 521.9 | 659.4572 | 6.8732 | 0.5 | 5917775125.5505 | 50000000 | 5967775125.5505
6 | 1 | 11 | 522.7 | 660.458 | 6.874 | 0.5 | 5926843552.0498 | 50000000 | 5976843552.0498
6 | 8 | 15 | 523 | 582.4529 | 5.5737 | 0.4 | 5231267666.5364 | 40000000 | 5271267666.5364
6 | 3 | 9 | 523.3 | 666.0857 | 6.6887 | 0.5 | 5979557222.714 | 50000000 | 6029557222.714
6 | 8 | 14 | 524 | 587.1773 | 5.9461 | 0.4 | 5270732443.9149 | 40000000 | 5310732443.9149
6 | 8 | 18 | 524.4 | 578.8469 | 5.4819 | 0.3 | 5199400506.5783 | 30000000 | 5229400506.5783
6 | 8 | 19 | 524.4 | 587.2091 | 5.8535 | 0.3 | 5271860147.4089 | 30000000 | 5301860147.4089
6 | 8 | 16 | 524.6 | 578.8626 | 5.2962 | 0.4 | 5201226148.1892 | 40000000 | 5241226148.1892
6 | 8 | 17 | 524.6 | 578.8626 | 5.2962 | 0.4 | 5201226148.1892 | 40000000 | 5241226148.1892
6 | 8 | 13 | 524.7 | 577.9412 | 5.6679 | 0.4 | 5189500144.2192 | 40000000 | 5229500144.2192
6 | 7 | 17 | 524.8 | 666.221 | 5.7609 | 0.5 | 5989197094.9802 | 50000000 | 6039197094.9802
6 | 8 | 8 | 524.8 | 663.4334 | 5.668 | 0.3 | 5964761710.0963 | 30000000 | 5994761710.0963
6 | 7 | 16 | 525.2 | 666.2569 | 5.6683 | 0.5 | 5990362806.9172 | 50000000 | 6040362806.9172
6 | 7 | 20 | 525.5 | 666.2838 | 5.7615 | 0.4 | 5989762162.313 | 40000000 | 6029762162.313
6 | 7 | 18 | 525.7 | 666.3018 | 5.7616 | 0.5 | 5989923353.2671 | 50000000 | 6039923353.2671
6 | 7 | 22 | 526 | 667.258 | 5.6689 | 0.3 | 5999435018.1413 | 30000000 | 6029435018.1413
6 | 7 | 21 | 526.9 | 666.4091 | 5.6696 | 0.3 | 5991730947.9383 | 30000000 | 6021730947.9383
6 | 7 | 23 | 527.3 | 667.3742 | 5.6699 | 0.3 | 6000480496.7943 | 30000000 | 6030480496.7943
6 | 8 | 1 | 527.4 | 662.7356 | 5.67 | 0.3 | 5958416031.5002 | 30000000 | 5988416031.5002
6 | 7 | 24 | 529.3 | 666.6223 | 5.7644 | 0.3 | 5992805423.7428 | 30000000 | 6022805423.7428

## Gas Heat Input
No Load Fuel = 238.232 mmBtu/hr
Fitted Regression Line Equation
MW

## Gas Data
MONTH | DAY | HOUR |  |  |  |  | #6 Oil | Gas | Total
|  |  | Net Load | MFO Flw | MFO Ret | KTherms | 151137
11 | 10 | 16 | 43.1 | 0 | 0 | 6.9499 | 0 | 694993983.1528 | 694993983.1528
11 | 22 | 12 | 43.1 | 0 | 0 | 6.8462 | 0 | 684620938.6282 | 684620938.6282
11 | 22 | 10 | 43.2 | 0 | 0 | 6.9058 | 0 | 690576923.0769 | 690576923.0769
11 | 22 | 11 | 43.2 | 0 | 0 | 6.8019 | 0 | 680192307.6923 | 680192307.6923
11 | 22 | 13 | 43.4 | 0 | 0 | 6.817 | 0 | 681702637.8897 | 681702637.8897
11 | 10 | 14 | 43.5 | 0 | 0 | 6.9287 | 0 | 692874251.497 | 692874251.497
11 | 22 | 9 | 43.5 | 0 | 0 | 7.0329 | 0 | 703293413.1737 | 703293413.1737
11 | 22 | 14 | 43.5 | 0 | 0 | 6.8766 | 0 | 687664670.6587 | 687664670.6587
11 | 22 | 15 | 43.5 | 0 | 0 | 6.8246 | 0 | 682455089.8204 | 682455089.8204
11 | 10 | 15 | 43.6 | 0 | 0 | 6.9885 | 0 | 698851674.6411 | 698851674.6411
11 | 19 | 18 | 43.8 | 0 | 0 | 7.1084 | 0 | 710835322.1957 | 710835322.1957
11 | 19 | 19 | 43.8 | 0 | 0 | 7.1084 | 0 | 710835322.1957 | 710835322.1957
9 | 4 | 5 | 43.9 | 0 | 0 | 7.0638 | 0 | 706376638.8558 | 706376638.8558
9 | 4 | 2 | 44 | 0 | 0 | 7.0714 | 0 | 707142857.1429 | 707142857.1429
11 | 11 | 11 | 44 | 0 | 0 | 7.2286 | 0 | 722857142.8571 | 722857142.8571
11 | 11 | 12 | 44 | 0 | 0 | 7.1762 | 0 | 717619047.619 | 717619047.619
11 | 11 | 14 | 44 | 0 | 0 | 7.2286 | 0 | 722857142.8571 | 722857142.8571
11 | 11 | 13 | 44.1 | 0 | 0 | 7.1839 | 0 | 718394768.1332 | 718394768.1332
11 | 22 | 8 | 44.1 | 0 | 0 | 7.0266 | 0 | 702663495.8383 | 702663495.8383
9 | 2 | 1 | 44.3 | 0 | 0 | 6.9892 | 0 | 698920521.9454 | 698920521.9454
9 | 2 | 2 | 44.5 | 0 | 0 | 7.2148 | 0 | 721479289.9408 | 721479289.9408
9 | 4 | 3 | 44.5 | 0 | 0 | 7.1621 | 0 | 716213017.7515 | 716213017.7515
11 | 8 | 21 | 44.5 | 0 | 0 | 7.3728 | 0 | 737278106.5089 | 737278106.5089
11 | 30 | 6 | 44.5 | 0 | 0 | 7.1095 | 0 | 710946745.5621 | 710946745.5621
11 | 18 | 11 | 44.6 | 0 | 0 | 7.1697 | 0 | 716973995.2719 | 716973995.2719
11 | 18 | 20 | 44.6 | 0 | 0 | 7.1697 | 0 | 716973995.2719 | 716973995.2719
11 | 8 | 22 | 44.7 | 0 | 0 | 7.3884 | 0 | 738842975.2066 | 738842975.2066
11 | 11 | 10 | 44.7 | 0 | 0 | 7.2829 | 0 | 728288075.5608 | 728288075.5608
11 | 17 | 20 | 44.7 | 0 | 0 | 7.1246 | 0 | 712455726.0921 | 712455726.0921
11 | 18 | 10 | 44.7 | 0 | 0 | 7.2301 | 0 | 723010625.7379 | 723010625.7379
11 | 18 | 21 | 44.7 | 0 | 0 | 7.1246 | 0 | 712455726.0921 | 712455726.0921
11 | 29 | 19 | 44.7 | 0 | 0 | 7.0718 | 0 | 707178276.2692 | 707178276.2692
11 | 29 | 21 | 44.7 | 0 | 0 | 7.0718 | 0 | 707178276.2692 | 707178276.2692
9 | 4 | 4 | 44.8 | 0 | 0 | 7.0792 | 0 | 707924528.3019 | 707924528.3019
11 | 18 | 9 | 44.8 | 0 | 0 | 7.2377 | 0 | 723773584.9057 | 723773584.9057
11 | 18 | 16 | 44.8 | 0 | 0 | 7.1849 | 0 | 718490566.0377 | 718490566.0377
11 | 20 | 14 | 44.8 | 0 | 0 | 6.8151 | 0 | 681509433.9623 | 681509433.9623
11 | 30 | 8 | 44.8 | 0 | 0 | 7.1849 | 0 | 718490566.0377 | 718490566.0377
9 | 2 | 3 | 44.9 | 0 | 0 | 7.2453 | 0 | 724534746.7609 | 724534746.7609
11 | 15 | 23 | 44.9 | 0 | 0 | 7.2982 | 0 | 729823321.5548 | 729823321.5548
11 | 18 | 12 | 44.9 | 0 | 0 | 7.2453 | 0 | 724534746.7609 | 724534746.7609
11 | 18 | 15 | 44.9 | 0 | 0 | 7.1925 | 0 | 719246171.967 | 719246171.967
11 | 20 | 15 | 44.9 | 0 | 0 | 6.8223 | 0 | 682226148.4099 | 682226148.4099
11 | 29 | 20 | 44.9 | 0 | 0 | 7.0867 | 0 | 708669022.3793 | 708669022.3793
11 | 11 | 9 | 45 | 0 | 0 | 7.3059 | 0 | 730588235.2941 | 730588235.2941
11 | 11 | 15 | 45 | 0 | 0 | 7.2529 | 0 | 725294117.6471 | 725294117.6471
11 | 18 | 22 | 45 | 0 | 0 | 7.2 | 0 | 720000000 | 720000000
11 | 20 | 11 | 45 | 0 | 0 | 6.8294 | 0 | 682941176.4706 | 682941176.4706
9 | 2 | 5 | 45.1 | 0 | 0 | 7.3135 | 0 | 731351351.3514 | 731351351.3514
11 | 11 | 8 | 45.1 | 0 | 0 | 7.3135 | 0 | 731351351.3514 | 731351351.3514
11 | 17 | 24 | 45.1 | 0 | 0 | 7.2075 | 0 | 720752056.4042 | 720752056.4042
11 | 18 | 2 | 45.1 | 0 | 0 | 7.2075 | 0 | 720752056.4042 | 720752056.4042
11 | 18 | 6 | 45.1 | 0 | 0 | 7.2605 | 0 | 726051703.8778 | 726051703.8778
11 | 19 | 20 | 45.1 | 0 | 0 | 7.2075 | 0 | 720752056.4042 | 720752056.4042
11 | 29 | 22 | 45.1 | 0 | 0 | 7.1015 | 0 | 710152761.4571 | 710152761.4571
11 | 18 | 14 | 45.2 | 0 | 0 | 7.215 | 0 | 721502347.4178 | 721502347.4178
11 | 19 | 17 | 45.2 | 0 | 0 | 7.215 | 0 | 721502347.4178 | 721502347.4178
9 | 2 | 4 | 45.3 | 0 | 0 | 7.2756 | 0 | 727561547.4795 | 727561547.4795
11 | 18 | 3 | 45.3 | 0 | 0 | 7.2756 | 0 | 727561547.4795 | 727561547.4795
11 | 18 | 13 | 45.3 | 0 | 0 | 7.2225 | 0 | 722250879.2497 | 722250879.2497
11 | 19 | 9 | 45.3 | 0 | 0 | 7.2225 | 0 | 722250879.2497 | 722250879.2497
11 | 20 | 12 | 45.3 | 0 | 0 | 6.8508 | 0 | 685076201.6413 | 685076201.6413
11 | 30 | 5 | 45.3 | 0 | 0 | 7.1694 | 0 | 716940211.0199 | 716940211.0199
11 | 18 | 4 | 45.4 | 0 | 0 | 7.23 | 0 | 722997658.0796 | 722997658.0796
11 | 19 | 13 | 45.4 | 0 | 0 | 7.23 | 0 | 722997658.0796 | 722997658.0796
11 | 29 | 24 | 45.4 | 0 | 0 | 7.1768 | 0 | 717681498.829 | 717681498.829
11 | 30 | 7 | 45.4 | 0 | 0 | 7.1768 | 0 | 717681498.829 | 717681498.829
11 | 18 | 1 | 45.5 | 0 | 0 | 7.2906 | 0 | 729064327.4854 | 729064327.4854
11 | 18 | 5 | 45.5 | 0 | 0 | 7.2374 | 0 | 723742690.0585 | 723742690.0585
11 | 18 | 8 | 45.5 | 0 | 0 | 7.2906 | 0 | 729064327.4854 | 729064327.4854
11 | 19 | 16 | 45.5 | 0 | 0 | 7.1842 | 0 | 718421052.6316 | 718421052.6316
11 | 19 | 21 | 45.5 | 0 | 0 | 7.2374 | 0 | 723742690.0585 | 723742690.0585
11 | 20 | 13 | 45.5 | 0 | 0 | 6.8649 | 0 | 686491228.0702 | 686491228.0702
11 | 20 | 17 | 45.5 | 0 | 0 | 6.8649 | 0 | 686491228.0702 | 686491228.0702
11 | 30 | 4 | 45.5 | 0 | 0 | 7.1842 | 0 | 718421052.6316 | 718421052.6316
11 | 19 | 15 | 45.6 | 0 | 0 | 7.2449 | 0 | 724485981.3084 | 724485981.3084
11 | 21 | 20 | 45.6 | 0 | 0 | 7.1383 | 0 | 713831775.7009 | 713831775.7009
11 | 23 | 11 | 45.6 | 0 | 0 | 7.2449 | 0 | 724485981.3084 | 724485981.3084
11 | 17 | 23 | 45.7 | 0 | 0 | 7.2523 | 0 | 725227537.923 | 725227537.923
11 | 19 | 11 | 45.7 | 0 | 0 | 7.2523 | 0 | 725227537.923 | 725227537.923
11 | 19 | 22 | 45.7 | 0 | 0 | 7.2523 | 0 | 725227537.923 | 725227537.923
11 | 30 | 1 | 45.7 | 0 | 0 | 7.1989 | 0 | 719894982.4971 | 719894982.4971
11 | 19 | 10 | 45.8 | 0 | 0 | 7.3131 | 0 | 731305361.3054 | 731305361.3054
11 | 19 | 14 | 45.8 | 0 | 0 | 7.2597 | 0 | 725967365.9674 | 725967365.9674
11 | 20 | 10 | 45.8 | 0 | 0 | 6.9394 | 0 | 693939393.9394 | 693939393.9394
11 | 30 | 2 | 45.8 | 0 | 0 | 7.2063 | 0 | 720629370.6294 | 720629370.6294
11 | 30 | 3 | 45.8 | 0 | 0 | 7.2063 | 0 | 720629370.6294 | 720629370.6294
11 | 18 | 7 | 45.9 | 0 | 0 | 7.3205 | 0 | 732048894.0629 | 732048894.0629
11 | 19 | 12 | 45.9 | 0 | 0 | 7.2136 | 0 | 721362048.8941 | 721362048.8941
11 | 21 | 18 | 45.9 | 0 | 0 | 7.1602 | 0 | 716018626.3097 | 716018626.3097
11 | 21 | 19 | 45.9 | 0 | 0 | 7.1068 | 0 | 710675203.7253 | 710675203.7253
11 | 20 | 16 | 46 | 0 | 0 | 6.9 | 0 | 690000000 | 690000000
11 | 23 | 9 | 46 | 0 | 0 | 7.1674 | 0 | 716744186.0465 | 716744186.0465
8 | 5 | 3 | 46.1 | 0 | 0 | 7.2282 | 0 | 722822299.6516 | 722822299.6516
11 | 21 | 22 | 46.1 | 0 | 0 | 7.1747 | 0 | 717468060.3949 | 717468060.3949
11 | 23 | 10 | 46.1 | 0 | 0 | 7.2282 | 0 | 722822299.6516 | 722822299.6516
11 | 20 | 18 | 46.2 | 0 | 0 | 6.9139 | 0 | 691392111.3689 | 691392111.3689
11 | 21 | 21 | 46.2 | 0 | 0 | 7.2355 | 0 | 723549883.9907 | 723549883.9907
11 | 22 | 22 | 46.2 | 0 | 0 | 7.1283 | 0 | 712830626.4501 | 712830626.4501
11 | 8 | 23 | 46.3 | 0 | 0 | 7.511 | 0 | 751100811.124 | 751100811.124
11 | 9 | 2 | 46.3 | 0 | 0 | 7.511 | 0 | 751100811.124 | 751100811.124
11 | 29 | 23 | 46.3 | 0 | 0 | 7.2428 | 0 | 724275782.1553 | 724275782.1553
11 | 21 | 23 | 46.4 | 0 | 0 | 7.1426 | 0 | 714259259.2593 | 714259259.2593
9 | 28 | 15 | 46.5 | 0 | 0 | 7.3647 | 0 | 736473988.4393 | 736473988.4393
11 | 18 | 23 | 46.5 | 0 | 0 | 7.311 | 0 | 731098265.896 | 731098265.896
11 | 19 | 1 | 46.5 | 0 | 0 | 7.3647 | 0 | 736473988.4393 | 736473988.4393
11 | 19 | 2 | 46.5 | 0 | 0 | 7.311 | 0 | 731098265.896 | 731098265.896
11 | 19 | 8 | 46.5 | 0 | 0 | 7.311 | 0 | 731098265.896 | 731098265.896
11 | 22 | 23 | 46.5 | 0 | 0 | 7.2572 | 0 | 725722543.3526 | 725722543.3526
10 | 3 | 1 | 46.6 | 0 | 0 | 7.8025 | 0 | 780254041.5704 | 780254041.5704
11 | 20 | 22 | 46.6 | 0 | 0 | 6.9954 | 0 | 699538106.2356 | 699538106.2356
10 | 1 | 13 | 46.7 | 0 | 0 | 7.6487 | 0 | 764867358.7082 | 764867358.7082
11 | 8 | 24 | 46.7 | 0 | 0 | 7.5948 | 0 | 759480968.8581 | 759480968.8581
11 | 9 | 1 | 46.7 | 0 | 0 | 7.5409 | 0 | 754094579.0081 | 754094579.0081
11 | 11 | 7 | 46.7 | 0 | 0 | 7.5409 | 0 | 754094579.0081 | 754094579.0081
11 | 18 | 24 | 46.7 | 0 | 0 | 7.3255 | 0 | 732549019.6078 | 732549019.6078
11 | 19 | 3 | 46.7 | 0 | 0 | 7.2716 | 0 | 727162629.7578 | 727162629.7578
11 | 20 | 19 | 46.7 | 0 | 0 | 6.9484 | 0 | 694844290.6574 | 694844290.6574
8 | 24 | 4 | 46.8 | 0 | 0 | 7.4406 | 0 | 744055299.5392 | 744055299.5392
11 | 16 | 1 | 46.8 | 0 | 0 | 7.7641 | 0 | 776405529.9539 | 776405529.9539
11 | 20 | 20 | 46.8 | 0 | 0 | 7.0092 | 0 | 700921658.9862 | 700921658.9862
8 | 24 | 5 | 46.9 | 0 | 0 | 7.4479 | 0 | 744787111.6226 | 744787111.6226
8 | 17 | 2 | 46.9 | 0 | 0 | 7.1241 | 0 | 712405063.2911 | 712405063.2911
11 | 19 | 4 | 46.9 | 0 | 0 | 7.3399 | 0 | 733993095.5121 | 733993095.5121
11 | 19 | 7 | 46.9 | 0 | 0 | 7.3399 | 0 | 733993095.5121 | 733993095.5121
11 | 20 | 21 | 46.9 | 0 | 0 | 7.0161 | 0 | 701611047.1807 | 701611047.1807
11 | 21 | 12 | 46.9 | 0 | 0 | 7.1241 | 0 | 712405063.2911 | 712405063.2911
11 | 21 | 17 | 46.9 | 0 | 0 | 7.178 | 0 | 717802071.3464 | 717802071.3464
10 | 1 | 12 | 47 | 0 | 0 | 7.6713 | 0 | 767126436.7816 | 767126436.7816
11 | 9 | 8 | 47 | 0 | 0 | 7.5632 | 0 | 756321839.0805 | 756321839.0805
11 | 19 | 5 | 47 | 0 | 0 | 7.3471 | 0 | 734712643.6782 | 734712643.6782
11 | 21 | 10 | 47 | 0 | 0 | 7.131 | 0 | 713103448.2759 | 713103448.2759
9 | 3 | 10 | 47.1 | 0 | 0 | 7.7869 | 0 | 778691159.5867 | 778691159.5867
10 | 1 | 11 | 47.1 | 0 | 0 | 7.6788 | 0 | 767876004.5924 | 767876004.5924
8 | 17 | 5 | 47.1 | 0 | 0 | 7.1921 | 0 | 719207807.1183 | 719207807.1183
11 | 19 | 23 | 47.1 | 0 | 0 | 7.2462 | 0 | 724615384.6154 | 724615384.6154
11 | 20 | 9 | 47.1 | 0 | 0 | 7.0299 | 0 | 702985074.6269 | 702985074.6269
11 | 9 | 3 | 47.2 | 0 | 0 | 7.6321 | 0 | 763211009.1743 | 763211009.1743
11 | 19 | 6 | 47.2 | 0 | 0 | 7.3615 | 0 | 736146788.9908 | 736146788.9908
11 | 21 | 11 | 47.2 | 0 | 0 | 7.1991 | 0 | 719908256.8807 | 719908256.8807
11 | 21 | 16 | 47.2 | 0 | 0 | 7.2532 | 0 | 725321100.9174 | 725321100.9174
11 | 23 | 12 | 47.2 | 0 | 0 | 7.4156 | 0 | 741559633.0275 | 741559633.0275
10 | 1 | 15 | 47.3 | 0 | 0 | 7.7479 | 0 | 774788087.0561 | 774788087.0561
8 | 17 | 3 | 47.3 | 0 | 0 | 7.2061 | 0 | 720607101.9473 | 720607101.9473
11 | 21 | 15 | 47.3 | 0 | 0 | 7.2603 | 0 | 726025200.4582 | 726025200.4582
10 | 2 | 12 | 47.4 | 0 | 0 | 7.8096 | 0 | 780961098.3982 | 780961098.3982
10 | 1 | 14 | 47.4 | 0 | 0 | 7.7011 | 0 | 770114416.476 | 770114416.476
9 | 28 | 14 | 47.4 | 0 | 0 | 7.43 | 0 | 742997711.6705 | 742997711.6705
11 | 9 | 9 | 47.4 | 0 | 0 | 7.5384 | 0 | 753844393.5927 | 753844393.5927
11 | 22 | 5 | 47.4 | 0 | 0 | 7.43 | 0 | 742997711.6705 | 742997711.6705
10 | 3 | 2 | 47.5 | 0 | 0 | 7.9257 | 0 | 792571428.5714 | 792571428.5714
10 | 2 | 24 | 47.5 | 0 | 0 | 7.8714 | 0 | 787142857.1429 | 787142857.1429
10 | 2 | 13 | 47.5 | 0 | 0 | 7.8171 | 0 | 781714285.7143 | 781714285.7143
8 | 17 | 4 | 47.5 | 0 | 0 | 7.22 | 0 | 722000000 | 722000000
11 | 9 | 7 | 47.5 | 0 | 0 | 7.6 | 0 | 760000000 | 760000000
11 | 10 | 22 | 47.5 | 0 | 0 | 7.4371 | 0 | 743714285.7143 | 743714285.7143
11 | 21 | 1 | 47.5 | 0 | 0 | 7.0571 | 0 | 705714285.7143 | 705714285.7143
11 | 21 | 14 | 47.5 | 0 | 0 | 7.3286 | 0 | 732857142.8571 | 732857142.8571
10 | 1 | 23 | 47.6 | 0 | 0 | 7.879 | 0 | 787899543.379 | 787899543.379
11 | 20 | 2 | 47.6 | 0 | 0 | 7.1183 | 0 | 711826484.0183 | 711826484.0183
11 | 20 | 7 | 47.6 | 0 | 0 | 7.1183 | 0 | 711826484.0183 | 711826484.0183
11 | 20 | 8 | 47.6 | 0 | 0 | 7.1183 | 0 | 711826484.0183 | 711826484.0183
11 | 20 | 23 | 47.6 | 0 | 0 | 7.0639 | 0 | 706392694.0639 | 706392694.0639
11 | 21 | 24 | 47.6 | 0 | 0 | 7.2813 | 0 | 728127853.8813 | 728127853.8813
10 | 3 | 14 | 47.7 | 0 | 0 | 7.8865 | 0 | 788654503.9909 | 788654503.9909
11 | 20 | 24 | 47.7 | 0 | 0 | 7.0707 | 0 | 707069555.3022 | 707069555.3022
11 | 22 | 6 | 47.7 | 0 | 0 | 7.3426 | 0 | 734264538.1984 | 734264538.1984
11 | 22 | 7 | 47.7 | 0 | 0 | 7.3426 | 0 | 734264538.1984 | 734264538.1984
10 | 3 | 12 | 47.8 | 0 | 0 | 7.8941 | 0 | 789407744.8747 | 789407744.8747
10 | 4 | 2 | 47.8 | 0 | 0 | 7.8941 | 0 | 789407744.8747 | 789407744.8747
11 | 20 | 1 | 47.8 | 0 | 0 | 7.1319 | 0 | 713189066.0592 | 713189066.0592
11 | 20 | 3 | 47.8 | 0 | 0 | 7.1319 | 0 | 713189066.0592 | 713189066.0592
11 | 20 | 5 | 47.8 | 0 | 0 | 7.1319 | 0 | 713189066.0592 | 713189066.0592
11 | 21 | 8 | 47.8 | 0 | 0 | 7.2408 | 0 | 724077448.7472 | 724077448.7472
11 | 21 | 13 | 47.8 | 0 | 0 | 7.2952 | 0 | 729521640.0911 | 729521640.0911
10 | 4 | 1 | 47.9 | 0 | 0 | 7.9016 | 0 | 790159271.8999 | 790159271.8999
11 | 19 | 24 | 47.9 | 0 | 0 | 7.1932 | 0 | 719317406.1433 | 719317406.1433
11 | 20 | 4 | 47.9 | 0 | 0 | 7.1387 | 0 | 713868031.8544 | 713868031.8544
11 | 21 | 9 | 47.9 | 0 | 0 | 7.1932 | 0 | 719317406.1433 | 719317406.1433
11 | 22 | 1 | 47.9 | 0 | 0 | 7.4111 | 0 | 741114903.2992 | 741114903.2992
10 | 3 | 13 | 48.1 | 0 | 0 | 7.9166 | 0 | 791657207.7185 | 791657207.7185
10 | 2 | 14 | 48.1 | 0 | 0 | 7.862 | 0 | 786197502.8377 | 786197502.8377
11 | 12 | 18 | 48.1 | 0 | 0 | 7.7528 | 0 | 775278093.0761 | 775278093.0761
11 | 20 | 6 | 48.1 | 0 | 0 | 7.1522 | 0 | 715221339.3871 | 715221339.3871
11 | 23 | 7 | 48.1 | 0 | 0 | 7.316 | 0 | 731600454.0295 | 731600454.0295
10 | 1 | 22 | 48.2 | 0 | 0 | 7.924 | 0 | 792403628.1179 | 792403628.1179
10 | 2 | 11 | 48.2 | 0 | 0 | 7.924 | 0 | 792403628.1179 | 792403628.1179
10 | 3 | 3 | 48.2 | 0 | 0 | 7.924 | 0 | 792403628.1179 | 792403628.1179
10 | 3 | 15 | 48.2 | 0 | 0 | 7.924 | 0 | 792403628.1179 | 792403628.1179
10 | 2 | 23 | 48.2 | 0 | 0 | 7.8694 | 0 | 786938775.5102 | 786938775.5102
9 | 28 | 10 | 48.2 | 0 | 0 | 7.4868 | 0 | 748684807.2562 | 748684807.2562
9 | 28 | 13 | 48.2 | 0 | 0 | 7.4868 | 0 | 748684807.2562 | 748684807.2562
11 | 10 | 23 | 48.2 | 0 | 0 | 7.5961 | 0 | 759614512.4717 | 759614512.4717
11 | 21 | 4 | 48.2 | 0 | 0 | 7.3229 | 0 | 732290249.4331 | 732290249.4331
11 | 22 | 4 | 48.2 | 0 | 0 | 7.4322 | 0 | 743219954.6485 | 743219954.6485
10 | 1 | 21 | 48.3 | 0 | 0 | 7.9315 | 0 | 793148357.8709 | 793148357.8709
10 | 4 | 5 | 48.3 | 0 | 0 | 7.9315 | 0 | 793148357.8709 | 793148357.8709
10 | 2 | 15 | 48.3 | 0 | 0 | 7.8768 | 0 | 787678369.1959 | 787678369.1959
10 | 4 | 3 | 48.3 | 0 | 0 | 7.8768 | 0 | 787678369.1959 | 787678369.1959
11 | 21 | 2 | 48.3 | 0 | 0 | 7.0563 | 0 | 705628539.0713 | 705628539.0713
11 | 22 | 2 | 48.3 | 0 | 0 | 7.3845 | 0 | 738448471.1212 | 738448471.1212
10 | 3 | 11 | 48.4 | 0 | 0 | 7.9937 | 0 | 799366515.8371 | 799366515.8371
10 | 1 | 20 | 48.4 | 0 | 0 | 7.9389 | 0 | 793891402.7149 | 793891402.7149
9 | 6 | 16 | 48.4 | 0 | 0 | 7.8842 | 0 | 788416289.5928 | 788416289.5928
10 | 4 | 4 | 48.4 | 0 | 0 | 7.8842 | 0 | 788416289.5928 | 788416289.5928
9 | 6 | 21 | 48.4 | 0 | 0 | 7.8294 | 0 | 782941176.4706 | 782941176.4706
11 | 12 | 12 | 48.4 | 0 | 0 | 7.6652 | 0 | 766515837.1041 | 766515837.1041
11 | 22 | 3 | 48.4 | 0 | 0 | 7.4462 | 0 | 744615384.6154 | 744615384.6154
9 | 5 | 12 | 48.5 | 0 | 0 | 7.8367 | 0 | 783672316.3842 | 783672316.3842
11 | 12 | 9 | 48.5 | 0 | 0 | 8.0011 | 0 | 800112994.3503 | 800112994.3503
11 | 21 | 3 | 48.5 | 0 | 0 | 7.1791 | 0 | 717909604.5198 | 717909604.5198
11 | 21 | 7 | 48.5 | 0 | 0 | 7.3435 | 0 | 734350282.4859 | 734350282.4859
10 | 1 | 24 | 48.6 | 0 | 0 | 7.9537 | 0 | 795372460.4966 | 795372460.4966
10 | 3 | 10 | 48.6 | 0 | 0 | 7.9537 | 0 | 795372460.4966 | 795372460.4966
9 | 6 | 13 | 48.6 | 0 | 0 | 7.8989 | 0 | 789887133.1828 | 789887133.1828
9 | 6 | 14 | 48.6 | 0 | 0 | 7.8989 | 0 | 789887133.1828 | 789887133.1828
9 | 6 | 17 | 48.6 | 0 | 0 | 7.8989 | 0 | 789887133.1828 | 789887133.1828
9 | 6 | 22 | 48.6 | 0 | 0 | 7.844 | 0 | 784401805.8691 | 784401805.8691
10 | 1 | 10 | 48.6 | 0 | 0 | 7.7892 | 0 | 778916478.5553 | 778916478.5553
11 | 12 | 19 | 48.6 | 0 | 0 | 7.7892 | 0 | 778916478.5553 | 778916478.5553
11 | 12 | 21 | 48.6 | 0 | 0 | 7.7343 | 0 | 773431151.2415 | 773431151.2415
11 | 21 | 5 | 48.6 | 0 | 0 | 7.2955 | 0 | 729548532.7314 | 729548532.7314
11 | 21 | 6 | 48.6 | 0 | 0 | 7.3503 | 0 | 735033860.0451 | 735033860.0451
11 | 23 | 5 | 48.6 | 0 | 0 | 7.3503 | 0 | 735033860.0451 | 735033860.0451
10 | 3 | 4 | 48.7 | 0 | 0 | 7.9611 | 0 | 796110484.7802 | 796110484.7802
9 | 5 | 14 | 48.7 | 0 | 0 | 7.9062 | 0 | 790620067.6437 | 790620067.6437
10 | 3 | 23 | 48.7 | 0 | 0 | 7.9062 | 0 | 790620067.6437 | 790620067.6437
9 | 6 | 23 | 48.7 | 0 | 0 | 7.8513 | 0 | 785129650.5073 | 785129650.5073
9 | 28 | 11 | 48.7 | 0 | 0 | 7.5768 | 0 | 757677564.8253 | 757677564.8253
10 | 3 | 24 | 48.8 | 0 | 0 | 7.9135 | 0 | 791351351.3514 | 791351351.3514
9 | 6 | 18 | 48.8 | 0 | 0 | 7.8586 | 0 | 785855855.8559 | 785855855.8559
10 | 1 | 16 | 48.8 | 0 | 0 | 7.8036 | 0 | 780360360.3604 | 780360360.3604
9 | 28 | 9 | 48.8 | 0 | 0 | 7.5838 | 0 | 758378378.3784 | 758378378.3784
11 | 23 | 8 | 48.8 | 0 | 0 | 7.364 | 0 | 736396396.3964 | 736396396.3964
10 | 2 | 21 | 48.9 | 0 | 0 | 7.9758 | 0 | 797581552.306 | 797581552.306
10 | 4 | 6 | 48.9 | 0 | 0 | 7.9758 | 0 | 797581552.306 | 797581552.306
9 | 2 | 21 | 48.9 | 0 | 0 | 7.9208 | 0 | 792080989.8763 | 792080989.8763
9 | 6 | 15 | 48.9 | 0 | 0 | 7.9208 | 0 | 792080989.8763 | 792080989.8763
10 | 1 | 17 | 48.9 | 0 | 0 | 7.9208 | 0 | 792080989.8763 | 792080989.8763
9 | 2 | 20 | 48.9 | 0 | 0 | 7.8658 | 0 | 786580427.4466 | 786580427.4466
9 | 5 | 15 | 48.9 | 0 | 0 | 7.8108 | 0 | 781079865.0169 | 781079865.0169
9 | 5 | 16 | 48.9 | 0 | 0 | 7.8108 | 0 | 781079865.0169 | 781079865.0169
11 | 11 | 5 | 48.9 | 0 | 0 | 7.8108 | 0 | 781079865.0169 | 781079865.0169
10 | 3 | 5 | 49 | 0 | 0 | 8.0382 | 0 | 803820224.7191 | 803820224.7191
9 | 3 | 9 | 49 | 0 | 0 | 7.9831 | 0 | 798314606.7416 | 798314606.7416
10 | 2 | 1 | 49 | 0 | 0 | 7.9831 | 0 | 798314606.7416 | 798314606.7416
10 | 2 | 16 | 49 | 0 | 0 | 7.9281 | 0 | 792808988.764 | 792808988.764
10 | 3 | 16 | 49 | 0 | 0 | 7.9281 | 0 | 792808988.764 | 792808988.764
11 | 9 | 4 | 49 | 0 | 0 | 7.7079 | 0 | 770786516.8539 | 770786516.8539
10 | 1 | 18 | 49.1 | 0 | 0 | 7.9905 | 0 | 799046015.7127 | 799046015.7127
10 | 2 | 22 | 49.1 | 0 | 0 | 7.9905 | 0 | 799046015.7127 | 799046015.7127
10 | 3 | 17 | 49.1 | 0 | 0 | 7.9354 | 0 | 793535353.5354 | 793535353.5354
9 | 6 | 11 | 49.1 | 0 | 0 | 7.8802 | 0 | 788024691.358 | 788024691.358
9 | 6 | 12 | 49.1 | 0 | 0 | 7.8802 | 0 | 788024691.358 | 788024691.358
11 | 12 | 11 | 49.1 | 0 | 0 | 7.77 | 0 | 777003367.0034 | 777003367.0034
9 | 5 | 20 | 49.2 | 0 | 0 | 7.8874 | 0 | 788744394.6188 | 788744394.6188
9 | 5 | 23 | 49.2 | 0 | 0 | 7.8874 | 0 | 788744394.6188 | 788744394.6188
9 | 6 | 20 | 49.2 | 0 | 0 | 7.8874 | 0 | 788744394.6188 | 788744394.6188
9 | 28 | 12 | 49.2 | 0 | 0 | 7.6117 | 0 | 761165919.2825 | 761165919.2825
11 | 11 | 16 | 49.2 | 0 | 0 | 7.7771 | 0 | 777713004.4843 | 777713004.4843
11 | 16 | 2 | 49.2 | 0 | 0 | 7.9426 | 0 | 794260089.6861 | 794260089.6861
11 | 28 | 20 | 49.2 | 0 | 0 | 7.6668 | 0 | 766681614.3498 | 766681614.3498
9 | 6 | 19 | 49.3 | 0 | 0 | 7.8946 | 0 | 789462486.0022 | 789462486.0022
11 | 12 | 20 | 49.3 | 0 | 0 | 7.7842 | 0 | 778421052.6316 | 778421052.6316
11 | 23 | 1 | 49.3 | 0 | 0 | 7.3978 | 0 | 739776035.8343 | 739776035.8343
11 | 23 | 2 | 49.3 | 0 | 0 | 7.3978 | 0 | 739776035.8343 | 739776035.8343
11 | 23 | 3 | 49.3 | 0 | 0 | 7.3978 | 0 | 739776035.8343 | 739776035.8343
11 | 23 | 4 | 49.3 | 0 | 0 | 7.3978 | 0 | 739776035.8343 | 739776035.8343
10 | 2 | 10 | 49.4 | 0 | 0 | 8.0123 | 0 | 801230425.0559 | 801230425.0559
9 | 5 | 13 | 49.4 | 0 | 0 | 7.957 | 0 | 795704697.9866 | 795704697.9866
10 | 3 | 22 | 49.4 | 0 | 0 | 7.957 | 0 | 795704697.9866 | 795704697.9866
9 | 5 | 21 | 49.4 | 0 | 0 | 7.9018 | 0 | 790178970.9172 | 790178970.9172
9 | 5 | 17 | 49.4 | 0 | 0 | 7.8465 | 0 | 784653243.8479 | 784653243.8479
11 | 11 | 3 | 49.4 | 0 | 0 | 7.9018 | 0 | 790178970.9172 | 790178970.9172
11 | 25 | 18 | 49.4 | 0 | 0 | 7.6808 | 0 | 768076062.6398 | 768076062.6398
11 | 28 | 19 | 49.4 | 0 | 0 | 7.5702 | 0 | 757024608.5011 | 757024608.5011
10 | 1 | 19 | 49.5 | 0 | 0 | 8.0196 | 0 | 801955307.2626 | 801955307.2626
10 | 2 | 2 | 49.5 | 0 | 0 | 8.0196 | 0 | 801955307.2626 | 801955307.2626
9 | 5 | 11 | 49.5 | 0 | 0 | 7.9642 | 0 | 796424581.0056 | 796424581.0056
10 | 2 | 19 | 49.5 | 0 | 0 | 7.9642 | 0 | 796424581.0056 | 796424581.0056
10 | 3 | 19 | 49.5 | 0 | 0 | 7.9642 | 0 | 796424581.0056 | 796424581.0056
10 | 1 | 9 | 49.5 | 0 | 0 | 7.9089 | 0 | 790893854.7486 | 790893854.7486
9 | 5 | 18 | 49.5 | 0 | 0 | 7.8536 | 0 | 785363128.4916 | 785363128.4916
11 | 9 | 5 | 49.5 | 0 | 0 | 7.743 | 0 | 774301675.9777 | 774301675.9777
11 | 9 | 6 | 49.5 | 0 | 0 | 7.7983 | 0 | 779832402.2346 | 779832402.2346
11 | 11 | 4 | 49.5 | 0 | 0 | 7.8536 | 0 | 785363128.4916 | 785363128.4916
11 | 12 | 13 | 49.5 | 0 | 0 | 7.743 | 0 | 774301675.9777 | 774301675.9777
11 | 15 | 12 | 49.5 | 0 | 0 | 7.9089 | 0 | 790893854.7486 | 790893854.7486
11 | 23 | 13 | 49.5 | 0 | 0 | 7.6877 | 0 | 768770949.7207 | 768770949.7207
11 | 25 | 19 | 49.5 | 0 | 0 | 7.6324 | 0 | 763240223.4637 | 763240223.4637
11 | 25 | 20 | 49.5 | 0 | 0 | 7.6324 | 0 | 763240223.4637 | 763240223.4637
11 | 25 | 21 | 49.5 | 0 | 0 | 7.6324 | 0 | 763240223.4637 | 763240223.4637
11 | 28 | 23 | 49.5 | 0 | 0 | 7.6877 | 0 | 768770949.7207 | 768770949.7207
10 | 2 | 20 | 49.6 | 0 | 0 | 8.0268 | 0 | 802678571.4286 | 802678571.4286
10 | 3 | 6 | 49.6 | 0 | 0 | 8.0268 | 0 | 802678571.4286 | 802678571.4286
9 | 2 | 22 | 49.6 | 0 | 0 | 7.9714 | 0 | 797142857.1429 | 797142857.1429
11 | 12 | 17 | 49.6 | 0 | 0 | 7.8054 | 0 | 780535714.2857 | 780535714.2857
11 | 14 | 18 | 49.6 | 0 | 0 | 7.6393 | 0 | 763928571.4286 | 763928571.4286
11 | 28 | 18 | 49.6 | 0 | 0 | 7.6393 | 0 | 763928571.4286 | 763928571.4286
10 | 2 | 3 | 49.7 | 0 | 0 | 8.034 | 0 | 803400222.9654 | 803400222.9654
9 | 2 | 19 | 49.7 | 0 | 0 | 7.9232 | 0 | 792318840.5797 | 792318840.5797
9 | 5 | 19 | 49.7 | 0 | 0 | 7.8678 | 0 | 786778149.3868 | 786778149.3868
9 | 6 | 10 | 49.7 | 0 | 0 | 7.8678 | 0 | 786778149.3868 | 786778149.3868
11 | 15 | 10 | 49.7 | 0 | 0 | 7.8124 | 0 | 781237458.194 | 781237458.194
11 | 15 | 11 | 49.7 | 0 | 0 | 7.8678 | 0 | 786778149.3868 | 786778149.3868
11 | 15 | 13 | 49.7 | 0 | 0 | 7.8678 | 0 | 786778149.3868 | 786778149.3868
11 | 28 | 22 | 49.7 | 0 | 0 | 7.6462 | 0 | 764615384.6154 | 764615384.6154
9 | 5 | 10 | 49.8 | 0 | 0 | 7.9303 | 0 | 793028953.2294 | 793028953.2294
9 | 5 | 22 | 49.8 | 0 | 0 | 7.9303 | 0 | 793028953.2294 | 793028953.2294
11 | 12 | 10 | 49.8 | 0 | 0 | 7.9857 | 0 | 798574610.245 | 798574610.245
11 | 14 | 19 | 49.8 | 0 | 0 | 7.653 | 0 | 765300668.1514 | 765300668.1514
11 | 28 | 21 | 49.8 | 0 | 0 | 7.653 | 0 | 765300668.1514 | 765300668.1514
10 | 3 | 9 | 49.9 | 0 | 0 | 8.0484 | 0 | 804838709.6774 | 804838709.6774
11 | 11 | 22 | 49.9 | 0 | 0 | 7.8264 | 0 | 782636262.5139 | 782636262.5139
11 | 11 | 23 | 49.9 | 0 | 0 | 7.8819 | 0 | 788186874.3048 | 788186874.3048
11 | 15 | 9 | 49.9 | 0 | 0 | 7.8264 | 0 | 782636262.5139 | 782636262.5139
11 | 15 | 14 | 49.9 | 0 | 0 | 7.9374 | 0 | 793737486.0957 | 793737486.0957
11 | 15 | 16 | 49.9 | 0 | 0 | 7.8264 | 0 | 782636262.5139 | 782636262.5139
11 | 27 | 23 | 49.9 | 0 | 0 | 7.5488 | 0 | 754883203.5595 | 754883203.5595
10 | 2 | 4 | 50 | 0 | 0 | 8.0556 | 0 | 805555555.5556 | 805555555.5556
10 | 3 | 18 | 50 | 0 | 0 | 8.0556 | 0 | 805555555.5556 | 805555555.5556
10 | 2 | 18 | 50 | 0 | 0 | 8 | 0 | 800000000 | 800000000
10 | 4 | 7 | 50 | 0 | 0 | 8 | 0 | 800000000 | 800000000
9 | 30 | 24 | 50 | 0 | 0 | 7.7778 | 0 | 777777777.7778 | 777777777.7778
11 | 27 | 21 | 50 | 0 | 0 | 7.6111 | 0 | 761111111.1111 | 761111111.1111
11 | 27 | 22 | 50 | 0 | 0 | 7.6667 | 0 | 766666666.6667 | 766666666.6667
11 | 29 | 9 | 50 | 0 | 0 | 7.6667 | 0 | 766666666.6667 | 766666666.6667
9 | 2 | 18 | 50.1 | 0 | 0 | 8.0627 | 0 | 806270810.2109 | 806270810.2109
10 | 2 | 17 | 50.1 | 0 | 0 | 8.0071 | 0 | 800710321.8646 | 800710321.8646
10 | 3 | 20 | 50.1 | 0 | 0 | 8.0071 | 0 | 800710321.8646 | 800710321.8646
10 | 1 | 8 | 50.1 | 0 | 0 | 7.9515 | 0 | 795149833.5183 | 795149833.5183
11 | 15 | 15 | 50.1 | 0 | 0 | 7.8403 | 0 | 784028856.8257 | 784028856.8257
10 | 2 | 9 | 50.2 | 0 | 0 | 8.0698 | 0 | 806984478.9357 | 806984478.9357
10 | 3 | 7 | 50.2 | 0 | 0 | 8.0698 | 0 | 806984478.9357 | 806984478.9357
10 | 3 | 8 | 50.2 | 0 | 0 | 8.0142 | 0 | 801419068.7361 | 801419068.7361
11 | 11 | 2 | 50.2 | 0 | 0 | 7.8472 | 0 | 784722838.1375 | 784722838.1375
11 | 11 | 21 | 50.2 | 0 | 0 | 7.8472 | 0 | 784722838.1375 | 784722838.1375
11 | 14 | 20 | 50.2 | 0 | 0 | 7.6803 | 0 | 768026607.5388 | 768026607.5388
11 | 23 | 20 | 50.2 | 0 | 0 | 7.569 | 0 | 756895787.1397 | 756895787.1397
11 | 25 | 22 | 50.2 | 0 | 0 | 7.6803 | 0 | 768026607.5388 | 768026607.5388
11 | 29 | 10 | 50.2 | 0 | 0 | 7.7359 | 0 | 773592017.7384 | 773592017.7384
9 | 3 | 6 | 50.3 | 0 | 0 | 8.0213 | 0 | 802126245.8472 | 802126245.8472
10 | 3 | 21 | 50.3 | 0 | 0 | 8.0213 | 0 | 802126245.8472 | 802126245.8472
10 | 1 | 1 | 50.3 | 0 | 0 | 7.8542 | 0 | 785415282.392 | 785415282.392
11 | 12 | 16 | 50.3 | 0 | 0 | 7.8542 | 0 | 785415282.392 | 785415282.392
10 | 4 | 15 | 50.4 | 0 | 0 | 8.2513 | 0 | 825132743.3628 | 825132743.3628
9 | 7 | 4 | 50.4 | 0 | 0 | 8.0841 | 0 | 808407079.646 | 808407079.646
9 | 3 | 8 | 50.4 | 0 | 0 | 8.0283 | 0 | 802831858.4071 | 802831858.4071
11 | 12 | 15 | 50.4 | 0 | 0 | 7.8611 | 0 | 786106194.6903 | 786106194.6903
11 | 13 | 19 | 50.4 | 0 | 0 | 7.6381 | 0 | 763805309.7345 | 763805309.7345
11 | 13 | 21 | 50.4 | 0 | 0 | 7.6938 | 0 | 769380530.9735 | 769380530.9735
11 | 13 | 22 | 50.4 | 0 | 0 | 7.6381 | 0 | 763805309.7345 | 763805309.7345
11 | 23 | 14 | 50.4 | 0 | 0 | 7.7496 | 0 | 774955752.2124 | 774955752.2124
11 | 28 | 10 | 50.4 | 0 | 0 | 7.7496 | 0 | 774955752.2124 | 774955752.2124
11 | 29 | 11 | 50.4 | 0 | 0 | 7.7496 | 0 | 774955752.2124 | 774955752.2124
10 | 2 | 8 | 50.5 | 0 | 0 | 8.0912 | 0 | 809116022.0994 | 809116022.0994
9 | 7 | 3 | 50.5 | 0 | 0 | 8.0354 | 0 | 803535911.6022 | 803535911.6022
11 | 12 | 14 | 50.5 | 0 | 0 | 7.868 | 0 | 786795580.1105 | 786795580.1105
11 | 13 | 20 | 50.5 | 0 | 0 | 7.589 | 0 | 758895027.6243 | 758895027.6243
11 | 25 | 23 | 50.5 | 0 | 0 | 7.6448 | 0 | 764475138.1215 | 764475138.1215
11 | 28 | 11 | 50.5 | 0 | 0 | 7.7006 | 0 | 770055248.6188 | 770055248.6188
10 | 4 | 14 | 50.6 | 0 | 0 | 8.2658 | 0 | 826578366.4459 | 826578366.4459
9 | 5 | 3 | 50.6 | 0 | 0 | 7.9307 | 0 | 793068432.6711 | 793068432.6711
11 | 23 | 22 | 50.6 | 0 | 0 | 7.6514 | 0 | 765143487.8587 | 765143487.8587
11 | 27 | 19 | 50.6 | 0 | 0 | 7.6514 | 0 | 765143487.8587 | 765143487.8587
11 | 27 | 20 | 50.6 | 0 | 0 | 7.6514 | 0 | 765143487.8587 | 765143487.8587
9 | 5 | 24 | 50.7 | 0 | 0 | 8.0494 | 0 | 804939360.5292 | 804939360.5292
9 | 6 | 24 | 50.7 | 0 | 0 | 8.0494 | 0 | 804939360.5292 | 804939360.5292
8 | 5 | 4 | 50.7 | 0 | 0 | 7.8258 | 0 | 782579933.8478 | 782579933.8478
11 | 23 | 21 | 50.7 | 0 | 0 | 7.6581 | 0 | 765810363.8368 | 765810363.8368
11 | 25 | 17 | 50.7 | 0 | 0 | 7.8258 | 0 | 782579933.8478 | 782579933.8478
9 | 6 | 2 | 50.8 | 0 | 0 | 8.0004 | 0 | 800044052.8634 | 800044052.8634
9 | 5 | 9 | 50.8 | 0 | 0 | 7.9445 | 0 | 794449339.207 | 794449339.207
8 | 5 | 5 | 50.8 | 0 | 0 | 7.8326 | 0 | 783259911.8943 | 783259911.8943
11 | 12 | 22 | 50.8 | 0 | 0 | 7.8326 | 0 | 783259911.8943 | 783259911.8943
11 | 12 | 23 | 50.8 | 0 | 0 | 7.7767 | 0 | 777665198.2379 | 777665198.2379
11 | 24 | 6 | 50.8 | 0 | 0 | 7.7207 | 0 | 772070484.5815 | 772070484.5815
11 | 28 | 9 | 50.8 | 0 | 0 | 7.7767 | 0 | 777665198.2379 | 777665198.2379
9 | 3 | 7 | 50.9 | 0 | 0 | 8.0074 | 0 | 800737073.7074 | 800737073.7074
9 | 5 | 2 | 50.9 | 0 | 0 | 8.0074 | 0 | 800737073.7074 | 800737073.7074
11 | 11 | 1 | 50.9 | 0 | 0 | 7.8394 | 0 | 783938393.8394 | 783938393.8394
11 | 24 | 8 | 50.9 | 0 | 0 | 7.7274 | 0 | 772739273.9274 | 772739273.9274
11 | 28 | 15 | 50.9 | 0 | 0 | 7.8394 | 0 | 783938393.8394 | 783938393.8394
11 | 28 | 17 | 50.9 | 0 | 0 | 7.7274 | 0 | 772739273.9274 | 772739273.9274
11 | 29 | 15 | 50.9 | 0 | 0 | 7.7834 | 0 | 778338833.8834 | 778338833.8834
10 | 4 | 13 | 51 | 0 | 0 | 8.2945 | 0 | 829450549.4505 | 829450549.4505
11 | 23 | 23 | 51 | 0 | 0 | 7.678 | 0 | 767802197.8022 | 767802197.8022
9 | 3 | 3 | 51.1 | 0 | 0 | 8.0773 | 0 | 807727771.6795 | 807727771.6795
9 | 3 | 5 | 51.1 | 0 | 0 | 8.0773 | 0 | 807727771.6795 | 807727771.6795
9 | 4 | 12 | 51.1 | 0 | 0 | 8.0773 | 0 | 807727771.6795 | 807727771.6795
9 | 2 | 23 | 51.1 | 0 | 0 | 8.0212 | 0 | 802118551.0428 | 802118551.0428
9 | 4 | 14 | 51.1 | 0 | 0 | 7.9651 | 0 | 796509330.4061 | 796509330.4061
9 | 5 | 4 | 51.1 | 0 | 0 | 7.9651 | 0 | 796509330.4061 | 796509330.4061
9 | 6 | 4 | 51.1 | 0 | 0 | 7.9651 | 0 | 796509330.4061 | 796509330.4061
9 | 6 | 8 | 51.1 | 0 | 0 | 7.9651 | 0 | 796509330.4061 | 796509330.4061
10 | 1 | 2 | 51.1 | 0 | 0 | 7.9651 | 0 | 796509330.4061 | 796509330.4061
11 | 13 | 18 | 51.1 | 0 | 0 | 7.6846 | 0 | 768463227.2228 | 768463227.2228
11 | 15 | 8 | 51.1 | 0 | 0 | 7.909 | 0 | 790900109.7695 | 790900109.7695
11 | 28 | 13 | 51.1 | 0 | 0 | 7.6846 | 0 | 768463227.2228 | 768463227.2228
11 | 28 | 14 | 51.1 | 0 | 0 | 7.7968 | 0 | 779681668.4962 | 779681668.4962
9 | 2 | 24 | 51.2 | 0 | 0 | 8.0281 | 0 | 802807017.5439 | 802807017.5439
9 | 4 | 21 | 51.2 | 0 | 0 | 8.0281 | 0 | 802807017.5439 | 802807017.5439
9 | 5 | 1 | 51.2 | 0 | 0 | 7.9719 | 0 | 797192982.4561 | 797192982.4561
11 | 23 | 15 | 51.2 | 0 | 0 | 7.8035 | 0 | 780350877.193 | 780350877.193
11 | 27 | 24 | 51.2 | 0 | 0 | 7.7474 | 0 | 774736842.1053 | 774736842.1053
11 | 28 | 8 | 51.2 | 0 | 0 | 7.7474 | 0 | 774736842.1053 | 774736842.1053
11 | 28 | 12 | 51.2 | 0 | 0 | 7.6912 | 0 | 769122807.0175 | 769122807.0175
11 | 29 | 13 | 51.2 | 0 | 0 | 7.8035 | 0 | 780350877.193 | 780350877.193
11 | 29 | 14 | 51.2 | 0 | 0 | 7.8035 | 0 | 780350877.193 | 780350877.193
10 | 2 | 5 | 51.3 | 0 | 0 | 8.1473 | 0 | 814731653.8883 | 814731653.8883
10 | 2 | 7 | 51.3 | 0 | 0 | 8.1473 | 0 | 814731653.8883 | 814731653.8883
9 | 3 | 2 | 51.3 | 0 | 0 | 8.0349 | 0 | 803493975.9036 | 803493975.9036
9 | 5 | 5 | 51.3 | 0 | 0 | 7.9788 | 0 | 797875136.9113 | 797875136.9113
9 | 6 | 5 | 51.3 | 0 | 0 | 7.9788 | 0 | 797875136.9113 | 797875136.9113
11 | 12 | 24 | 51.3 | 0 | 0 | 7.8102 | 0 | 781018619.9343 | 781018619.9343
11 | 27 | 15 | 51.3 | 0 | 0 | 7.5854 | 0 | 758543263.965 | 758543263.965
11 | 27 | 16 | 51.3 | 0 | 0 | 7.6978 | 0 | 769780941.9496 | 769780941.9496
11 | 29 | 3 | 51.3 | 0 | 0 | 7.8664 | 0 | 786637458.9266 | 786637458.9266
11 | 29 | 4 | 51.3 | 0 | 0 | 7.8102 | 0 | 781018619.9343 | 781018619.9343
11 | 29 | 5 | 51.3 | 0 | 0 | 7.8664 | 0 | 786637458.9266 | 786637458.9266
10 | 4 | 16 | 51.4 | 0 | 0 | 8.323 | 0 | 832297592.9978 | 832297592.9978
8 | 23 | 5 | 51.4 | 0 | 0 | 8.098 | 0 | 809803063.4573 | 809803063.4573
9 | 3 | 4 | 51.4 | 0 | 0 | 8.098 | 0 | 809803063.4573 | 809803063.4573
9 | 3 | 1 | 51.4 | 0 | 0 | 8.0418 | 0 | 804179431.0722 | 804179431.0722
9 | 4 | 24 | 51.4 | 0 | 0 | 7.9856 | 0 | 798555798.6871 | 798555798.6871
9 | 6 | 3 | 51.4 | 0 | 0 | 7.9856 | 0 | 798555798.6871 | 798555798.6871
12 | 8 | 13 | 51.4 | 0 | 0 | 7.8168 | 0 | 781684901.5317 | 781684901.5317
12 | 9 | 9 | 51.4 | 0 | 0 | 7.9293 | 0 | 792932166.302 | 792932166.302
11 | 26 | 8 | 51.4 | 0 | 0 | 7.7044 | 0 | 770437636.7615 | 770437636.7615
11 | 26 | 9 | 51.4 | 0 | 0 | 7.7044 | 0 | 770437636.7615 | 770437636.7615
9 | 7 | 2 | 51.5 | 0 | 0 | 8.0486 | 0 | 804863387.9781 | 804863387.9781
9 | 4 | 17 | 51.5 | 0 | 0 | 7.9923 | 0 | 799234972.6776 | 799234972.6776
9 | 4 | 23 | 51.5 | 0 | 0 | 7.9923 | 0 | 799234972.6776 | 799234972.6776
9 | 6 | 6 | 51.5 | 0 | 0 | 7.9923 | 0 | 799234972.6776 | 799234972.6776
11 | 14 | 12 | 51.5 | 0 | 0 | 7.7672 | 0 | 776721311.4754 | 776721311.4754
11 | 26 | 22 | 51.5 | 0 | 0 | 7.7109 | 0 | 771092896.1749 | 771092896.1749
9 | 7 | 1 | 51.6 | 0 | 0 | 8.1118 | 0 | 811179039.3013 | 811179039.3013
9 | 4 | 20 | 51.6 | 0 | 0 | 7.9991 | 0 | 799912663.7555 | 799912663.7555
9 | 6 | 9 | 51.6 | 0 | 0 | 7.9991 | 0 | 799912663.7555 | 799912663.7555
11 | 24 | 7 | 51.6 | 0 | 0 | 7.7738 | 0 | 777379912.6638 | 777379912.6638
11 | 25 | 24 | 51.6 | 0 | 0 | 7.7175 | 0 | 771746724.8908 | 771746724.8908
11 | 26 | 11 | 51.6 | 0 | 0 | 7.7175 | 0 | 771746724.8908 | 771746724.8908
11 | 26 | 20 | 51.6 | 0 | 0 | 7.7175 | 0 | 771746724.8908 | 771746724.8908
11 | 28 | 7 | 51.6 | 0 | 0 | 7.7738 | 0 | 777379912.6638 | 777379912.6638
11 | 28 | 16 | 51.6 | 0 | 0 | 7.7738 | 0 | 777379912.6638 | 777379912.6638
11 | 29 | 2 | 51.6 | 0 | 0 | 7.8865 | 0 | 788646288.2096 | 788646288.2096
11 | 29 | 16 | 51.6 | 0 | 0 | 7.8301 | 0 | 783013100.4367 | 783013100.4367
9 | 4 | 22 | 51.7 | 0 | 0 | 8.0059 | 0 | 800588876.7721 | 800588876.7721
12 | 8 | 15 | 51.7 | 0 | 0 | 7.8368 | 0 | 783675027.2628 | 783675027.2628
11 | 16 | 24 | 51.7 | 0 | 0 | 7.8931 | 0 | 789312977.0992 | 789312977.0992
11 | 17 | 1 | 51.7 | 0 | 0 | 7.8931 | 0 | 789312977.0992 | 789312977.0992
11 | 24 | 5 | 51.7 | 0 | 0 | 7.724 | 0 | 772399127.59 | 772399127.59
11 | 26 | 4 | 51.7 | 0 | 0 | 7.724 | 0 | 772399127.59 | 772399127.59
11 | 26 | 6 | 51.7 | 0 | 0 | 7.7804 | 0 | 778037077.4264 | 778037077.4264
11 | 26 | 7 | 51.7 | 0 | 0 | 7.724 | 0 | 772399127.59 | 772399127.59
11 | 26 | 21 | 51.7 | 0 | 0 | 7.724 | 0 | 772399127.59 | 772399127.59
11 | 29 | 1 | 51.7 | 0 | 0 | 7.8931 | 0 | 789312977.0992 | 789312977.0992
10 | 4 | 18 | 51.8 | 0 | 0 | 8.3512 | 0 | 835119825.7081 | 835119825.7081
9 | 6 | 1 | 51.8 | 0 | 0 | 8.1255 | 0 | 812549019.6078 | 812549019.6078
9 | 4 | 13 | 51.8 | 0 | 0 | 8.0691 | 0 | 806906318.0828 | 806906318.0828
9 | 5 | 6 | 51.8 | 0 | 0 | 8.0126 | 0 | 801263616.5577 | 801263616.5577
10 | 1 | 7 | 51.8 | 0 | 0 | 8.0126 | 0 | 801263616.5577 | 801263616.5577
10 | 1 | 3 | 51.8 | 0 | 0 | 7.9562 | 0 | 795620915.0327 | 795620915.0327
12 | 8 | 14 | 51.8 | 0 | 0 | 7.7869 | 0 | 778692810.4575 | 778692810.4575
12 | 9 | 10 | 51.8 | 0 | 0 | 7.8998 | 0 | 789978213.5076 | 789978213.5076
11 | 13 | 9 | 51.8 | 0 | 0 | 7.7305 | 0 | 773050108.9325 | 773050108.9325
11 | 14 | 17 | 51.8 | 0 | 0 | 7.7869 | 0 | 778692810.4575 | 778692810.4575
11 | 26 | 10 | 51.8 | 0 | 0 | 7.7305 | 0 | 773050108.9325 | 773050108.9325
11 | 26 | 12 | 51.8 | 0 | 0 | 7.7305 | 0 | 773050108.9325 | 773050108.9325
11 | 26 | 13 | 51.8 | 0 | 0 | 7.7305 | 0 | 773050108.9325 | 773050108.9325
11 | 26 | 18 | 51.8 | 0 | 0 | 7.7305 | 0 | 773050108.9325 | 773050108.9325
11 | 28 | 24 | 51.8 | 0 | 0 | 7.8434 | 0 | 784335511.9826 | 784335511.9826
10 | 4 | 17 | 51.9 | 0 | 0 | 8.3582 | 0 | 835821545.1578 | 835821545.1578
10 | 2 | 6 | 51.9 | 0 | 0 | 8.1888 | 0 | 818879216.5397 | 818879216.5397
9 | 4 | 15 | 51.9 | 0 | 0 | 8.0194 | 0 | 801936887.9217 | 801936887.9217
9 | 4 | 16 | 51.9 | 0 | 0 | 8.0194 | 0 | 801936887.9217 | 801936887.9217
9 | 4 | 18 | 51.9 | 0 | 0 | 8.0194 | 0 | 801936887.9217 | 801936887.9217
9 | 6 | 7 | 51.9 | 0 | 0 | 8.0194 | 0 | 801936887.9217 | 801936887.9217
12 | 8 | 12 | 51.9 | 0 | 0 | 7.8499 | 0 | 784994559.3036 | 784994559.3036
11 | 13 | 17 | 51.9 | 0 | 0 | 7.737 | 0 | 773699673.5582 | 773699673.5582
11 | 14 | 13 | 51.9 | 0 | 0 | 7.7935 | 0 | 779347116.4309 | 779347116.4309
11 | 24 | 4 | 51.9 | 0 | 0 | 7.737 | 0 | 773699673.5582 | 773699673.5582
11 | 26 | 2 | 51.9 | 0 | 0 | 7.737 | 0 | 773699673.5582 | 773699673.5582
11 | 26 | 15 | 51.9 | 0 | 0 | 7.737 | 0 | 773699673.5582 | 773699673.5582
11 | 26 | 19 | 51.9 | 0 | 0 | 7.737 | 0 | 773699673.5582 | 773699673.5582
11 | 28 | 4 | 51.9 | 0 | 0 | 7.7935 | 0 | 779347116.4309 | 779347116.4309
9 | 4 | 9 | 52 | 0 | 0 | 8.0826 | 0 | 808260869.5652 | 808260869.5652
9 | 5 | 7 | 52 | 0 | 0 | 8.0261 | 0 | 802608695.6522 | 802608695.6522
9 | 5 | 8 | 52 | 0 | 0 | 8.0261 | 0 | 802608695.6522 | 802608695.6522
12 | 9 | 8 | 52 | 0 | 0 | 8.0826 | 0 | 808260869.5652 | 808260869.5652
11 | 17 | 2 | 52 | 0 | 0 | 7.913 | 0 | 791304347.8261 | 791304347.8261
11 | 28 | 6 | 52 | 0 | 0 | 7.8 | 0 | 780000000 | 780000000
11 | 25 | 7 | 52.1 | 0 | 0 | 7.6934 | 0 | 769337676.4387 | 769337676.4387
11 | 25 | 11 | 52.1 | 0 | 0 | 7.6934 | 0 | 769337676.4387 | 769337676.4387
11 | 26 | 1 | 52.1 | 0 | 0 | 7.7499 | 0 | 774994571.1183 | 774994571.1183
11 | 26 | 3 | 52.1 | 0 | 0 | 7.7499 | 0 | 774994571.1183 | 774994571.1183
10 | 4 | 12 | 52.2 | 0 | 0 | 8.3792 | 0 | 837917570.4989 | 837917570.4989
9 | 4 | 19 | 52.2 | 0 | 0 | 8.0395 | 0 | 803947939.2625 | 803947939.2625
11 | 13 | 10 | 52.2 | 0 | 0 | 7.7564 | 0 | 775639913.2321 | 775639913.2321
11 | 14 | 21 | 52.2 | 0 | 0 | 7.813 | 0 | 781301518.4382 | 781301518.4382
11 | 24 | 1 | 52.2 | 0 | 0 | 7.7564 | 0 | 775639913.2321 | 775639913.2321
11 | 24 | 24 | 52.2 | 0 | 0 | 7.7564 | 0 | 775639913.2321 | 775639913.2321
11 | 25 | 10 | 52.2 | 0 | 0 | 7.6998 | 0 | 769978308.026 | 769978308.026
11 | 25 | 16 | 52.2 | 0 | 0 | 7.813 | 0 | 781301518.4382 | 781301518.4382
11 | 26 | 5 | 52.2 | 0 | 0 | 7.7564 | 0 | 775639913.2321 | 775639913.2321
11 | 26 | 17 | 52.2 | 0 | 0 | 7.7564 | 0 | 775639913.2321 | 775639913.2321
11 | 28 | 5 | 52.2 | 0 | 0 | 7.813 | 0 | 781301518.4382 | 781301518.4382
11 | 13 | 11 | 52.3 | 0 | 0 | 7.7628 | 0 | 776283856.9881 | 776283856.9881
11 | 14 | 22 | 52.3 | 0 | 0 | 7.8195 | 0 | 781950162.5135 | 781950162.5135
11 | 25 | 13 | 52.3 | 0 | 0 | 7.7062 | 0 | 770617551.4626 | 770617551.4626
11 | 26 | 14 | 52.3 | 0 | 0 | 7.7628 | 0 | 776283856.9881 | 776283856.9881
11 | 28 | 1 | 52.3 | 0 | 0 | 7.8195 | 0 | 781950162.5135 | 781950162.5135
11 | 28 | 2 | 52.3 | 0 | 0 | 7.8195 | 0 | 781950162.5135 | 781950162.5135
12 | 8 | 23 | 52.4 | 0 | 0 | 7.9394 | 0 | 793939393.9394 | 793939393.9394
11 | 14 | 2 | 52.4 | 0 | 0 | 7.826 | 0 | 782597402.5974 | 782597402.5974
11 | 14 | 11 | 52.4 | 0 | 0 | 7.826 | 0 | 782597402.5974 | 782597402.5974
11 | 14 | 14 | 52.4 | 0 | 0 | 7.826 | 0 | 782597402.5974 | 782597402.5974
11 | 25 | 8 | 52.4 | 0 | 0 | 7.7126 | 0 | 771255411.2554 | 771255411.2554
11 | 25 | 9 | 52.4 | 0 | 0 | 7.7126 | 0 | 771255411.2554 | 771255411.2554
11 | 25 | 14 | 52.4 | 0 | 0 | 7.7693 | 0 | 776926406.9264 | 776926406.9264
11 | 26 | 23 | 52.4 | 0 | 0 | 7.7693 | 0 | 776926406.9264 | 776926406.9264
11 | 28 | 3 | 52.4 | 0 | 0 | 7.8827 | 0 | 788268398.2684 | 788268398.2684
10 | 1 | 6 | 52.5 | 0 | 0 | 8.0595 | 0 | 805945945.9459 | 805945945.9459
12 | 4 | 12 | 52.5 | 0 | 0 | 7.9459 | 0 | 794594594.5946 | 794594594.5946
12 | 4 | 13 | 52.5 | 0 | 0 | 7.9459 | 0 | 794594594.5946 | 794594594.5946
11 | 15 | 6 | 52.5 | 0 | 0 | 7.9459 | 0 | 794594594.5946 | 794594594.5946
11 | 24 | 2 | 52.5 | 0 | 0 | 7.8324 | 0 | 783243243.2432 | 783243243.2432
11 | 26 | 16 | 52.5 | 0 | 0 | 7.7757 | 0 | 777567567.5676 | 777567567.5676
11 | 27 | 7 | 52.5 | 0 | 0 | 7.7189 | 0 | 771891891.8919 | 771891891.8919
9 | 4 | 8 | 52.6 | 0 | 0 | 8.1229 | 0 | 812289416.8467 | 812289416.8467
12 | 4 | 14 | 52.6 | 0 | 0 | 7.9525 | 0 | 795248380.1296 | 795248380.1296
12 | 8 | 16 | 52.6 | 0 | 0 | 7.8957 | 0 | 789568034.5572 | 789568034.5572
11 | 13 | 1 | 52.6 | 0 | 0 | 7.8957 | 0 | 789568034.5572 | 789568034.5572
11 | 14 | 23 | 52.6 | 0 | 0 | 7.8389 | 0 | 783887688.9849 | 783887688.9849
11 | 15 | 7 | 52.6 | 0 | 0 | 7.9525 | 0 | 795248380.1296 | 795248380.1296
11 | 23 | 24 | 52.6 | 0 | 0 | 7.7821 | 0 | 778207343.4125 | 778207343.4125
11 | 25 | 5 | 52.6 | 0 | 0 | 7.7821 | 0 | 778207343.4125 | 778207343.4125
11 | 25 | 12 | 52.6 | 0 | 0 | 7.7253 | 0 | 772526997.8402 | 772526997.8402
11 | 26 | 24 | 52.6 | 0 | 0 | 7.7821 | 0 | 778207343.4125 | 778207343.4125
11 | 27 | 3 | 52.6 | 0 | 0 | 7.7821 | 0 | 778207343.4125 | 778207343.4125
10 | 4 | 11 | 52.7 | 0 | 0 | 8.4138 | 0 | 841380798.274 | 841380798.274
11 | 12 | 5 | 52.7 | 0 | 0 | 8.1864 | 0 | 818640776.699 | 818640776.699
11 | 14 | 1 | 52.7 | 0 | 0 | 7.8453 | 0 | 784530744.3366 | 784530744.3366
11 | 14 | 10 | 52.7 | 0 | 0 | 7.7885 | 0 | 778845738.9428 | 778845738.9428
11 | 14 | 16 | 52.7 | 0 | 0 | 7.8453 | 0 | 784530744.3366 | 784530744.3366
11 | 17 | 3 | 52.7 | 0 | 0 | 8.0159 | 0 | 801585760.5178 | 801585760.5178
11 | 17 | 4 | 52.7 | 0 | 0 | 8.0159 | 0 | 801585760.5178 | 801585760.5178
11 | 24 | 3 | 52.7 | 0 | 0 | 7.8453 | 0 | 784530744.3366 | 784530744.3366
11 | 27 | 1 | 52.7 | 0 | 0 | 7.7316 | 0 | 773160733.5491 | 773160733.5491
11 | 27 | 2 | 52.7 | 0 | 0 | 7.7885 | 0 | 778845738.9428 | 778845738.9428
10 | 1 | 4 | 52.8 | 0 | 0 | 8.0224 | 0 | 802241379.3103 | 802241379.3103
11 | 13 | 8 | 52.8 | 0 | 0 | 7.7948 | 0 | 779482758.6207 | 779482758.6207
11 | 15 | 5 | 52.8 | 0 | 0 | 7.9655 | 0 | 796551724.1379 | 796551724.1379
11 | 25 | 6 | 52.8 | 0 | 0 | 7.7379 | 0 | 773793103.4483 | 773793103.4483
11 | 25 | 15 | 52.8 | 0 | 0 | 7.7948 | 0 | 779482758.6207 | 779482758.6207
11 | 27 | 5 | 52.8 | 0 | 0 | 7.7379 | 0 | 773793103.4483 | 773793103.4483
11 | 12 | 3 | 52.9 | 0 | 0 | 8.2567 | 0 | 825672766.4155 | 825672766.4155
11 | 12 | 4 | 52.9 | 0 | 0 | 8.1998 | 0 | 819978471.4747 | 819978471.4747
11 | 14 | 9 | 52.9 | 0 | 0 | 7.8012 | 0 | 780118406.8891 | 780118406.8891
11 | 14 | 24 | 52.9 | 0 | 0 | 7.8581 | 0 | 785812701.8299 | 785812701.8299
11 | 15 | 4 | 52.9 | 0 | 0 | 7.9151 | 0 | 791506996.7707 | 791506996.7707
10 | 4 | 10 | 53 | 0 | 0 | 8.4344 | 0 | 843440860.2151 | 843440860.2151
11 | 11 | 24 | 53 | 0 | 0 | 8.1495 | 0 | 814946236.5591 | 814946236.5591
11 | 14 | 8 | 53 | 0 | 0 | 7.8075 | 0 | 780752688.172 | 780752688.172
11 | 15 | 3 | 53 | 0 | 0 | 7.9785 | 0 | 797849462.3656 | 797849462.3656
11 | 25 | 1 | 53 | 0 | 0 | 7.8075 | 0 | 780752688.172 | 780752688.172
11 | 27 | 4 | 53 | 0 | 0 | 7.7505 | 0 | 775053763.4409 | 775053763.4409
11 | 27 | 6 | 53 | 0 | 0 | 7.7505 | 0 | 775053763.4409 | 775053763.4409
10 | 1 | 5 | 53.1 | 0 | 0 | 8.099 | 0 | 809903329.753 | 809903329.753
11 | 12 | 2 | 53.1 | 0 | 0 | 8.2131 | 0 | 821310418.9044 | 821310418.9044
11 | 13 | 16 | 53.1 | 0 | 0 | 7.7568 | 0 | 775682062.2986 | 775682062.2986
11 | 14 | 15 | 53.1 | 0 | 0 | 7.8709 | 0 | 787089151.4501 | 787089151.4501
11 | 25 | 2 | 53.1 | 0 | 0 | 7.8139 | 0 | 781385606.8743 | 781385606.8743
11 | 27 | 8 | 53.1 | 0 | 0 | 7.8139 | 0 | 781385606.8743 | 781385606.8743
10 | 4 | 19 | 53.2 | 0 | 0 | 8.4481 | 0 | 844806866.9528 | 844806866.9528
12 | 4 | 15 | 53.2 | 0 | 0 | 7.9914 | 0 | 799141630.9013 | 799141630.9013
12 | 4 | 17 | 53.2 | 0 | 0 | 7.9914 | 0 | 799141630.9013 | 799141630.9013
11 | 12 | 1 | 53.2 | 0 | 0 | 8.1056 | 0 | 810557939.9142 | 810557939.9142
11 | 13 | 13 | 53.2 | 0 | 0 | 7.8202 | 0 | 782017167.382 | 782017167.382
11 | 13 | 14 | 53.2 | 0 | 0 | 7.8202 | 0 | 782017167.382 | 782017167.382
11 | 13 | 24 | 53.2 | 0 | 0 | 7.8202 | 0 | 782017167.382 | 782017167.382
11 | 15 | 1 | 53.2 | 0 | 0 | 7.9343 | 0 | 793433476.3949 | 793433476.3949
11 | 15 | 2 | 53.2 | 0 | 0 | 7.9914 | 0 | 799141630.9013 | 799141630.9013
11 | 16 | 5 | 53.2 | 0 | 0 | 8.0485 | 0 | 804849785.4077 | 804849785.4077
11 | 25 | 4 | 53.2 | 0 | 0 | 7.8202 | 0 | 782017167.382 | 782017167.382
11 | 13 | 12 | 53.3 | 0 | 0 | 7.8265 | 0 | 782647374.0622 | 782647374.0622
11 | 13 | 15 | 53.3 | 0 | 0 | 7.8265 | 0 | 782647374.0622 | 782647374.0622
11 | 25 | 3 | 53.3 | 0 | 0 | 7.8265 | 0 | 782647374.0622 | 782647374.0622
11 | 14 | 3 | 53.4 | 0 | 0 | 7.8328 | 0 | 783276231.2634 | 783276231.2634
11 | 14 | 4 | 53.4 | 0 | 0 | 7.8328 | 0 | 783276231.2634 | 783276231.2634
11 | 14 | 6 | 53.4 | 0 | 0 | 7.8328 | 0 | 783276231.2634 | 783276231.2634
11 | 14 | 7 | 53.4 | 0 | 0 | 7.7756 | 0 | 777558886.5096 | 777558886.5096
9 | 4 | 7 | 53.5 | 0 | 0 | 8.1824 | 0 | 818235294.1176 | 818235294.1176
12 | 9 | 7 | 53.5 | 0 | 0 | 8.1251 | 0 | 812513368.984 | 812513368.984
11 | 13 | 2 | 53.5 | 0 | 0 | 7.9535 | 0 | 795347593.5829 | 795347593.5829
11 | 13 | 3 | 53.5 | 0 | 0 | 8.0107 | 0 | 801069518.7166 | 801069518.7166
11 | 13 | 4 | 53.5 | 0 | 0 | 7.9535 | 0 | 795347593.5829 | 795347593.5829
11 | 13 | 6 | 53.6 | 0 | 0 | 7.8453 | 0 | 784529914.5299 | 784529914.5299
11 | 16 | 4 | 53.6 | 0 | 0 | 8.1316 | 0 | 813162393.1624 | 813162393.1624
12 | 4 | 16 | 53.7 | 0 | 0 | 8.0235 | 0 | 802347918.8901 | 802347918.8901
11 | 10 | 11 | 53.7 | 0 | 0 | 8.1954 | 0 | 819541088.5806 | 819541088.5806
11 | 13 | 5 | 53.7 | 0 | 0 | 7.9089 | 0 | 790885805.7631 | 790885805.7631
11 | 14 | 5 | 53.7 | 0 | 0 | 7.8515 | 0 | 785154749.1996 | 785154749.1996
11 | 16 | 6 | 53.7 | 0 | 0 | 8.1381 | 0 | 813810032.0171 | 813810032.0171
10 | 4 | 20 | 53.8 | 0 | 0 | 8.4887 | 0 | 848869936.0341 | 848869936.0341
12 | 4 | 9 | 53.8 | 0 | 0 | 7.9725 | 0 | 797249466.951 | 797249466.951
12 | 9 | 4 | 53.8 | 0 | 0 | 8.0872 | 0 | 808720682.3028 | 808720682.3028
12 | 4 | 10 | 54 | 0 | 0 | 7.9851 | 0 | 798510638.2979 | 798510638.2979
12 | 9 | 2 | 54 | 0 | 0 | 8.1 | 0 | 810000000 | 810000000
12 | 9 | 3 | 54 | 0 | 0 | 8.1 | 0 | 810000000 | 810000000
12 | 9 | 6 | 54 | 0 | 0 | 8.1 | 0 | 810000000 | 810000000
12 | 10 | 15 | 54 | 0 | 0 | 8.1574 | 0 | 815744680.8511 | 815744680.8511
10 | 4 | 21 | 54.1 | 0 | 0 | 8.5088 | 0 | 850882040.3826 | 850882040.3826
12 | 4 | 8 | 54.1 | 0 | 0 | 8.0489 | 0 | 804888416.5781 | 804888416.5781
12 | 9 | 1 | 54.1 | 0 | 0 | 8.1064 | 0 | 810637619.5537 | 810637619.5537
12 | 9 | 5 | 54.1 | 0 | 0 | 8.1064 | 0 | 810637619.5537 | 810637619.5537
12 | 10 | 14 | 54.2 | 0 | 0 | 8.1127 | 0 | 811273885.3503 | 811273885.3503
11 | 10 | 10 | 54.2 | 0 | 0 | 8.2278 | 0 | 822781316.3482 | 822781316.3482
11 | 13 | 7 | 54.2 | 0 | 0 | 7.9401 | 0 | 794012738.8535 | 794012738.8535
12 | 8 | 24 | 54.4 | 0 | 0 | 8.1254 | 0 | 812542372.8814 | 812542372.8814
12 | 10 | 13 | 54.4 | 0 | 0 | 8.1254 | 0 | 812542372.8814 | 812542372.8814
9 | 3 | 20 | 54.5 | 0 | 0 | 8.5354 | 0 | 853544973.545 | 853544973.545
11 | 9 | 21 | 54.5 | 0 | 0 | 8.3624 | 0 | 836243386.2434 | 836243386.2434
12 | 10 | 16 | 54.6 | 0 | 0 | 8.1958 | 0 | 819577167.019 | 819577167.019
11 | 16 | 3 | 54.8 | 0 | 0 | 8.2662 | 0 | 826624472.5738 | 826624472.5738
12 | 24 | 2 | 55.3 | 0 | 0 | 8.2979 | 0 | 829790136.4113 | 829790136.4113
11 | 24 | 20 | 55.3 | 0 | 0 | 8.2399 | 0 | 823987408.1847 | 823987408.1847
11 | 10 | 1 | 55.7 | 0 | 0 | 8.4976 | 0 | 849759665.6217 | 849759665.6217
11 | 10 | 9 | 55.7 | 0 | 0 | 8.3812 | 0 | 838119122.2571 | 838119122.2571
11 | 10 | 8 | 56.3 | 0 | 0 | 8.4187 | 0 | 841869158.8785 | 841869158.8785
11 | 24 | 22 | 56.9 | 0 | 0 | 8.397 | 0 | 839700722.3942 | 839700722.3942
11 | 24 | 21 | 57 | 0 | 0 | 8.4031 | 0 | 840309278.3505 | 840309278.3505
11 | 9 | 24 | 57.1 | 0 | 0 | 8.5268 | 0 | 852677651.9053 | 852677651.9053
11 | 9 | 23 | 57.2 | 0 | 0 | 8.5329 | 0 | 853292181.07 | 853292181.07
11 | 9 | 22 | 57.8 | 0 | 0 | 8.5695 | 0 | 856952965.2352 | 856952965.2352
11 | 10 | 7 | 58.3 | 0 | 0 | 8.5404 | 0 | 854038657.1719 | 854038657.1719
11 | 10 | 6 | 58.4 | 0 | 0 | 8.5463 | 0 | 854634146.3415 | 854634146.3415
11 | 10 | 2 | 58.9 | 0 | 0 | 8.5759 | 0 | 857593528.817 | 857593528.817
11 | 10 | 3 | 59.1 | 0 | 0 | 8.5877 | 0 | 858768920.2825 | 858768920.2825
11 | 10 | 4 | 59.5 | 0 | 0 | 8.6111 | 0 | 861105527.6382 | 861105527.6382
11 | 10 | 5 | 59.6 | 0 | 0 | 8.6169 | 0 | 861686746.988 | 861686746.988
8 | 23 | 2 | 65.2 | 0 | 0 | 10.2882 | 0 | 1028821292.7757 | 1028821292.7757
11 | 24 | 13 | 67.1 | 0 | 0 | 9.5857 | 0 | 958571428.5714 | 958571428.5714
11 | 24 | 10 | 67.4 | 0 | 0 | 9.6017 | 0 | 960167597.7654 | 960167597.7654
11 | 24 | 12 | 67.5 | 0 | 0 | 9.607 | 0 | 960697674.4186 | 960697674.4186
11 | 24 | 14 | 67.5 | 0 | 0 | 9.607 | 0 | 960697674.4186 | 960697674.4186
11 | 24 | 11 | 67.7 | 0 | 0 | 9.6175 | 0 | 961754874.6518 | 961754874.6518
11 | 24 | 15 | 67.7 | 0 | 0 | 9.6175 | 0 | 961754874.6518 | 961754874.6518
8 | 23 | 3 | 70.2 | 0 | 0 | 10.6383 | 0 | 1063829401.0889 | 1063829401.0889
11 | 24 | 16 | 71.1 | 0 | 0 | 9.9194 | 0 | 991944194.4194 | 991944194.4194
11 | 22 | 20 | 109.8 | 0 | 0 | 14.0732 | 0 | 1407316421.8959 | 1407316421.8959
11 | 22 | 19 | 110 | 0 | 0 | 14.08 | 0 | 1408000000 | 1408000000
11 | 18 | 18 | 110.2 | 0 | 0 | 14.3069 | 0 | 1430692410.1198 | 1430692410.1198
8 | 17 | 7 | 116.5 | 0 | 0 | 14.5904 | 0 | 1459041533.5463 | 1459041533.5463
11 | 16 | 8 | 116.5 | 0 | 0 | 14.9626 | 0 | 1496261980.8307 | 1496261980.8307
9 | 30 | 22 | 142.3 | 0 | 0 | 18.5778 | 0 | 1857783872.7373 | 1857783872.7373
9 | 30 | 21 | 144 | 0 | 0 | 18.5478 | 0 | 1854782608.6957 | 1854782608.6957
9 | 30 | 20 | 144.3 | 0 | 0 | 18.6345 | 0 | 1863450895.2794 | 1863450895.2794
9 | 30 | 12 | 144.7 | 0 | 0 | 18.6457 | 0 | 1864569572.2794 | 1864569572.2794
9 | 30 | 11 | 145 | 0 | 0 | 18.6541 | 0 | 1865405405.4054 | 1865405405.4054
9 | 30 | 13 | 145.9 | 0 | 0 | 18.679 | 0 | 1867896718.666 | 1867896718.666
9 | 30 | 10 | 146.3 | 0 | 0 | 18.69 | 0 | 1868996242.6194 | 1868996242.6194
9 | 30 | 9 | 147.1 | 0 | 0 | 18.7118 | 0 | 1871181186.5313 | 1871181186.5313
9 | 30 | 19 | 147.1 | 0 | 0 | 18.7118 | 0 | 1871181186.5313 | 1871181186.5313
9 | 30 | 8 | 148.1 | 0 | 0 | 18.8176 | 0 | 1881759702.286 | 1881759702.286
9 | 30 | 14 | 148.2 | 0 | 0 | 18.7416 | 0 | 1874155154.0914 | 1874155154.0914
9 | 30 | 15 | 149.2 | 0 | 0 | 18.7683 | 0 | 1876828752.6427 | 1876828752.6427
9 | 30 | 16 | 149.2 | 0 | 0 | 18.7683 | 0 | 1876828752.6427 | 1876828752.6427
9 | 30 | 18 | 149.8 | 0 | 0 | 18.7053 | 0 | 1870526870.3899 | 1870526870.3899
9 | 30 | 17 | 150.2 | 0 | 0 | 18.7947 | 0 | 1879474237.6446 | 1879474237.6446
9 | 7 | 7 | 150.9 | 0 | 0 | 19.1293 | 0 | 1912928234.6778 | 1912928234.6778
11 | 10 | 20 | 160.1 | 0 | 0 | 19.5224 | 0 | 1952243878.061 | 1952243878.061
11 | 23 | 18 | 183.6 | 0 | 0 | 21.5952 | 0 | 2159516994.6333 | 2159516994.6333
8 | 24 | 13 | 259.2 | 0 | 0 | 29.9743 | 0 | 2997433155.0802 | 2997433155.0802
8 | 24 | 15 | 259.8 | 0 | 0 | 30.0702 | 0 | 3007024683.1221 | 3007024683.1221
8 | 24 | 14 | 260.2 | 0 | 0 | 30.0764 | 0 | 3007641572.2851 | 3007641572.2851
8 | 24 | 12 | 260.6 | 0 | 0 | 29.9959 | 0 | 2999587491.6833 | 2999587491.6833
8 | 24 | 11 | 262.1 | 0 | 0 | 30.279 | 0 | 3027901357.1665 | 3027901357.1665
8 | 24 | 19 | 310.3 | 0 | 0 | 35.1667 | 0 | 3516674279.1893 | 3516674279.1893
8 | 23 | 22 | 325.8 | 0 | 0 | 36.1604 | 0 | 3616041552.7611 | 3616041552.7611
8 | 23 | 20 | 325.9 | 0 | 0 | 36.1616 | 0 | 3616162886.0344 | 3616162886.0344
8 | 23 | 21 | 326.7 | 0 | 0 | 36.1713 | 0 | 3617131169.8937 | 3617131169.8937
6 | 11 | 22 | 447.4 | 0 | 0 | 50.9865 | 0 | 5098652646.6968 | 5098652646.6968
6 | 11 | 17 | 454 | 0 | 0 | 52.0124 | 0 | 5201240890.6883 | 5201240890.6883
6 | 11 | 16 | 454.4 | 0 | 0 | 51.9196 | 0 | 5191961165.0485 | 5191961165.0485
6 | 11 | 18 | 454.5 | 0 | 0 | 52.017 | 0 | 5201704246.7139 | 5201704246.7139