## L2 Form
PJM 2026 Black Start Reliability Backstop RFP | [5 empty] | Select Proposal Type, Fuel Assurance Type, and Resource Status using the drop down menus by clicking on cells highlighted yellow. Each proposal/option should be entered in separate columns.
Level 2 Proposal Response
Send Level 2 Proposal Responses to Blackstart@pjm.com by March 5, 2027
[6 empty] | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type | Proposal Type
[6 empty] | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type | Fuel Assurance Type
[6 empty] | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status | Resource Status
Category |  |  |  | Data Required | Response | Proposal 1 (Name of Facility) | Proposal 2 (Name of Facility) | Proposal 3 (Name of Facility) | Proposal 4 (Name of Facility) | Proposal 5 (Name of Facility) | Proposal 6 (Name of Facility) | Proposal 7 (Name of Facility) | Proposal 8 (Name of Facility) | Proposal 9 (Name of Facility) | Proposal 10 (Name of Facility) | Proposal 11 (Name of Facility) | Proposal 12 (Name of Facility) | Proposal 13 (Name of Facility) | Proposal 14 (Name of Facility) | Proposal 15 (Name of Facility) | Proposal 16 (Name of Facility) | Proposal 17 (Name of Facility) | Proposal 18 (Name of Facility) | Proposal 19 (Name of Facility) | Proposal 20 (Name of Facility)
5.1. | Purpose and Scope
| 5.1.1. | Facility
|  | 5.1.1.1. | Name of facility | Name | Text
|  | 5.1.1.2. | Owner of facility | Owner | Text
|  | 5.1.1.3. | Geographic details | Address | Text
|  |  |  | County | Text
|  |  |  | State | Text
|  |  |  | Latitude / Longitude | Text
|  | 5.1.1.4. | Age of proposed Black Start Unit | Age of proposed Black Start Unit at time Black Start Service would commence | Number
| 5.1.2. | Black Start Unit
|  | 5.1.2.1. | Type of generation | Type of generation - CT, Combined Cycle (or CT that is part of a Combined Cycle plant), Intermittent, Run of River Hydro, Pump Storage Hydro, Diesel, Storage, Hybrids (renewables with storage), DER, etc. | Text
Please See Section 5.2.6 Below for Unit Specific Questions for Each Unit Type
|  | 5.1.2.2. | Manufacturer | Manufacturer (e.g. GE, Siemens) | Text
|  |  |  | Model/Unit Type (e.g. 7FA) | Text
|  |  |  | Diesel or battery or CT or other resource cranking the Black Start Unit (See Section 6.5 “Black Start Unit Configurations”). | Text
|  | 5.1.2.3. | Black Start MW capability | MW Capability (ICAP or equivalent) of the intended Black Start Unit and the full plant (if applicable). Indicate whether MW capability is in terms of capacity resource ICAP, maximum dependable capability (for energy only resources), ELCC MW, or nameplate MW rating. | Text
|  |  |  | Proposed Black Start Unit MW | Text
|  |  |  | Provide details if proposed Black Start Unit MW are different than MW capability specified above. | Text
|  |  |  | Confirm any Power Augmentation MW included in Black Start MW Above (if applicable) | Text
|  |  |  | Indicate Power Augmentation Type (if applicable) | Text
|  |  |  | Describe any limitations due to the use of power augmentation (e.g. ambient temp.) where the unit would not be able to meet the proposed Black Start MWs year round during a restoration scenario. | Text
|  |  |  | For CC indicate ST MW Capability (ICAP or equivalent) | Text
|  | 5.1.2.4. | Black Start Unit fuel type(s) | Primary Fuel Type | Text
|  |  |  | Secondary Fuel Type (if applicable) | Text
|  |  |  | Primary Start-Up Fuel (if applicable) | Text
|  |  |  | Secondary Start-up fuel (if applicable) | Text
|  |  |  | Indicate if unit is directly connected to one or more interstate natural gas pipelines not behind a LDC (if applicable) | Text
|  |  |  | Indicate fuel(s) used (if different) for any starting or cranking engines/diesels. | Text
|  | 5.1.2.5. | Plant with multiple units | For a plant with multiple units, identify which units are being proposed as Black Start resources. Also indicate which of the other units can be started by the proposed Black Start Units. | Text
|  | 5.1.2.6. | Black Start operating mode | Provide details on Black Start Units ability to operate in automatic isochronous mode or equivalent control scheme | Text
|  | 5.1.2.7. | Cranking Resource information | If the Black Start Unit relies on a cranking resource (e.g. diesel generator, battery, or combustion turbine, compressed air), confirm cranking resource has sufficient fuel to power the Black Start Unit's auxiliary loads for 24 hours and 4 start attempts. | Text
|  |  |  | Provide details on the cranking resource configuration. | Text
|  |  |  | For inverter-based resources, confirm the proposed configuration is capable of powering auxiliary loads for 24 hours, sustaining operation at the proposed Black Start MW level for 16 hours, and supporting a minimum of four start attempts | Text
|  |  |  | Provide energy storage details for inverter based resources. | Text
|  | 5.1.2.8. | Black Start Test | Can the unit perform an annual Black Start Test where it operates isolated from the grid in isochronous or equivalent control scheme, carrying only station auxiliary load for at least thirty minutes? | Yes/No
|  |  |  | If not, provide details. | Text
|  |  |  | Provide description of proposed annual Black Start Test | Text
| 5.1.3. | Interconnection
|  | 5.1.3.1. | Transmission level | Interconnecting Station Name | Text
|  |  |  | Voltage Level of Interconnecting Station | Text
|  |  |  | Transmission Owner zone | Text
| 5.1.4. | Necessary Upgrade(s) for Black Start Capability
|  | 5.1.4.1. | Brief description of the modifications required to convert the facility to Black Start | Briefly describe the modifications that are required to convert the facility to Black Start. If adding a diesel, please indicate quantity, the manufacturer, model, and rating of the unit, as well as which unit(s) it will be cranking. If adding a battery indicate cranking power, cranking duration, and overall battery MW size. | Text
5.2. | Generator Operational Details
| 5.2.1. | Fuel Assurance Requirements
|  | 5.2.1.1. | 16 hour run time requirement | Can unit operate for a minimum of 16 hours at proposed Black Start MWs based on fuel and non-fuel consumables? | Yes/No
|  |  |  | If not, how many hours can the unit run based on the proposed Black Start MW and provide details on limitations. | Text
|  | 5.2.1.2. | Onsite Fuel Storage | Onsite fuel storage description | Text
|  |  |  | Volume / tank size (gallons) | Number
|  |  |  | Tank storage in hours based on sustained output at proposed Black Start MWs | Number
|  |  |  | Permitting limitations (and challenges to obtain permits) associated with burning on-site fuel | Text
|  |  |  | Is Black Start Unit fuel storage shared with other non-Black Start Units? | Yes/No
|  |  |  | Explain the fuel supply and replenishment arrangements for this resource and provide contractual details. | Text
|  | 5.2.1.3. | Non-Fuel Consumable Storage | Describe storage capabilities/tank sizes for any non-fuel consumables (ammonia, demin water, etc.) and replenishment arrangements required for Black Start Service or Fuel Assured Black Start Service | Text
| 5.2.2. | One-Line Diagram
|  | 5.2.2.1. | One-line diagram | Provide a one-line diagram for the plant site, which includes the Black Start facility. The one-line diagram should include the proposed RFP response unit(s), all associated auxiliary loads, and transmission and distribution level equipment. Formal drawings are not required. Legible hand-written mark-ups of existing diagrams are sufficient. Visio diagrams with adequate detail are also sufficient. | Provide Diagram
| 5.2.3. | Unit Capabilities
|  | 5.2.3.1. | Black Start Unit Start-up sequencing description | Provide a detailed description of the actions and procedures the generating facility would follow immediately following a full or partial system blackout to: (1) start the proposed Black Start Unit, (2) energize and synchronize to a dead bus, and (3) support load pickup from the unit's minimum operating level through its proposed Black Start MW output. References to the applicable one-line diagram shall be included throughout the narrative to clearly illustrate the proposed restoration sequence and equipment configuration. | Text
|  | 5.2.3.2. | Start-up Time | Estimated time to close to a dead bus | Number
|  |  |  | Estimated time to ramp to minimum load | Number
|  |  |  | Estimated time to ramp to proposed Black Start MWs | Number
|  |  |  | Confirm these times include time to start-up cranking power source as applicable. | Yes/No
|  |  |  | If offering more than one unit for Black Start Service, can all units close to a dead bus in 180 minutes when requested to start by the Transmission Owner or PJM. | Yes/No
|  |  |  | If not, provide details. | Text
|  | 5.2.3.3. | Plant staffing details | Indicate whether the unit will be staffed 24 x 7 if selected to provide Black Start Service. If the plant will not be staffed 24 x 7, can the unit be started remotely? If so, describe the plan for starting the Black Start unit in the event of a telemetry failure. | Text
|  | 5.2.3.4. | Ramp rate details | Provide unit ramp rate under an emergency scenario such as a black out event, accounting for any permit exceptions or waivers. | Number
|  |  |  | Indicate largest block of load that can be picked up instantaneously | Number
|  |  |  | Provide the time between load pick-ups | Number
|  |  |  | Describe any ramp rate limitations | Text
|  | 5.2.3.5. | Minimum Output Restrictions | Provide minimum output restrictions at various stages of the startup sequence. | Text
|  |  |  | Provide step by step sequence (timing/ load pick up / ramp/ hold points/ critical zones) | Text
|  |  |  | Provide the units maximum allowable time at minimum load, and state the minimum load. Preference is placed on those units that are able to “idle” for the longest time serving only house load with no net output to the transmission grid because this reduces the complexity of GO/TO load pickup coordination. Plants that have multiple units should consider the potential of cranking auxiliaries of other units as additional “house load.” | Text
|  | 5.2.3.6. | Stabilizing Load | Can unit operate at full speed no load during restoration emergency? | Yes/No
|  |  |  | If not, provide details. | Text
|  |  |  | Does the unit require stabilizing load that exceeds internal plant loads? | Yes/No
|  |  |  | If stabilizing load is required, provide details such as the amount of load needed upon initial breaker closing. | Text
|  | 5.2.3.7. | Station auxiliary load | Provide the station’s auxiliary load in MWs | Number
|  |  |  | Is the existing unit Black Start capable in accordance with the requirements stated in PJM's Tariff, Schedule 6A, and PJM Manual 12 – Balancing Operations? | Yes/No
| 5.2.4. | Reactive Capability
|  | 5.2.4.1. | Reactive (MVAR) capability curve (D-Curve) | Provide a reactive (MVAR) capability curve (D-Curve) indicating the over and under excitation limits, including MW, Min. MVAR, Max. MVAR, and a table including up to 8 MW points (if possible) with associated minimum and maximum MVAR points. Include the maximum sustained leading and lagging (MVAR absorption) capability. | Provide Attachment
|  | 5.2.4.2. | Restrictions to MVAR capability curve | Describe any anticipated administrative (operational/procedural) restrictions that prevent the unit from providing MVARs up to over excitation and under excitation limit? | Text
|  |  |  | Can unit provide reactive support at 0 MWs (full speed no load) as cranking path is energized w/ no load | Yes/No
|  |  |  | What is acceptable generator terminal voltage range (ex. 0.95 to 1.05 of nominal)? | Text
|  |  |  | For inverter based resources, how does inverter based resource get online without outside electrical grid? | Text
|  | 5.2.4.3. | Voltage Regulator | Can voltage regulator operate in automatic voltage control mode or an equivalent control scheme during a restoration event? | Text
| 5.2.5. | Unit Permit Limitations
|  | 5.2.5.1. | Permit Compliance/Limitations | Provide the unit’s minimum load (MW) under the current emissions permit | Text
|  |  |  | Provide the maximum allowable time to come into compliance with emissions permit minimum load above during a restoration emergency. | Text
|  |  |  | What is the lowest load the unit can operate in a stable steady state configuration if there were no emission permit restrictions? | Text
|  |  |  | Are unit's run hours limited on primary or secondary fuel? If so, what is the limitation? | Text
|  |  |  | Identify any current or proposed legislation that will impact a units ability to provide Black Start service? | Text
|  |  |  | Provide a copy of current permit and or renewal application if applicable. | Provide Attachment
|  | 5.2.5.2. | Emissions permit modifications | Does the unit have a permit emergency exemption from emission limits during restoration events? | Text
|  |  |  | Confirm the feasibility of obtaining an emissions permit modification to allow the unit to operate at the lowest possible load for restoration and Black Start testing (Units with emergency waivers or permits that allow low load capabilities for extended periods of time are strongly preferred) and willingness to obtain a permit modification. | Text
| 5.2.6. | Additional Unit Details Based on Unit Type
|  | 5.2.6.1. | Natural Gas Units | Indicate single or multiple pipelines, or LDC, and indicate name of pipeline(s) / LDC(s). | Text
|  |  |  | Gas Transportation and Supply Arrangements - If a primary or secondary fuel is natural gas, indicate gas transportation and supply arrangements. Indicate if these arrangements are primary firm or non-firm transportation contracts for primary or alternate pipeline feeds. Indicate any arrangements for the unit to secure additional fuel. | Text
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.2. | Combined Cycle Units | Can the Combustion turbines be operated in simple cycle mode? | Yes/No
|  |  |  | If yes, identify any limitations accounting for seasonality | Text
|  |  |  | If no, does the unit have steam bypass capability? | Yes/No
|  |  |  | If yes, what is the minimum and maximum load the combustion turbine can operate in Steam bypass mode and provide details | Text
|  |  |  | If yes, identify any limitations in steam by-pass mode (duration, output, etc.) | Text
|  |  |  | Does the unit have any limitation which requires bringing the steam turbine on line during the restoration event and provide details. | Text
|  |  |  | If the steam turbine must be brought online can the ramp rate be manually controlled? | Text
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.3. | Dual Fuel Units | Can the unit start on both primary and secondary fuel? | Yes/No
|  |  |  | Is no, provide details and identify any start-up fuel requirements | Text
|  |  |  | Indicate any fuel switching requirements to move from primary to alternate fuel (or vice versa) - e.g. does the unit need to reduce or shutdown in order to switch between primary and alternate fuels | Text
|  |  |  | How long does it take to switch from primary to secondary fuel and vice versa | Number
|  |  |  | Is the unit willing to run on both fuels during a restoration event ? | Yes/No
|  |  |  | Will resource be dual fuel available year round for Black Start without changing of equipment (e.g. burners, etc.)? Are there any other limitations such as emissions, ozone season, etc.? Provide details if there are any limitations. | Text
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.4. | Hydro Units | Pumped Storage or Run of River | Text
|  |  |  | Pumped Storage - Indicate maximum run time at proposed Black Start MW with a full pond | Text
|  |  |  | Run of River - indicate number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment (if applicable) | Provide Attachment
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.5. | Storage | Type of Storage Unit (e.g. Battery, Flywheel, or other) | Text
|  |  |  | Indicate how the Storage Unit will be charged. | Text
|  |  |  | Provide details on grid forming and grid following modes and the ability to switch between both modes. | Text
|  |  |  | Provide the continuous rating, peak rating, and total mWh rating and include sizing calculation details | Text
|  |  |  | Provide the maximum run time at proposed Black Start MW and MVAR based on full charge | Text
|  |  |  | Provide the Storage Unit's design life (years) and indicate whether augmentation or replacement will be required during that period to maintain compliance with PJM's Fuel Assured Black Start requirements. | Text
|  |  |  | For existing storage resources, provide historical storage and run profile data as a separate attachment | Provide Attachment
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.6. | Hybrid | Type of Hybrid (e.g. Solar/Battery, Wind/Battery or other) | Text
|  |  |  | Indicate max run time at proposed Black Start MW with a full charge. | Text
|  |  |  | Indicate the number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment | Provide Attachment
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.7. | Intermittent | Type of Intermittent (e.g. Solar, Wind, or other) | Text
|  |  |  | Indicate max run time at proposed Black Start MW | Text
|  |  |  | Indicate the number of years of historical data available | Text
|  |  |  | Provide historical data as a separate attachment | Provide Attachment
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes | Provide Attachment
|  | 5.2.6.8. | DER | Type of DER | Text
|  |  |  | Fuel Type | Text
|  |  |  | Indicate max run time at proposed Black Start MW | Text
|  |  |  | Provide details as indicated above in 5.2.5.1 through 5.2.5.7 for respective fuel types as applicable | Text
|  |  |  | Provide PSS/E steady state and dynamic models for isochronous/droop/grid forming/grid following modes. | Provide Attachment
|  | 5.2.6.9. | Necessary Upgrades for Fuel Assurance | Briefly describe the modifications that are required for the facility to provide Fuel Assured Black Start Service, if applicable (Costs are reflected in Section 5.3.1 or Section 5.4.2 below) | Text
5.3. | Generation Owner (GO) Solution - Total Estimated Capital Cost for Black Start Service and/or Fuel Assured Black Start Service
| 5.3.1 | Estimated Capital Costs
|  | 5.3.1.1. | Black Start Capital Recovery Rate(s) | Specify which Schedule 6A Fixed Black Start Service Cost (Fixed BSSC) Rate is being selected. If selecting the Base Formula Rate, enter 0 for the capital costs for Sections 5.4.1.2 and 5.4.1.3 below. | Text
|  | 5.3.1.2. | Black Start Service Capital Cost (if applicable) | Capital Cost required to provide Black Start Service (excluding any Black Start Service Fuel Assured Cost) | Number
|  | 5.3.1.3. | Black Start Service Fuel Assured Capital Cost (if applicable) | Capital Cost to become Black Start Fuel Assured (excluding any Black Start Service Cost) | Number
|  | 5.3.1.4. | Expected Capital Recovery Period | Provide the expected capital recovery period (years) based on the age of the unit when it enters Black Start or Fuel Assured Black Start Service. | Number
|  | 5.3.1.5. | Summary of Black Start Service and/or Fuel Assurance Capital Costs | Provide detailed summary of capital cost for both Black Start Service and/or Fuel Assurance at a minimum including engineering, construction, materials, in-house labor, overheads and contingency costs. | Text
|  | 5.3.1.6. | Existing Black Start Unit ONLY: Capability of proposed unit to be refurbished (if applicable) | Is the existing unit Black Start capable in accordance with the requirements stated in Tariff, Schedule 6A, and PJM Manual 12 – Balancing Operations? | Yes/No
|  |  |  | If not, what modifications are required? | Text
|  | 5.3.1.7. | Existing Black Start Units that would otherwise retire (if applicable) | Identify any equipment overhauls or refurbishment work that would be required for continued reliable Black Start Service | Text
| 5.3.2. | Estimated Fixed Black Start Service Cost
|  | 5.3.2.1. | Estimated Fixed Black Start Service Cost | Provide estimated Fixed Black Start Service Cost which includes cost for both Black Start Service and if applicable Fuel Assurance | Number
| 5.3.3. | Estimated Black Start Service Annual O&M Cost
|  | 5.3.3.1. | Estimated Variable Black Start Service Cost | Provide estimated Black Start O&M Cost including any cost required to meet NERC Standards and or Fuel Assurance | Number
|  | 5.3.3.2. | Summary of Variable Black Start Service Cost | Provide detailed summary of annual O&M costs for providing Black Start Service and Fuel Assurance | Provide Attachment
| 5.3.4. | Estimated Black Start Service Annual Fuel Storage Costs
|  | 5.3.4.1. | Estimated Black Start Service Annual Fuel Storage Costs | Provide estimated Black Start Service Fuel Storage Cost | Number
|  | 5.3.4.2. | Fuel Usage Rate at Full Load (i.e. Burn Rate) | Provided estimated Black Start unit(s) fuel usage rate at full load | Text
|  | 5.3.4.3. | Minimum Tank Suction Level Volume | Provide Minimum Tank Suction Level Volume | Text
|  | 5.3.4.4. | Summary of Fuel Storage Cost | Provide summary of the calculation of the annual fuel storage costs above | Provide Attachment
5.4. | Transmission Owner (TO) Solution - Total Estimated Capital Cost for Black Start Service and/or Fuel Assured Black Start Service
| 5.4.1. | Ownership Model
|  | 5.4.1.1. | Summary of Fuel Assured Black Start Service Ownership | Indicate if Transmission Owner will i. Contract with a Generation Owner of an Existing Fuel Assured Black Start Resource, ii. Contract with a Generation Owner to build a new Fuel Assured Black Start Resource, or iii. Own a Fuel Assured Black Start Resource (choose one). This should align with the drop downs menus at the top of the column. | Text
| 5.4.2. | Estimated Capital Costs
|  | 5.4.2.1. | Black Start Service Capital Cost (if applicable) | Estimated capital cost required to provide Fuel Assured Black Start Service. | Text
|  | 5.4.2.2. | Summary of Fuel Assured Black Start Service Capital Costs | Provide detailed summary of capital costs for Fuel Assured Black Start Service at a minimum including engineering, construction, materials, in-house labor, overheads and contingency costs | Provide Attachment
| 5.4.3. | Proposed Contractual Obligations
|  | 5.4.3.1. | TO Contract for Fuel Assured Black Start Service (if applicable) | Provide a detailed summary of possible contractual agreements in which the TO contracts with a Generation Owner to provide Fuel Assured Black Start. The Transmission Owner shall be responsible for establishing terms and conditions associated with its proposed solution, including, but not limited to, compensation, cost recovery, performance penalties, and service termination provisions. Such arrangements shall not conflict or supersede PJM’s operational requirements, PJM Tariff, or applicable governing documents. | Text
| 5.4.4. | Regulatory Cost Recovery Approach
|  | 5.4.4.1. | TO Cost Recovery | Detail how the TO will recover costs; through its annual revenue requirement under Attachment H or other recovery methods (i.e. FERC filing). | Text
5.5. | Project Schedule
| 5.5.1. | Estimated In-Service Date
|  | 5.5.1.1. | Estimated In-Service Date | Indicate the estimated in-service date as a Black Start capable unit. | Text
| 5.5.2. | Project Schedule
|  | 5.5.2.1. | Project Schedule | Detail the project milestones in tabular and/or graphical form. Include the milestone description and projected start/finish dates. | Provide Attachment
| 5.5.3. | Procurement Plan
|  | 5.5.3.1. | Procurement Plan | Detail any work that is planned with vendors. | Text
5.6. | Black Start Unit Owner Contact Information
| 5.6.1. | Primary Contact
|  | 5.6.1.1. | Provide Primary Contact Information | Name | Text
|  |  |  | Title | Text
|  |  |  | Company | Text
|  |  |  | Phone Number | Text
|  |  |  | Email Address | Text
| 5.6.2. | Alternate Contact
|  | 5.6.2.1. | Provide Alternate Contact Information | Name | Text
|  |  |  | Title | Text
|  |  |  | Company | Text
|  |  |  | Phone Number | Text
|  |  |  | Email Address | Text