## Key System Upgrades 2025_2026
System Upgrades With Potential Impact to Congestion June 2025 Through May 2026
Description | Transmission Owner | Projected In-Service Date
Reconductor approximately 1.07 miles of 230 kV line #2008 segment from Cub Run-Walney to achieve a summer rating of 1574 MVA. Replace line switch 200826 with a 4000A switch. | Dominion | 11/15/2024
Rebuild the 13707 Vienna-Nelson 138 kV line | DPL | 12/18/2024
Perform a Sag Study of the Saltville - Tazewell 138 kV line to increase the thermal rating of the line | AEP | 3/1/2025
Rebuild a 13 mile section of 138 kV line 0108 between LaSalle and Mazon with 1113 ACSR or higher rated conductor. The 13 mile portion of line 7713 from Oglesby (future Corbin) to Mazon that shares double circuit towers with line 0108 will also be reconductored due to the rebuild. | ComEd | 6/1/2025
Reconductor approximately 24.42 miles of 230 kV line #2114 Remington CT-Elk Run-Gainesville to achieve a summer rating of 1574 MVA by fully reconductoring the line and upgrading the wave trap and substation conductor at Remington CT and Gainesville. | Dominion | 6/1/2025
Reconductor approximately 2.9 miles of 230 kV line #211 Chesterfield-Hopewell to achieve a minimum summer emergency rating of 1046 MVA. | Dominion | 6/1/2025
Reconductor approximately 2.9 miles of 230 kV line #228 Chesterfield-Hopewell to achieve a minimum summer emergency rating of 1046 MVA. | Dominion | 6/1/2025
Partial wreck and rebuild 10.34 miles of 230 kV line #249 Carson-Locks to achieve a minimum summer emergency rating of 1047 MVA. Upgrade terminal equipment at Carson and Locks to not limit the new conductor rating. | Dominion | 6/1/2025
Reconductor Kammer - George Washington 138 kV line (~0.08 miles). Replace the wave trap at Kammer 138 kV. | AEP | 6/2/2025
Rebuild 0.2 mile of the West End Fostoria - Lumberjack Switch 69 kV line with 556 ACSR (Dove) conductors. Replace jumpers on West End Fostoria line at Lumberjack Switch. | AEP | 7/30/2025
Install a 2nd 230kV circuit with a minimum summer emergency rating of 1047 MVA between Lanexa and Northern Neck Substations. The 2nd circuit will utilize the vacant arms on the double-circuit structures that are being installed on the Line #224 (Lanexa-Northern Neck) End-of-Life rebuild project (b3089). | Dominion | 7/31/2025
Replace the 2156 ACSR & 2874 ACSR bus and risers with 2-bundled 2156 ACSR at Muskingum River 345 kV station to address loading issues on Muskingum-Waterford 345 kV line. | AEP | 9/1/2025
Upgrade Windy Edge 115 kV substation conductor to increase ratings of the Windy Edge-Chesco Park 110501 circuit. | BGE | 10/1/2025
Rebuild the 18.6 mile section of 115kV Line #81 which includes 1.7 miles of double circuit Line #81 with 230kV Line #2056 and 1.3 miles of double circuit Line #81 with 230kV Line #239. This segment of Line #81 will be rebuilt to current standards with a minimum rating of 261 MVA. This segment of Line #239 will be rebuilt to current standards with a minimum rating of 1046 MVA. Line #2056 rating will not change. | Dominion | 11/29/2025
Rebuild the Summer Shade-West Columbia 69 kV 0.19 miles of 266 conductor double circuit to 556 conductor. | EKPC | 12/1/2025
Rebuild approximately 15.1-mile-long line segment between 115 kV line #183 Bristers and Minnieville D.P. with 2-768 ACSS and 4000 A supporting equipment from Bristers to Ox to allow for future 230 kV capability of 115 kV line #183. The continuous summer normal rating will be 523 MVA from Ox-Minnieville. The continuous summer normal rating will be 786 MVA from Minnieville-Bristers. | Dominion | 12/17/2025
Convert 115 kV Line #172 Liberty-Lomar and 115 kV Line #197 Cannon Branch-Lomar to 230 kV to provide a new 230 kV source between Cannon Branch and Liberty. The majority of 115 kV Line #172 Liberty-Lomar and Line #197 Cannon Branch-Lomar is adequate for 230 kV operation. Lines to have a summer rating of 1047 MVA/1047 MVA (SN/SE) | Dominion | 12/19/2025
Install one 500/230kV 1440MVA transformer at a new substation called Wishing Star. Cut and extend 500 kV Line #546 (Brambleton-Mosby) and 500 kV Line #590 (Brambleton-Mosby) to the proposed Wishing Star substation. Lines to terminate in a 500 kV breaker and a half configuration. | Dominion | 12/19/2025
Install one 500/230 kV 1440 MVA transformer at a new substation called Mars near Dulles International Airport. | Dominion | 12/19/2025
Construct a new 500 kV transmission line for ~ 3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the line. New conductor to have a minimum summer normal rating of 4357 MVA. | Dominion | 12/19/2025
Construct a new 230 kV transmission line for ~3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the 500 kV line. New conductor to have a minimum summer normal rating of 1573 MVA. | Dominion | 12/19/2025
Construct a new 34.5 kV circuit from Atlantic to Red Bank 34.5 kV (10.3 Miles) - (replaces B1690) | JCPL | 12/19/2025
Reconductor the Blairsville East to Social Hall 138 kV line and upgrade terminal equipment - AP portion. 4.8 miles total. The new conductor will be 636 ACSS replacing the existing 636 ACSR conductor. At Social Hall, meters, relays, bus conductor, a wavetrap, circuit breaker and disconnects will be replaced. | APS | 12/31/2025
Rebuild the 1.3 mile section of 500 kV Line No.569 (Loudoun - Morrisville) with single-circuit 500 kV structures at the current 500 kV standard. This will increase the rating of the line to 3424 MVA. | Dominion | 12/31/2025
East Towanda-North Meshoppen 115 kV line: Rebuild 2.5 miles of 636 ACSR with 1113 ACSS conductor using single circuit construction. Upgrade all terminal equipment to the rating of 1113 ACSS. | PENELEC | 12/31/2025
Upgrade Seward Terminal Equipment of the Seward-Blairsville 115 kV Line to increase the line rating such that the Transmission Line conductor is the limiting component. | PENELEC | 5/1/2026
Rebuild 500kV Line #574 Ladysmith to Elmont - 26.2 miles long | Dominion | 5/29/2026
Highlighted upgrades will be modeled as in-service in the annual ARR allocation and annual FTR auction
Note: See the Project Status & Cost Allocation page in the Planning section of the PJM web site for a complete list of all planned upgrades including up-to-date projections of in-service dates