## Key System Upgrades 2026_2027
System Upgrades With Potential Impact to Congestion June 2026 Through May 2027
Description | Transmission Owner | Projected In-Service Date
Construct a new 230 kV transmission line for ~3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the 500 kV line. New conductor to have a minimum summer normal rating of 1573 MVA. | Dominion | 12/19/2025
Rebuild the Chatfield-Melmore 138kV line (~ 10 miles) to 1033 ACSR conductor. | AEP | 2/24/2026
Construct a new 500 kV transmission line for ~ 3.5 miles along with substation upgrades at Wishing Star and Mars. New right-of-way will be needed and will share same structures with the line. New conductor to have a minimum summer normal rating of 4357 MVA. | Dominion | 2/28/2026
Construct a new ~3.4 mile 115 kV single circuit transmission line from Williams Grove to Allen substation. | PPL | 3/6/2026
Reconductor ~1.52 miles of 230 kV line #2031 (Enterprise-Greenway-Roundtable) to achieve a summer rating of 1574 MVA. | Dominion | 3/13/2026
Reconductor ~0.84 miles of 230 kV line #2223 (Lockridge-Roundtable) to achieve a summer rating of 1574 MVA. | Dominion | 3/13/2026
Reconductor/rebuild approximately 7.6 miles of 230 kV line #2104 Cranes Corner-Stafford to achieve a summer rating of 1047 MVA(1). Reconductor/rebuild approximately 0.34 miles of 230 kV line #2104 Stafford-Aquia Harbor to achieve a summer rating of 1047 MVA. Upgrade terminal equipment at Cranes Corner to not limit the new conductor rating. | Dominion | 4/17/2026
Install one 500/230kV 1440MVA transformer at a new substation called Wishing Star. Cut and extend 500 kV Line #546 (Brambleton-Mosby) and 500 kV Line #590 (Brambleton-Mosby) to the proposed Wishing Star substation. Lines to terminate in a 500 kV breaker and a half configuration. | Dominion | 4/30/2026
Install one 500/230 kV 1440 MVA transformer at a new substation called Mars near Dulles International Airport. | Dominion | 4/30/2026
At the existing PPL Williams Grove substation, install a new 300 MVA 230/115 kV transformer. | PPL | 5/6/2026
Rebuild 500kV Line #574 Ladysmith to Elmont - 26.2 miles long | Dominion | 5/29/2026
Rebuild the Corson-Court 69 kV line to achieve ratings equivalent to 795 ACSR conductor or better | AEC | 6/1/2026
Install a second 345/138 kV transformer at Hayes, 448 MVA nameplate rating. Add one 345 kV circuit breaker (3000A) to provide transformer high-side connection between breaker B-18 and the new breaker. Connect the new transformer low side to the 138 kV bus. Add one 138 kV circuit breaker (3000A) at Hayes 138 kV substation between B-42 and the new breaker. Relocate the existing 138 kV No. 1 capacitor bank between B-42 and the new breaker. Protection per FE standard. | ATSI | 6/1/2026
Upgrade terminal equipment on the Loretto-Fruitland 69 kV circuit: Replace the 477 ACSR stranded bus on the 6711 line terminal inside Loretto substation and the 500 SDCU stranded bus on the 6711 line terminal inside Fruitland substation with 954 ACSR conductor. | DPL | 6/1/2026
To increase the Maximum Operating Temperature of DPL Circuit 22088 (Colora-Conowingo 230 kV), install cable shunts on each phase, on each side of four (4) dead-end structures and replace existing insulator bells. | DPL | 6/1/2026
Replace line drops to Doubs transformer 3. New transformer rating: 721MVA SN /862 MVA SE | APS | 6/15/2026
Connect and energize a second 765/345 kV bank at Vassell station. | AEP | 7/15/2026
Rebuild approximately 2.3 miles of the existing North Van Wert Sw-Van Wert 69 kV line utilizing 556 ACSR conductor. | AEP | 7/23/2026
Convert 115 kV Line #172 Liberty-Lomar and 115 kV Line #197 Cannon Branch-Lomar to 230 kV to provide a new 230 kV source between Cannon Branch and Liberty. The majority of 115 kV Line #172 Liberty-Lomar and Line #197 Cannon Branch-Lomar is adequate for 230 kV operation. Lines to have a summer rating of 1047 MVA/1047 MVA (SN/SE) | Dominion | 8/14/2026
Reconductor idle 230kV Line #242 (radial from Midlothian to Trabue junction) to allow a minimum summer rating of 1047 MVA and connect to the section of 230kV Line #2066 between Trabue junction and Winterpock; re-number 230kV Line #242 structures to #2066; | Dominion | 10/30/2026
Perform sag study mitigation work on the Dumont-Stillwell 345 kV line (remove a center-pivot irrigation system from under the line, allowing for the normal and emergency ratings of the line to increase, replace two structures and modify a third structure). | AEP | 11/20/2026
Install a second 500/230 kV transformer at Possum Point substation and replace bus work and associated equipment as needed. | Dominion | 11/30/2026
Cut and loop 230 kV Line #2079 (Sterling Park-Dranesville) into Davis Drive substation and install two GIS 230 kV breakers. | Dominion | 11/30/2026
Perform a sag study on the Olive – University Park 345kV line to increase the operating temperature to 225 F. Remediation work includes two tower replacements on the line. | AEP | 12/1/2026
Upgrade the limiting element at Stillwell substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | AEP | 12/1/2026
Upgrade the limiting element at Dumont substation to increase the rating of the Stillwell-Dumont 345 kV line to match conductor rating. | AEP | 12/1/2026
Rebuild ComEd’s section of 345 kV double circuit in IL from St. John to Crete (5 miles) with twin bundled 1277 ACAR conductor. | ComEd | 12/1/2026
Rebuild 12.7 miles of 345 kV double circuit extending from Crete to E. Frankfort with twin bundled 1277 ACAR conductor. | ComEd | 12/1/2026
Reconductor NEET’s section of Crete(IN/IL border)-St. John 345 kV line (6.95 miles). | NEET | 12/1/2026
Reconductor 230kV Line #2213 from Cabin Run to Yardley Ridge along with upgrading the line leads at Yardley to achieve a summer emergency rating of 1574 MVA. | Dominion | 12/15/2026
Uprate existing Goose Creek 500/230kV transformer to 1440 MVA. | Dominion | 12/30/2026
Rebuild the Silverside – Darley 69 kV circuit | DPL | 12/30/2026
Rebuild the Darley – Naamans 69 kV circuit | DPL | 12/30/2026
Upgrade disconnect switch at Vienna to increase ratings of existing Vienna-Mardela transmission facility. | DPL | 12/31/2026
Reconductor 230kV Line #2172 from Brambleton to Evergreen Mills along with upgrading the line leads at Brambleton to achieve a summer emergency rating of 1574 MVA. | Dominion | 2/26/2027
Outside of the Green Acres substation, swap the NIPSCO Green Acre Tap towers from the St. John-Green Acres-Olive 345 kV line to the University Park N-Olive 345 kV line to create a University Park N-Green Acres-Olive and St. John-Olive 345 kV lines. | NEET | 3/30/2027
Upgrade the existing terminal equipment (substation conductor) at St. John on the existing Crete to St. John 345 kV line with bundled 2x1590 ACSR Lapwing | NEET | 3/30/2027
Upgrade the existing terminal equipment (substation conductor) at Green Acres on the existing St. John to Green Acres 345 kV line with bundled 2x1590 ACSR Lapwing | NEET | 3/30/2027
Build New Otter Creek 500 kV (Collinsville) - (switching station -Two bay three breaker configuration). | PPL | 4/23/2027
Rebuild 115 kV Line No.29 segment between Fredericksburg and Aquia Harbor to current 230 kV standards (operating at 115 kV) utilizing steel H-frame structures with 2-636 ACSR to provide a normal continuous summer rating of 524 MVA at 115 kV (1047 MVA at 230 kV) | Dominion | 4/30/2027
Build New 500kV AC line from the new Otter Creek (Chanceford) 500 kV switchyard – towards PA/MD border ~12.5 miles Ø Rebuild the existing Otter Creek - Conastone 230 kV line to become a double-circuit 500 kV line, operate Conastone circuit at 230 kV initially | PPL | 4/30/2027
Construct a double circuit 500 kV line from the existing TMI-Peach Bottom 500 kV right-of-way to the proposed Chanceford switchyard ~1.0 miles in length. | PPL | 4/30/2027
Install a 2nd 500-230 kV 1440MVA transformer at Mars substation | Dominion | 5/20/2027
Upgrade Paragon Park substation conductor and line leads to 4000A continuous current rating for 230kV Line #2207. | Dominion | 5/28/2027
Upgrade BECO substation equipment to 4000A continuous current rating for 230kV Line #2207. | Dominion | 5/28/2027
Highlighted upgrades will be modeled as in-service in the annual ARR allocation and annual FTR auction
Note: See the Project Status & Cost Allocation page in the Planning section of the PJM web site for a complete list of all planned upgrades including up-to-date projections of in-service dates