Cover

- Exhibit C: Electric Transmission Generator Interconnection Protection Requirements

Dominion Energy Virginia

Generator Interconnection Protection Requirements

| Author Name and Title | Signature | Date Reviewed |
| --- | --- | --- |
| Daniel Ridenour Engineer III, System Protection Standards |  |  |

| Approved By Name and Title | Signature | Date Reviewed |
| --- | --- | --- |
| Jonathan Deverick Supervisor - System Protection Standards |  |  |
| Philip VanSant Manager – ET Engineering Standards |  |  |

This Page Intentionally Left Blank.

Table of Contents

Exhibit C: Electric Transmission Generator Interconnection Protection Requirements	1

List of Figures and Tables	5

Abbreviations	6

Definitions	7

1	Purpose and Introduction	8

2	Wide Area Protection and Isolation	9

2.1	Line Transfer-Trip Requirements	9

2.2	Anti-Islanding Requirements	9

3	Interconnection Protection Requirements	10

3.1	Point of Interconnection Protection Requirements	10

3.1.1	Networked Transmission Line Interconnection	11

3.1.2	Transmission Tap Line Interconnection	11

3.1.3	Radial Transmission Line Interconnection	12

3.1.4	Other Considerations	13

3.2	Interconnection Generator Step-up Transformer Requirements	14

3.3	Instrument Transformer Requirements	14

3.4	Transmission Elements Requirements	14

3.4.1	Short, Medium, and Long Transmission Line Protection	14

3.5	Breaker Failure and Reclosing Equipment	16

3.6	Mandatory Protective Relay Element Coordination	16

3.7	Electrical Models of Customer Facilities	17

4	Impact of Networked Transmission Line Split on Line Terminal Protection	18

4.1	Short Transmission Line Protection	19

4.2	Medium and Long Transmission Line Protection	22

5	Power Quality Protection at Point of Common Coupling	24

5.1	Undervoltage (27)	24

5.2	Overvoltage (59)	24

5.3	Under/Overfrequency (81/U, 81/O)	24

5.4	Reverse Power (32)	24

5.5	Power Factor	24

5.6	Imbalance	24

5.7	Waveform Distortion	24

5.7.1	Harmonics	24

5.8	Voltage Fluctuations	24

6	Disturbance and Power Quality Monitoring	25

6.1	Digital Fault Recorder Requirements	25

6.2	Phasor Measurement Units/Synchrophasors Requirements	25

6.3	Power Quality Monitoring	25

6.4	Requests for Data from Customer Devices	26

Upon request from DEV, Customer power quality and Relay data shall be provided electronically to Dominion Energy no later than 14 calendar days after the date requested.	26

7	Bibliography	27

8	Revision History	28

# List of Figures and Tables

Figure 1: Complex (left) and Simplified (right) Customer Interconnection Generation Station	10

Figure 2: Network Transmission Line Interconnection	11

Figure 3: Typical Tap Line Customer Generation Interconnection Station (Generation Resources ≤ 20 MW)	12

Figure 4: Typical Tap Line Customer Generation Interconnection Station (Generation Resources > 20 MW)	12

Figure 5: Interconnection Zone of Protection	15

Figure 6: Breaker Failure and Reclosing Relays	16

Figure 7: Existing Transmission Line	18

Figure 8: Transmission Line Split	18

Figure 9: Short Line with Fiber	19

Figure 10: Traditional Zone of Protection for a Short Line	20

Figure 11: Medium Line Requiring Carrier Blocking at Distribution Substation Follows Short Line Requirements	21

Figure 12: Medium or Long Transmission Line Zone of Protection	22

Figure 13: Medium or Long Transmission Line Zone of Protection with Carrier Blocking Tap	23

# Abbreviations

CCVT (also CVT) – Coupling Capacitor Voltage Transformer (similar to Capacitor Voltage Transformer)

GSU – Generation Step-Up Transformer

MW – Megawatt(s)

N-1 – Single Contingency Outage (Normal minus One Transmission Element)

OPGW – Optical Ground Wire

PCC or POI – Point of Common Coupling or Point of Interconnection

PJM – Regional transmission organization of which Dominion Energy is a member (www.pjm.com)

SIR – Source Impedance Ratio

# Definitions

Transmission Element – Transmission elements are primary equipment (69kV and above) that constitutes, or interconnects with, the Dominion Energy Electric Transmission System. Examples include buses, lines, or transformers with low side voltage 69kV or above, regardless of Bulk Electric System status.

Breaker Failure Transfer Trip - Trips remote sources in the event of a breaker failure.

Customer Interconnected Generation Station or Customer Interconnected Collector Station – Customer owned substation containing line or collector line terminals, breakers, transformers, and protection, metering, and monitoring equipment

Dominion Energy Interconnected Switching Station – Dominion Energy owned substation containing line terminals, breakers, transformers, and protection, metering, and monitoring equipment. The Dominion Energy Interconnected Switching Station is included as a line terminal transmission substation.

Islanding Transfer Trip - Trips interconnection in the event a generating facility is operating disconnected from the transmission grid

Line Transfer Trip - Trips remote sources that are not capable of clearing a fault because current magnitude is below the protective relay scheme setpoints.

Networked Transmission Line – A transmission line that connects to two or more network transmission sources (lines and/or substations).

Radial Transmission Line - A radial transmission line is defined as a single line that has one transmission source and does NOT tie to any other transmission network source (line or substation).

Transmission Tap Line – A transmission tap line is defined as a radial line that connects to either a network or radial transmission line. Dominion Energy Facility Interconnection Requirements diagrams 5.3.2.A and 5.3.2.B provides examples.

N-1 – Contingency analysis for determining relay settings. This may be the lowest flow first contingency outage, or the highest flow first contingency outage depending on the relay element being analyzed.

Power Line Carrier (also Carrier; PLC) – Higher frequency signal coupled to the AC transmission system used to transmit one bit of information

# Purpose and Introduction

Virginia Electric and Power Company is commonly referred to as Dominion Energy.

The purpose of the Dominion Energy Electric Transmission Generator Interconnection Protection Requirements document is to provide protection requirements and expectations to any individual or group seeking to connect electric power generation to Dominion Energy’s electric transmission system.

Two primary drivers for these protection requirements are safety of personnel and customers, and the reliability of the electric transmission system.

This document supplements Dominion Energy’s Facility Interconnection Requirements document.

# Wide Area Protection and Isolation

Boundary analysis and protection studies are required for identifying transfer-trip and anti-islanding requirements. Transfer-trip and anti-islanding requirements are dependent on system configuration.

## Line Transfer-Trip Requirements

Weak, partial, or variable sources may not provide enough fault current for protective relaying to completely isolate faulted transmission elements†. Dominion Energy will require installation of transfer-trip equipment on all lines contained within the identified transfer trip boundary. The transfer-trip boundary is expanded from the POI out to the nearest remote transmission terminal substation where three or more non-generation sources are encountered. The line connecting the interconnect station to the remote station is counted towards meeting the criteria. The line connecting to the substation, which satisfies the boundary requirement, also requires transfer-trip. All transmission elements within the transfer-trip boundary are subject to transfer-trip requirements. Additional transfer-trip equipment (such as transfer-trip electronics, including relays and accessories, wave traps, CCVTs, etc.) may be required due to the installation of the generation station. Transfer-trip equipment will also be used for breaker failure conditions outlined in Section 3.7.

## Anti-Islanding Requirements

Dominion Energy will require application of its anti-islanding protection standard at all customer interconnected switching stations. Dominion Energy’s anti-islanding protection standard requires each breaker or terminal’s status within the anti-island boundary be sent to Dominion Energy’s interconnected switching station to determine whether the generation source is isolated from the rest of the electric transmission system. The purpose of the anti-islanding scheme is to prevent individual generation sources from exclusively energizing transmission elements within the islanding boundary and to prevent unsynchronized reclosing on the generator. The anti-islanding boundary is expanded from the POI out to the nearest terminal substations with three, or more, non-generation sources. The boundary substations may be included in the anti-islanding scheme depending on boundary substation configuration. The anti-islanding boundary may also be extended beyond three sources if one of the lines at the boundary exceeds its thermal limits due to unloading the generation, trips due to excessive loading, or trips due to a power swing in a power system simulation. All transmission elements within the anti-islanding boundary are subject to anti-islanding requirements. Anti-islanding schemes require separate relaying at each substation inside the anti-islanding boundary and a method to transmit breaker statuses between substations. Breaker or line terminal status will be transmitted via fiber, where available, or via power line carrier where existing fiber is unavailable and power line carrier is an acceptable transmission method (see Section 4.1 for more details).

# Interconnection Protection Requirements

Interconnection protection requirements include specifications for fault protection of the interconnection line, breaker failure and reclosing, generation step-up transformers, and instrument transformers. Determination of the necessary protection for the POI is dependent on the individual and agregate total MW of the generation resource(s), length and configuration of the interconnection line, and technical limitations of existing facilities.

## Point of Interconnection Protection Requirements

A customer-owned transformer-high-side breaker is required at the POI to separate the POI line zone of protection and the customer-owned transformer zone of protection. The customer-owned high-side breaker will be the disconnecting element should the generation source become islanded from the rest of the electric transmission system.

A high-side breaker in conjunction with a breaker ring station provides optimal isolation should a device fail to operate and initiate breaker failure (also see Section 3.7, Breaker Failure and Reclosing Requirements). To ensure reliability of the transmission system, this configuration, shown in Figure 1, is required for a POI at any network transmission line on Dominion Energy’s transmission system. A high-side breaker in conjunction with a breaker ring station is also required for a POI to a radial tap line on a network line of the transmission system for an individual generation resource or the aggregate total of generation resources that is greater than 20 MW.

For simplicity, the customer interconnection generation station will be represented as a simplified single source as shown in Figure 1.

Figure 1: Complex (left) and Simplified (right) Customer Interconnection Generation Station

### Networked Transmission Line Interconnection

The Dominion Energy Interconnection Switching Station shall be a three- or four-breaker ring, or comparable layout as outlined in Section 5 of the main document [1] for generation resources of any MW size that connect to a network transmission line. A breaker station ring ensures separation in zones of protection between the Dominion Energy electric transmission system and the customer interconnected generation station. The three-breaker ring provides increased reliability as two paths are available to export power from the generation source to the electric transmission system. The breaker ring station also creates two independent zones of protection for adjacent transmission lines allowing the generator to stay online for any single momentary or sustained line outage. See Figure 2.

Figure 2: Network Transmission Line Interconnection

### Transmission Tap Line Interconnection

The Dominion Energy Interconnection Switching Station may be a single breaker when the total aggregate generation resource connected to the tap line is less than or equal to 20 MW and connecting to a line segment that is tapped off of a networked transmission line (Figure 3). A breaker ring substation will be required for an individual generation resource or the aggregate total of generation resources from all sources on the tap line greater than 20 MW (Figure 4).

There may be instances when the generation resource(s) connected to a tap line will desensitize the network relays and not allow proper protection. Additionally, design constraints (e.g., limitations on power line carrier or transfer trip communications channels) may prove unresolvable without system upgrades including line reconductoring, expanding communication channels, building a breaker ring station, or interfacing to the transmission system through a more distant POI. A detailed protection study will be required to determine if a breaker ring station or other upgrades are required regardless of the generation resource’s size.

Figure 3: Typical Tap Line Customer Generation Interconnection Station (Generation Resources ≤ 20 MW)

Figure 4: Typical Tap Line Customer Generation Interconnection Station (Generation Resources > 20 MW)

### Radial Transmission Line Interconnection

The Dominion Energy Interconnection Switching Station may be a single breaker. However, generation resource POIs on radial transmission lines in Dominion Energy’s transmission system must be considered on a case-by-case basis to evaluate potential reduction of relay sensitivity due to fault current contributions from the generation sources. If existing line relays cannot adequately protect against fault conditions with the addition of the generation resource, additional upgrades may be required.

### Other Considerations

A generation resource may choose to have a breaker ring substation installed at the tap point to provide a more reliable interconnection regardless of POI, see Table 1 for further detail.

Table 1: Ring Bus Considerations

|  | Ring Bus connection | Single Breaker connection on tap line or radial line |
| --- | --- | --- |
| Advantages | - Increased Reliability: The generation resource will have two outlets to delivery power. An outage on the networked line will only remove one side of the ring and still allow generation. - More uptime for the generation resource that leads to higher revenue. - Initial cost savings for no utility owned breaker at POI. | - Possible decrease of initial capital cost for not building line back to networked transmission line. |
| Disadvantages | - Possible increase of initial capital cost for building line back to networked transmission line. | - Decreased Reliability: The generation resource will only have one outlet to delivery power. An outage on the tap line will remove the generation resource from service and not allow generation. - Less uptime for the generation resource that leads to lower revenue. - Additional cost for utility owned breaker at POI. |

## Interconnection Generator Step-up Transformer Requirements

The customer interconnected generation step-up transformer (GSU) is required to provide a source of zero sequence current to the transmission system aiding in ground fault detection. The utility side of the GSU shall be effectively grounded to prevent an excessive increase in voltage during single phase to ground faults. A GSU that can pass, but is not a source of, zero sequence current is only appropriate if a ground source is present on the medium voltage terminal, and will require evaluation prior to permission being granted. The interconnected GSU shall be protected using dual high-speed current differentials.

The following transformer configurations are commonly used to meet the above requirements:

- Utility side – grounded wye, generator side – delta (typical for synchronous generation)

- Utility side – grounded wye, generator side – grounded wye, delta on the tertiary (typical for inverted-based generation)

While utility side delta – generator side grounded wye transformers are appropriate for applications in a fully radial system where energy always flows from transmission-level voltages to distribution-level voltages, this design blinds high-side residual and/or ground devices to potential problems behind the transformer. For applications in systems with the ability to produce network flows, ground sources are required.

See Section 3.7 for more details concerning modeling of generator step-up transformers.

## Instrument Transformer Requirements

Independent three-phase capacitor coupled voltage transformer (CCVT) and current transformers (CT) connections are required for protective relaying purposes at the point of interconnection. Accuracy class “0.3WXYZ,ZZ” CCVTs will be required for all power quality applications at the Dominion Energy Interconnection Switching Station. If the interconnected transmission element is longer than 1000 feet (short, medium, or long length transmission line), two CCVTs may be used within the zone of protection at Dominion Energy Interconnection Switching Station (1) and (2) shown in Figure 6. The additional CCVT at Dominion Energy Interconnection Switching Station (2) may be accuracy class “1.2RWXYZ,ZZ” for backup impedance protect

## Transmission Elements Requirements

Protection systems classified as dual primary are required for all transmission elements connected to Dominion Energy’s transmission grid [2]. Schemes will require two independent high speed, phase and ground fault protection systems designated system one and system two. Together these systems provide a redundant set of all normal primary and backup functions.

### Short, Medium, and Long Transmission Line Protection

All interconnections will be treated as a transmission line regardless of length and Figure 5 will be protected using dual line current differential relays as shown in . Addtionally, directionalized backup elements are required thus potential is needed at both terminals. In all cases, dedicated fiber will be required between the Dominion Energy Interconnection Switching Stations (1) and the Customer Switching Station (2).

Figure 5: Interconnection Zone of Protection

## Breaker Failure and Reclosing Equipment

Separate breaker failure and reclosing relays (Figure 6) will be installed on all transmission breakers (the customer-owned high-side generation step-up transformer (GSU) breaker will only require breaker failure). All breaker failure relays will be required to send transfer trip to remote stations. A reclosing sync-check will be performed prior to the breaker closing for all time delayed reclosing attempts.

Figure 6: Breaker Failure and Reclosing Relays

## Mandatory Protective Relay Element Coordination

Per NERC Reliability Standard PRC-027, all protective relay elements subject to the standard must be analyzed by Dominion Energy System Protection Engineering prior to energization. The customer shall refer to the latest version of the standard to determine any protective element that must comply. The customer shall communicate all applicable protective relay settings and facility drawings to Dominion Energy in an electronic form at least forty-five (45) days prior to energization. The customer shall clearly identify any protective relay elements that can detect faults on the Dominion Energy transmission system.  The customer’s failure to provide protective relay settings and facility drawings in a timely manner may result in delayed energization.

Per NERC Reliability Standard PRC-027, in the event of future work nearby on the Dominion Energy transmission system, Dominion Energy and the customer may need to coordinate changes to protective relay elements.  The customer shall respond in a timely manner to communications requesting reviews of protective relay element coordination with its system.  Likewise, Dominion Energy shall respond in a timely manner to communications requesting reviews of protective relay element coordination with its system.

The customer shall provide Dominion Energy with long-term contact information for a person or group of people who Dominion Energy can reliably contact with respect to protective relays if the need should arise.  This contact shall be valid in perpetuity for as long as the customer’s facility is connected to the Dominion Energy transmission system. Failure to respond in a timely manner to inquiries sent to the last known good contact for a facility may result in Dominion Energy reporting the customer’s facility to SERC for violation of NERC Reliability Standard PRC-027.  The customer is responsible for providing Dominion Energy updated contact information as needed.  Any type of sale or transfer of ownership of the facility to another entity does not remove the new owner’s obligation to respond timely to inquiries or to provide updated contact information.  Customers should refer to the standard’s text available on the NERC website to learn more about communication requirements.

## Electrical Models of Customer Facilities

To support coordination of protective relay elements and accuracy of Dominion Energy’s short circuit, planning, and operational models of the transmission grid, the customer shall provide Dominion Energy with electrical models of the customer’s facilities and manufacturer test reports that corroborate the customer’s electrical model. The electrical models shall accurately reflect the customer’s facility. Therefore, all changes that may occur during the course of the project shall be communicated to Dominion Energy in new electrical models and updated manufacturer test reports that reflect the changes. The final electrical model and final manufacturer test reports for the customer’s facility shall be communicated electronically to Dominion Energy at least forty-five (45) days prior to energization. The electrical models shall be sufficiently detailed such that Dominion Energy can appropriately assess the impact of the customer’s facilities. The term “sufficient detail” shall be construed to mean the equipment parameters needed to model the customer’s facility such as but not limited to:

- Step up transformer impedance*

- Step down station service transformer impedance

- Transformer winding configuration

- Transformer voltage fixed tap selection (the fixed tap selection that will be used)

- Transmission line impedance

- For synchronous generation, unit impedances and grounding impedance

- For asynchronous generation, inverter make and model, and functionally accurate model of the inverter’s controls during dynamic and short circuit system conditions

*For generation step-up transformers (the transformers connecting generation to the transmission system), a frequent choice for the transformer’s winding configuration is a grounded wye-grounded wye with a buried delta tertiary winding. For short circuit electrical models, the buried delta tertiary is relevant to the development of electrical models for the zero-sequence network. Since the buried tertiary is not accessible for testing, customers shall obtain estimated values for the primary-tertiary reactance and secondary-tertiary reactance based on the transformer design from the manufacturer. Dominion Energy will not contact transformer manufacturers on behalf of customers to obtain this information. The information shall be present in test reports or other official documents from the customer.

Dominion Energy will not accept missing or incomplete electrical models for a facility. A customer’s failure to provide adequate electrical models of their facility may result in project delays.

# Impact of Networked Transmission Line Split on Line Terminal Protection

In many cases, interconnection switching stations are built near an existing transmission line (Figure 7) resulting in the existing transmission line being split into two shorter transmission lines (Figure 8). The two shorter transmission lines may require protection modifications due to power line carrier or relaying constraints (ex. a medium length line now becomes two short length lines).

Figure 7: Existing Transmission Line

Figure 8: Transmission Line Split

## Short Transmission Line Protection

Short transmission lines and line segments less than five (5) miles will be protected using dual line current differential relays. Line current differential relays require dedicated fiber be available between line and tap terminals. Relaying constraints permit the allowance of one tapped distribution substation within the line differential as shown in Figure 9.

Figure 9: Short Line with Fiber

When a direct fiber connection is not available between the interconnect station (Dominion Energy Interconnection Switching Station), remote terminal station (Dominion Energy Existing Substation), and tapped distribution station, modifications to the lines, structures, towers, conduits, terminating and other equipment may be required to accomodate a direct fiber connection between the interconnect substation, existing remote substation, and tapped distribution substation. Shown in Figure 10, the 5-mile requirement is normally between line terminal stations.

If the distance between line terminal stations is greater than 5 miles and impedance relays would require carrier blocking be installed at a tapped distribution substation due to transformer penetration, then the 5-mile requirement is between the line terminal substation and the tapped distribution substation shown in Figure 11. In summary, the 5-mile requirement is between a location with a power line carrier transmitter and a location with a power line carrier receiver.

Power line carrier will not be used on transmission lines less than 5 miles long to maintain a high level of protection system dependability. Power line carrier systems coupled to short transmission lines have low signal attenuation causing several problems. Most prominently, low signal attenuation results in high voltage standing wave ratios and can cause carrier beating between opposite terminal power line carrier equipment [3] [4]. Carrier beating results in the power line carrier strength oscillating between zero and two times rated power resulting in power line carrier equipment being damaged, shutting down entirely, or misoperating.

Short lines are also problematic for impedance relaying. Transmission lines with a source impedance ratio (SIR) of 4.0 or greater are considered electrically short [5]. Source impedance ratio is the ratio of Thévenin equivalent source impedance to line impedance. Short lines protected by impedance relays are subject to transient overreach due to suppressed voltage measured at the relay, and transient instrument and relay errors [6].

Figure 10: Traditional Zone of Protection for a Short Line

Figure 11: Medium Line Requiring Carrier Blocking at Distribution Substation Follows Short Line Requirements

## Medium and Long Transmission Line Protection

Medium and long transmission lines, longer than five (5) miles, will be protected using either dual impedance or dual differential relays.

If fiber is already available on a transmission line, upgrading existing impedance relays to differential relays at both terminals may be required to mitigate the effects that inverter based resources have on fault detection and directionality detection by protection relays.

In cases where fiber exists on a line, but the line has a tapped distribution station that does not need carrier blocking at the tapped substation, upgrading existing impedance realys to new impedance relays at both terminals that can accommodate a directional comparison blocking (DCB) scheme over fiber may be required to help mitigate the the effects of inverter based resources.

In cases where carrier blocking is needed at a tapped distribution station or there is no existing fiber on the line, a DCB scheme via power line carrier may be specified. Regardless, customers will not be required to install fiber on lines longer than five (5) miles.

Figure 12: Medium or Long Transmission Line Zone of Protection

Figure 13: Medium or Long Transmission Line Zone of Protection with Carrier Blocking Tap

# Power Quality Protection at Point of Common Coupling

Power quality relaying capable of tripping will be required at all generator interconnections for criteria listed in IEEE Standard 1159 [7] and other applicable standards. Power quality concerns associated with solar photovoltaic are reiterated in IEEE Standard 929 [8]. Protective relays can make erroneous directional determinations due to waveform distortion and other power quality issues [9]. All power quality protective elements will measure individual phase quantities. Quantities include but are not limited to:

## Undervoltage (27)

An undervoltage is an RMS decrease in AC voltage.

## Overvoltage (59)

An overvoltage is an RMS increase in AC voltage.

## Under/Overfrequency (81/U, 81/O)

Frequency deviations above or below nominal frequency.

## Reverse Power (32)

Reverse power protection may be implemented as a supervisory function or to ensure contracted power agreements are not exceeded.

## Power Factor

Power factor requirements will be based on contracted power factor agreement.

## Imbalance

Imbalance will be measured through differing phase quantities of voltage or current.

## Waveform Distortion

Waveform distortion is defined as steady-state deviation from an ideal power frequency sinusoid characterized by the spectral content of the deviation. Five primary types of waveform distortion are DC offset, harmonics, inter-harmonics, notching, and noise.

### Harmonics

Voltage or current harmonics may be calculated in terms of total harmonic distortion (THD) or total demand distortion (TDD) as outlined in IEEE Standard 519 [10].

## Voltage Fluctuations

Voltage fluctuations are defined as a varying voltage between 0.95 and 1.05 per-unit. Voltage flicker, an undesirable result of voltage fluctuations, may be measured or monitored using methods outlined in IEEE Standard 1453 [11], which is an adoption of IEC 61000-4-15.

# Disturbance and Power Quality Monitoring

Disturbance and power quality monitoring equipment must be independent of any protective equipment used for tripping outlined in Section 2 through Section 5 and must be time synched to UTC with a satellite clock.

## Digital Fault Recorder Requirements

A digital fault recorder (DFR) is required at all interconnected transmission substations. This device will provide high integrity triggered oscillography (minimum 4800 Hz sampling), triggered long-term RMS plus phase data (minimum 960 Hz sampling) and continuous oscillography data (minimum 720 Hz sampling) for the purpose of disturbance location and analysis. The device must also serve as a sequence of events recorder (minimum 1 millisecond resolution) logging all circuit breaker activity.  Digital fault recorder data will be the primary means for fault and event analysis.  Data must adhere to the IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 [12] or later and IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 [13] or later.

    - Customers must provide breaker position for all GSU high side breaker(s) via the a-finger contacts to the utility’s DFR.  This is to ensure millisecond accuracy of the sequence of events report.

    - Customers must provide breaker failure lockout position for all GSU high side breaker(s) via a physical contact to the utility’s DFR.  This is to ensure millisecond accuracy of the sequence of events report.

    - Any additional trip paths from the Customer Interconnection site to the utility must be monitored and recorded by the utility’s DFR. This is to ensure millisecond accuracy of the sequence of events report.

## Phasor Measurement Units/Synchrophasors Requirements

Phasor measurement units are required at all interconnection substations to provide real time synchrophasor data to Dominion Energy’s synchrophasor system. PJM Manual 14D specifies all generation greater than 100 MW must provide synchrophasor data to PJM’s synchrophasor system as well.

## Power Quality Monitoring

Power quality monitoring must be independent of power quality protection and may trigger on several layers of set points. Data collected from power quality monitors will strictly be used for engineering analysis.

## Requests for Data from Customer Devices

## Upon request from DEV, Customer power quality and Relay data shall be provided electronically to Dominion Energy no later than 14 calendar days after the date requested.

# Bibliography

- "Facility Interconnection Requirements," Section 5

- "Facility Interconnection Requirements," Dominion Energy, most recent version.

- Special Considerations in Applying Power Line Carrier for Protective Relaying, IEEE Power Systems Relaying Committee, Working Group H9.

- IEEE Guide for Power-Line Carrier Applications, IEEE Std 643, 2004.

- M. J. Thompson and A. Somani, A Tutorial on Calculating Source Impedance Ratios for Determining Line Length, 2015.

- D. Costello and K. Zimmerman, CVT Transients Revisited - Distance, Directional Overcurrent, and Communications-Assisted Tripping Concerns, 2012.

- IEEE Recommended Practice for Monitoring Electric Power Quality, IEEE Std 1159, 2009.

- IEEE Recommended Practice for Utility Interface of Photovoltaic (PV) Systems, IEEE Std 929, 2000.

- Protective Relaying and Power Quality, IEEE Power System Relaying Committee.

- IEEE Recommended Practice and Requirements for Harmonic Control in Electric Power Systems, IEEE Std 519, 2014.

- IEEE Recommended Practice--Adoption of IEC 61000-4-15:2010, Electromagnetic compatibility (EMC)--Testing and Measurement Techniques--Flickermeter--Function and Design Specifications, IEEE Std 1453, 2011.

- IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), IEEE C37.111.

- IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), IEEE C37.232.

# Revision History

| Revision Date | Revision # | Description | Revised By | Effective Date |
| --- | --- | --- | --- | --- |
| 02/10/2022 | 4.0 | See Details for Revision 4.0 | Daniel Ridenour | 04/01/2022 |
| 2/23/2021 | 3.1 | See Details for Revision 3.1 | Joseph Saylor | 04/01/2021 |
| 12/11/2018 | 3.0 | See Details for Revision 3.0 | Douglas Ladd | 1/1/2019 |
| 5/26/2017 | 2.0 | See Details for Revision 2.0 | Marlu Deverick | 06/01/2017 |
| 8/17/2015 | 1.0 | See Details for Revision 1.0 | Christopher Mertz | 01/01/2016 |
| 7/16/2015 | 0.0 | Document Creation | Christopher Mertz | - |

Details for Revision 1.0

- Updated short-line requirement drawings to show fiber into relaying at tapped distribution station

- Modified wording to exclude customer-owned GSU breaker from reclosing requirement

Details for Revision 2.0

- Revised references for new Dominion Energy corporate identity.

- Added additional definitions and minor sentence changes

- Updated reference 6

Details for Revision 3.0

- Added clarification for interconnections on network tap lines and radial lines.

- Expanded on Section 3.4

- Rearranged layout of several sections to improve flow of material

Details for Revision 3.1

- Updated the signature page

- Added Section 3.6 and 3

Details for Revision 4.0

- Minor formatting changes throughout document

- Expanded on Section 3.6

- Updated the signature page

Details for Revision 5.0

- Added reference to Section 3.2 pointing to Section 3.7.

- Expanded on Section 3.6

- Expanded on Section 3.7

- Minor typographical and grammatical improvements throughout document

- Removed Section 7; Attachment 5 now contains this information and additional detail