- Exhibit D - Dominion Energy Bulk Power System Generator Ride-Through Requirements

Dominion Energy Virginia
Bulk Power System Generator 
Ride-Through Requirements

| Author Name and Title | Signature | Date Reviewed |
| --- | --- | --- |
| ??? Engineer III, Electric Transmission Planning & Strategic Initiatives |  |  |

| Approved By Name and Title | Signature | Date Reviewed |
| --- | --- | --- |
| Mathew Parker Manager Electric Transmission Planning & Strategic Initiatives |  |  |
| Ronnie Bailey Director Electric Transmission Planning & Strategic Initiatives |  |  |
| Brian Starling Manager System Protection Engineering |  |  |
| Jason Hawkins Director ET Engineering |  |  |

Ride-Through Requirements for Bulk Power System (BPS) Resources

Dominion Energy’s voltage ride-through requirements are derived from NERC PRC-024 and other NERC guidelines related to inverter-based resource (IBR) integration. If the inverter lacks sufficient setpoints within its internal controls, the longest ride-through time duration shall be retained for all thresholds of increasing severity.  For example, if the inverter has only one (1) low voltage setpoint, the low voltage ride-through duration shall be set to three (3) seconds.

Table 1: Dominion Energy Ride-Through Requirements (69 - 499 kV)

Figure 1: Dominion Energy Ride-Through Requirements (69 - 499 kV)

Generators interconnecting at 500kV must be able to continuously operate through 1.15 Vpu, as Dominion Energy operates the 500kV system typically between 1.00 and 1.10 Vpu.  Ride-through requirements for 500kV interconnections as modified to accommodate the operating point.

Table 2: Dominion Energy Ride-Through Requirements (500 kV)

Figure 2: Dominion Energy Ride-Through Requirements (500 kV)

Dominion Energy’s frequency ride-through requirements adheres to NERC PRC-024 and other NERC guidelines related to inverter-based resource (IBR) integration. The generation Interconnection Customer Facility shall have frequency ride-through capability and shall be set such that generation units remain connected during frequency excursion defined in NERC Reliability Standard PRC-024-3, Attachment 1.

| Revision Date | Revision # | Description | Revised By | Effective Date |
| --- | --- | --- | --- | --- |
| 02/27/2023 | 3.0 | Updated signature page | Amirreza Sahami | 04/01/2023 |
| 2/7/2022 | 2.0 | Add frequency ride-through requirements | Jiecheng Zhao | 04/01/2022 |
| 1/19/2021 | 1.0 | Initial creation of document | Chris Mertz | 04/01/2021 |