Cover

Virginia Electric and Power Company - (DP, TO)

Electric Transmission

d.b.a. Dominion Energy Virginia

| Author Name and Title | Signature | Date Reviewed |
| --- | --- | --- |
| Amirreza Sahami Engineer III, Electric Transmission Planning |  |  |

| Reviewed By Name and Title | Signature | Date Reviewed |
| --- | --- | --- |
| Donnie Wilkerson Senior NERC Compliance Specialist, ET Compliance |  |  |

| Approved By Name and Title | Signature | Date Approved |
| --- | --- | --- |
| Harrison Potter Manager, Electric Transmission Planning & Strategic Initiatives |  |  |
| Mathew Parker Manager, Electric Transmission Planning & Strategic Initiatives |  |  |
| Ronnie Bailey Director, Electric Transmission Planning & Strategic Initiatives |  |  |

| Approved By Name and Title | Signature | Date Approved |
| --- | --- | --- |
| Nancy Ashberry Director, Electric Transmission NERC Reliability Compliance |  |  |

TABLE OF CONTENTS

1.0	Purpose	4

2.0	REFERENCES	4

3.0	Applicability	4

4.0	PROCEDURE	5

4.1.	Supplemental Material per NERC Std FAC-001 Guidelines and Technical Basis	10

4.1.1.	Procedures for requesting a new Facility interconnection or material modification to an existing interconnection	10

4.1.2.	Data required to properly study the interconnection	11

4.1.3.	Voltage level and MW and MVAR capacity or demand at point of interconnection	11

4.1.4.	Breaker duty and surge protection	11

4.1.5.	System protection and coordination	12

4.1.6.	Metering and telecommunications	14

4.1.7.	Grounding and safety issues	23

4.1.8.	Insulation and insulation coordination	24

4.1.9.	Voltage, Reactive Power, and power factor control	25

4.1.10.	Power quality impacts	28

4.1.11.	Equipment Ratings	28

4.1.12.	Synchronizing of Facilities	29

4.1.13.	Maintenance coordination	31

4.1.14.	Operational issues (abnormal frequency and voltages)	32

4.1.15.	Load-shed program as required by PJM	32

4.1.16.	Communications and procedures during normal and emergency operating conditions.	33

4.2.	Transmission Line Connections – Generation	35

4.2.1.	Single circuit interconnections to a transmission line	36

4.2.2.	Transmission interconnections located remote from a transmission line	37

4.2.3.	Interconnection to Radial Transmission Line or Radial Transmission Tap	39

4.2.4.	Substation interconnection requirements	41

4.2.5.	Transmission interconnection breakers	42

4.2.6.	Generation interconnection breakers	42

4.3.	Load Criteria – End User	44

4.3.1.	Tapping line for loads below 100 MW	46

4.3.2	Tapping lines for loads 100 MW and greater	49

4.4.	Prohibited arrangements and allowable alternatives	51

4.5.	Tapping Company’s bus	54

5.0	Definitions & Abbreviations	56

5.1.	Definitions	56

5.2.	Abbreviations	57

6.0	Revision History	58

Attachment 1: Dominion Energy Virginia Electric Transmission Planning Criteria

Attachment 2: Customer Request Form

Attachment 3: Dominion Energy Virginia Generator Interconnection Protection Requirements

Attachment 4: Dev Bulk Power System Generator Ride-Through Requirements

Attachment 5: Electric Transmission Generator Interconnection Data Communications and Data Exchange Requirements

Purpose

Purpose of NERC Standard FAC-001: To avoid adverse impacts on the reliability of the Bulk Electric System, Transmission Owners and applicable Generator Owners must document and make Facility interconnection requirements available so that entities seeking to interconnect will have the necessary information.

Purpose of this Document: This Virginia Electric and Power Company d/b/a Dominion Energy Virginia-Electric Transmission (DEV-ET) NERC Compliance Procedure (NCP) establishes a primary resource for procedures (detailed within the document or referenced) that demonstrate DEV-ET’s compliance with NERC Standard FAC-001, Requirements R1 and R3.

REFERENCES

North American Electric Reliability Corporation (NERC) website at www.nerc.com

NERC Glossary of Terms

NERC Reliability Standards

PJM Manual 14A: New Services Request Process

PJM Manual 14C: Generation and Transmission Interconnection Facility Construction

PJM Manual 14D: Generator Operational Requirements

PJM Manual 14G: Generation Interconnection Requests

PJM Manual 01: Control Center and Data Exchange Requirements

PJM Manual 03: Transmission Operations

Applicability

Applies to Virginia Electric and Power Company – (DP, TO) as a registered Transmission Owner (TO) with NERC.

NERC Reliability Standard FAC-001 Requirements applicable to DEV-ET as a registered TO: R1 and R3.

NERC Reliability Standard FAC-001 Requirements not applicable to DEV-ET as a registered TO: R2 and R4.

PROCEDURE

R1

Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for:

    - generation Facilities;

    - transmission Facilities; and

    - end-user Facilities.

Compliance R1

DEV-ET’s Facility Interconnection Requirements (FIR) document is publicly available on the company’s web site (www.dominionenergy.com) and is provided to PJM (www.pjm.com) to provide guidance to Interconnection Customers seeking to connect to its Transmission System.  It also serves as evidence that DEV-ET documents Facility interconnection requirements, updates them as needed, and makes them available upon request, as required by NERC Standard FAC-001.

DEV-ET is also referred to in this document “Company”.

- 1.1 Generation Facilities

This document complies with NERC Standard FAC-001 Requirement R1.1 by addressing interconnection requirements for generation Facilities for each subrequirement of NERC Standard FAC-001 Requirement R3.

- 1.2 Transmission Facilities

This document complies with NERC Standard FAC-001 Requirement R1.2 by addressing interconnection requirements for transmission Facilities for each subrequirement of NERC Standard FAC-001 Requirement R3.

- 1.3 End-user Facilities

This document complies with NERC Standard FAC-001 Requirement R1.3 by addressing interconnection requirements for end-user Facilities for each subrequirement of NERC Standard FAC-001 Requirement R3.

The provisions of this document apply to Interconnection Customers seeking to connect to DEV-ET’s Transmission System, except as may be otherwise provided for in applicable tariffs or agreements, or as may be otherwise agreed by DEV-ET and the Interconnection Customer.

R3

Each Transmission Owner shall address the following items in its Facility interconnection requirements:

  - Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s).

  - Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections.

  - Procedures for confirming with those responsible for the reliability of affected systems that new or materially modified Facilities are within a Balancing Authority Area’s metered boundaries.

Compliance R3

DEV-ET individually addresses the interconnection requirements of generation, transmission, and electricity end-user Facilities in this document. These Facility interconnection requirements are to be adhered to by any requesting Interconnection Customer who wishes to establish a connection to DEV-ET’s transmission Facilities.  DEV-ET adheres to these same requirements as it constructs additions to its Transmission System.  These requirements should be evaluated as a whole when determining the actions necessary to develop a complete interconnection request.

Transmission connections covered by this document include all generation resources, ties with transmission Facilities owned by others, and Interconnection Customer substations at voltages of 69 kV or greater. It is not practical to include the particular requirements applicable to every possible transmission connection scenario since each connection is specific to the party requesting the connection and the Transmission System at the point of customer connection.  There are several factors to be considered when connecting DEV-ET’s Transmission System to (1) another transmission system, (2) a new or additional generation, and (3) a new or additional customer load. The evaluation of these factors requires a power system analysis of the transmission network as described in Attachment 1 of this document.

The standards in this document apply to new Facilities and to modification of existing Facilities.  The standards in effect at the time a Facility was constructed or modified are to continue to apply to such Facility until it is subsequently modified, or until DEV-ET or PJM determine the Facility must be upgraded to the current standard to avoid unacceptable risk to the reliability or operation of the Transmission System, or to the safety of workers or the public.

Typical connections are provided in Attachment 1 of this document.

This section identifies the requirements and subrequirements of NERC Reliability Standard FAC-001 R3, along with additional information per the standard’s associated Supplemental Guidelines.  Unless otherwise noted, details under each topic in this section apply globally to generation Facilities, transmission Facilities, and end-user Facilities.  For topics warranting additional, specific requirements regarding generation Facilities, transmission Facilities, and/or end-user Facilities, an associated sub header is clearly provided for the reader.

R3.1

Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s).

Compliance R3.1

The following is DEV-ET’s procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected systems.

Utility Interconnections

DEV-ET’s Planning group performs planning studies to ensure delivery of bulk power to a continuously changing customer demand under a wide variety of operating conditions.

Should DEV-ET receive an interconnection request that may impact a neighboring interconnected transmission system, DEV-ET initiates contact with that neighboring system for the purpose of coordinating those joint interconnection studies required to assess the impact of the interconnection request on the transmission systems of all affected parties.

Studies are performed in coordination with DEV-ET’s Regional Transmission Organization (PJM Interconnection, L.L.C.), and in accordance with NERC Reliability Standards, which promote and maintain the reliability and security of the interconnected bulk power system.

DEV-ET has entered into various Inter-Area Reliability Agreements with neighboring utilities. The major purpose of these agreements is to further augment reliability and security of each member’s bulk power supply system through coordination of planning and operation of their generation and bulk power transmission Facilities. The following is a list of groups with which DEV-ET engages in joint transmission interconnection activities:

- Southeastern Electric Reliability Council (SERC) East-RFC (SER) Studies under the Eastern Interconnection Reliability Assessment Group (ERAG) Agreement

- SERC Intra-Regional Near-Term Studies

- SERC Intra-Regional Long-Term Studies

- ERAG – Multi-Regional Modeling Working Group (MMWG)

Each of these groups has various Working Groups, Study Groups, Committees, Task Forces etc. that deal with various aspects of power system reliability and security issues.  Various studies performed by these groups at the interconnection level include: power flows, stability, transfer capabilities, voltage collapse scenarios, tie-line re-closing angles, etc.  The basic purpose of these studies is to measure the ability of the transmission network to reliably transfer power in bulk amount from one area to another under the most limiting contingency assumptions that are judged to be credible. These studies can be used in identifying any deficiencies and the needed corrective actions, either through short term operating procedures or by future system upgrades.  Transmission interconnections are planned such that the amount of power that can be transferred between and among the utilities, in addition to firm transactions, is adequate to withstand the most severe credible generation and transmission contingency.

Wholesale Delivery Points

DEV-ET provides transmission service to wholesale delivery points throughout its service area under Mutual Operating Agreement(s) (MOA).  The criteria for serving wholesale Interconnection Customers are the same as that used to serve DEV-ET’s other customers and is predicated on “Good Utility Practice” and sound engineering and economic principles without regard for the ownership of the Facilities.

Regardless of the generation source of supply to wholesale customers in the company’s service area, all supplies are delivered over the company’s transmission Facilities.  Therefore, it is essential that wholesale Interconnection Customer load requirements be included in the company’s planning process.

The following criteria apply to all joint planning between DEV-ET’s and its wholesale Interconnection Customers:

- Contractual obligations must be observed.

- Studies must be based on sound engineering and economic principles consistent with long range system plans.

- All applicable sections of the DEV-ET Planning Criteria as stated in Attachment 1 of this document are to apply to the connection of any wholesale Interconnection Customer to DEV-ET’s Transmission System.

Joint planning should be conducted periodically with each wholesale Interconnection Customer.  This joint plan includes a review of each company’s construction program based on annually updated load forecasts for the general area.  The procedure is similar to the following:

- Load forecasts for each year up to ten years will be prepared by the wholesale Interconnection Customer for their area and by DEV-ET for the general area around the Interconnection Customer.

- Special emphasis should be given to identify high load growth areas.

- Existing distributed generation output for both conventional and alternative (solar, wind, etc.) sources, indicating the maximum output of each unit/site, and the output of each unit/site that is coincidental to the summer and winter peak day and time for the DEV zone.

- The Interconnection Customer and DEV-ET each prepares preliminary studies of their respective systems for meeting the future load requirements identified by the forecasts.

- The Interconnection Customer and DEV-ET exchange study information and, based on joint analysis, prepare a long-range plan.

There will be instances where deviations from the long-range joint planning process are necessary to accommodate third party delivery point requests.  In these cases, the DEV-ET’s Planning Department and, as needed, entities interconnected with DEV-ET Facilities, expedite review of appropriate elements of the long-range plan to address such projects.

All delivery point requests include a completed “Customer Request Form” as shown in Attachment 2 of this document.

R3.2

Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections.

Compliance R3.2

The Interconnection Customer is to notify DEV-ET of planned additions of new Facilities, or modifications to existing electrical Facilities which have the potential to impact the reliability of the interconnected transmission systems.  Interconnection Customers are to provide such notification as soon as it is feasible for them to do so, even if the information is in a preliminary form.  Prompt notification is important so that DEV-ET can begin any needed coordination with other entities responsible for the reliability of interconnected transmission systems.  Attachment 2 of this document, “Customer Request Form”, is to be completed for initial requests as well as subsequent changes.

The form is to be submitted with sufficient advance notice to allow DEV-ET to:

- review the proposed addition or modification,

- conduct the necessary studies to assess the impact of the change on DEV-ET’s System and/or neighboring Facility owners,

- respond to the requesting Facility owner

- complete any necessary modifications to DEV-ET Facilities including ownership demarcation of equipment and/or Protection System(s) elements.

Subsequent changes to the approved design basis are interpreted to include, but are not limited to:

- changes to electrical equipment ratings

- changes to primary conductor(s) or connectors

- changes to transformer tap settings

- changes impacting Protection Systems such as:

- significant source impedance changes at the interconnection point

- modifications to Protection System communications equipment

- modifications to Protection System relay settings

- changes to breaker reclosing times

- Interconnection of new generating Facilities, including distribution connected generation

As modifications are determined to impact other parties, such as power generators, end users, and interconnect parties, DEV-ET will make appropriate notifications and pursue mutually agreeable resolutions as necessary.

R3.3

Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified transmission Facilities are within a Balancing Authority Area’s metered boundaries.

Compliance R3.3

PJM is the Balancing Authority (BA) for DEV-ET.

PJM Compliance Bulletin CB028 NERC Standard FAC-001 – Facilities within the metered boundaries of a Balancing Authority, specifies that PJM assesses facilities within its Balancing Authority Area metered boundaries. An Interconnection customer with new or materially modified transmission Facilities seeking interconnection to, or upgrade facilities on the PJM system must do so via the PJM New Services Queue.  PJM approved projects are given an Interconnection Service Agreement (ISA) and/or an Upgrade Construction Service Agreement (UCSA) and sent to FERC for review and approval.  When FERC approves the ISA/UCSA, PJM sends a copy of the approved ISA/UCSA to DEV-ET Planning where it is filed.  PJM specifies that the presence of a PJM issued ISA/UCSA is evidence that can be used by each interconnection customer as confirmation that their new or materially modified Facilities are within the PJM Balancing Authority Area’s metered boundaries.

Supplemental Material per NERC Std FAC-001 Guidelines and Technical Basis

Procedures for requesting a new Facility interconnection or material modification to an existing interconnection

To install, modify, or remove DEV-ET Facilities, or to modify the capacity or characteristics required at a Delivery Point, or to discontinue the delivery of electricity to a Delivery Point, Customer is to initiate requests in writing using the Request/Notification for Changes Impacting DEV-ET Facilities form included in this document. Customer is to also submit a Request Form when making changes to Customer’s Facilities that are reasonably anticipated to (i) lead to a modification to DEV-ET’s Facilities or (ii) impact the operation of DEV-ET’s Facilities.  See Attachment 2 of this document.

Data required to properly study the interconnection

The Request Form is to be submitted by Customer as soon as useful information is available. As additional or updated information becomes available, Customer is to make timely submission of a revised Request Form. For Request Forms submitted with notations of “(E)” or “TBD by [date]” as described below, DEV-ET and Customer is to determine a schedule for the provision of complete and final information.  See Attachment 2 of this document, pages B-3 thru B-5.

Voltage level and MW and MVAR capacity or demand at point of interconnection

Except as may be otherwise provided for in applicable tariffs or agreements, or as may be otherwise agreed by DEV-ET and the Interconnection Customer, the Interconnection Customer should use the “Customer Request Form” shown in Attachment 2 of this document to provide DEV-ET with the necessary information regarding the voltage level and MW and MVAR capacity or demand at point of connection.  Since voltage and interconnection points are site-and project-specific, DEV-ET will perform studies and exercise engineering judgment to determine appropriate voltage levels, interconnection points, and system capabilities.

Breaker duty and surge protection

Electrical circuit breakers are to be designed to meet or exceed the expected load and short circuit currents on the Interconnection Customer’s transmission system. High voltage circuit breakers and other current interrupting devices are to be designed to clear (interrupt) the worst-case short circuit fault calculated for the protection zone as determined using fault analysis engineering programs.

All current carrying equipment and devices are to be designed to carry the maximum loads that are predicted by load flow analysis.  Loads exceeding “nameplate” or “normal” design capacities are only acceptable when allowed by manufacturers design documentation or standard industry practices.

Circuit breakers are to be designed and tested according to the latest Institute of Electrical and Electronics Engineers (IEEE) C37 collection of standards.

Shielding, and surge protective devices are to meet the requirements as determined by lightning and switching surge analysis, and the latest IEEE C62 standards.

Basic Impulse Levels (BIL) for electrical equipment and high voltage substation buses are to meet or exceed DEV-ET’s standard values listed below.

| Nominal KV (phase to phase) | Basic Impulse Level (BIL) |
| --- | --- |
| 115 | 550 |
| 138 | 650 |
| 230 | 900 |
| 500 | 1550 |

The Interconnection Customer must meet the following design requirements described in NERC Reliability Standard FAC-001 and its SERC Guideline:

- Each party is responsible for designing equipment to meet the short circuit capabilities on their Facilities.

- Each party is responsible for the ratings of their own interrupting devices. It is the responsibility of the Interconnection Customer to coordinate their relays and devices with DEV-ET’s Transmission System.

- Parties are to provide existing and future fault current levels when requested.

- It is the responsibility of the Interconnection Customer to notify DEV-ET of any changes in their Facilities that may cause an increase in fault currents (generator and transmission Interconnection Customers).

System protection and coordination

The Interconnection Customer is responsible for providing a properly designed and tested Protection System that will safeguard the general public, protect its equipment against disturbances on DEV-ET’s system, and minimize the effects of disturbances from its Facilities on DEV-ET’s equipment and Transmission System.  Protection Systems installed by the Interconnection Customer are expected to follow the latest IEEE C37 and C57 guides and standards for protective relaying systems and adhere to all NERC and PJM standards related to system protection.  The Interconnection Customer’s Protection System is to coordinate with the interconnected Protection System owned by DEV.  NERC Reliability Standards, operating voltage and proximity to a generating unit will be major considerations for establishing the required protection scheme on a transmission line that connects to DEV-ET’s transmission grid.  For more information on generator interconnection, see Attachment 3 of this document.

Prior to the development of the Protection System, the Interconnection Customer should complete all appropriate studies, including, but not limited to, grounding studies, short circuit studies, stability studies, and power quality studies. These studies should be completed using Good Utility Practice and the results made available to DEV-ET upon request.

In addition, DEV-ET performs studies on existing Protection Systems which may require changes to the Interconnection Customer’s Protection System.  In such cases, those customers will be notified and consulted regarding the changes required to ensure the reliable operation of DEV-ET’s transmission Facilities.

Protection System Design

The Interconnection Customer is to design the Protection System to minimize the effects of disturbances from its Facilities affecting DEV-ET interconnected Transmission System or customers.  The Protection System is to:  be adequately sensitive to detect all faults and abnormal conditions, provide coordination between protection zones, and operate quickly to achieve Transmission System reliability.  In some cases, DEV-ET may require the Interconnection Customer to install additional equipment as necessary to address issues such as, but not limited to: relay overreach, transformer penetration, weak source, source impedance ratio (SIR), anti-islanding, and power quality.  DEV-ET is to own and maintain transmission Protection System elements necessary to protect the transmission portion of the interconnection; however, DEV-ET is not responsible for protection of the Interconnection Customer’s equipment and other electrical assets.

The Protection System is to protect against or minimize the effects of abnormal conditions including, but not limited to, over/under-voltage, over/under-frequency, harmonics, overload, short circuits, open circuits, phase imbalance, switching surges, lightning surges, and other harmful electrical conditions. Utility grade protective relays and fault clearing systems are to be provided on the interconnected power system. All protective relays are to meet or exceed American National Standards Institute (ANSI)/IEEE Standard C37.90. Mechanical and electrical logic, interlocking mechanisms, and operational data may be required between interconnected Facilities to ensure safe and reliable operation. Examples of mechanical and electrical logic, interlocking mechanisms, and operation data include, but are not limited to, breaker and switch auxiliary contacts, synch-check relays, physical locking devices, solar irradiance, and inverter operating modes or setpoints.

The following defines DEV-ET’s protection requirements for protecting transmission elements connecting to DEV-ET’s transmission grid.

Dual Primary Phase and Ground Protection Systems

Protection Systems classified as Dual Primary are required for all transmission elements connecting to DEV-ET’s transmission grid.  This scheme will require two independent high-speed, phase and ground fault Protection Systems designated System 1 and System 2. Together these systems provide a redundant set of all normal primary and backup functions.

Breaker Failure Protection

A breaker failure function is required for all interrupting devices of transmission elements connecting to a DEV-ET transmission bus as defined by the protection scheme. For Generation Interconnections, there are additional requirements as outlined in Attachment 3 of this document, Section 3 Interconnection Protection Requirements.

Protection System Components

The Interconnection Customer’s Protection System, including the protective relays, associated communication systems, voltage and current sensing devices, station batteries and DC control circuitry, must be compatible with DEV-ET’s standard design for common equipment and/or common zones of protection.  Compatibility includes protection application, redundancy, operating speed, communication type, and communication medium.

The Protection System must be powered by a DC battery for reliability.  The battery is to be sized to power continuous loads for a minimum of 8 hours and power all momentary tripping loads without a charger available. The battery sizing calculation is to be in accordance with IEEE 485.  A DC under-voltage alarm must be provided for remote monitoring by the Facilities owner, who are to take immediate action to restore power to the protective equipment.

Protection System Misoperations

The Interconnection Customer is to investigate all Protection System operations and misoperations, affecting the interconnected Facility and will provide DEV-ET with the findings of the investigations upon request.  Likewise, DEV-ET will cooperate with the Interconnection Customer and will provide any necessary findings related to Protection System operations and Misoperations directly affecting the interconnected Facility subject to code of conduct restrictions.

Metering and telecommunications

Metering

DEV-ET approved revenue metering equipment is to be installed for energy accounting and billing purposes.  Except as may be otherwise provided for in applicable tariffs or agreements, or as may be otherwise agreed by DEV-ET and the Interconnection Customer, the Interconnection Customer is to install, own, operate and maintain all revenue metering equipment as set forth below.

Interconnection Customers that will be a PJM market participant is to install metering that is to be of sufficient quality to meet the applicable requirements as defined in PJM Manuals 14A – New Services Request Process, 14C – Generation and Transmission Interconnection Facility Construction, 14D – Generator Operational Requirements, and 01 – Control Center and Data Exchange Requirements.  Additional requirements may be applicable on a case-by-case basis.

Revenue metering equipment includes, but is not limited to, current transformers, voltage transformers, revenue meters, meter sockets, test switches, communication circuits and associated devices.  The revenue metering equipment is to be located at the Interconnection Customer’s Facility unless otherwise agreed to by DEV-ET, PJM, and the Interconnection Customer (referred to collectively in this section as the “Parties”).  The revenue metering equipment is to meet or exceed all applicable industry standards (e.g., NERC, PJM, ANSI, IEEE, and National Electrical Manufacturers Association (NEMA)).  At least (N-1) metering elements are to be used for the revenue metering, where N is the number of wires in the electrical system associated with the revenue metering. Three metering elements are to be the standard for revenue metering unless otherwise agreed to by the Parties. The revenue metering installation is to meet all applicable industry standards for phase-to-phase and phase-to-ground electrical clearances.

DEV-ET will provide the Interconnection Customer with manufacturer’s installation information for the current and voltage transformers when these devices will be furnished by DEV-ET and installed by the Interconnection Customer.

Revenue Meters

The revenue meters are to be capable of recording, storing, and transmitting bidirectional megawatt-hour (MWh) data and megavar-hour (MVARh) data. However, if required by the applicable tariffs, or if mutually agreed by the Parties, the revenue meters are to instead record bi-directional kilowatt-hour (kWh) data and kilovar-hour (kVARh) data. In general, this data is to be recorded in hourly intervals unless other interval lengths are required by the applicable tariffs or agreed upon by the Parties.

The revenue meters are to have an accuracy class of 0.2% standards as defined in ANSI C12.20.  In addition, the revenue meter should meet ANSI C12.1 and C12.10 standards.  Testing of meters in service may be requested by DEV-ET, any regulatory agency having jurisdiction over the interconnection, or any other lawfully constituted authority having jurisdiction over meter accuracy.

Revenue Metering Current Transformers

The revenue meters are to be connected to current transformers (CTs) having a minimum metering accuracy class of 0.15% (as defined in IEEE C57.13) at a minimum burden designation of B-1.8 from 1% of nameplate to rating factor.  CTs with standard accuracy and/or lower burden designations may be allowed by DEV-ET in special cases, but the secondary burden on the CTs must not exceed the nameplate burden rating.  In addition, the CTs meet the ANSI C12.11 standard.  The continuous current on the CTs are not to exceed the primary nameplate rating with the thermal current rating factor (RF) applied. The available fault current must not exceed the mechanical and short time thermal limits of the CTs.  The revenue meters are to generally be connected to dedicated metering CT secondary circuits and should not share the same circuits with relays or other devices.  In cases where power flow varies significantly (e.g., at wind generation Facilities), the Interconnection Customer may be required to provide extended range CTs or additional metering equipment at their own expense.

Revenue Metering Voltage Transformers

The revenue meters are to be connected to voltage transformers (VTs) or coupling capacitor voltage transformers (CCVTs) having a minimum metering accuracy class of 0.3% (as defined in IEEE C57.13) with a minimum burden on the VTs or CCVTs that exceeds the circuit burden.  In addition, the VTs and CCVTs should meet the ANSI C12.11 standard.  The revenue meters are to be connected to dedicated metering VT or CCVT secondary circuits and should not share the same circuits with relays or other devices; however, if the VTs or CCVTs have separate secondary windings used for relays or other devices, the revenue meters may be connected to dedicated secondary windings of such VTs or CCVTs.  VTs are preferred for revenue metering. The use of CCVTs for revenue metering is to be limited to Facilities connecting to DEV-ET system voltages 115 kV and higher or where DEV-ET has determined it is impractical to use VTs for technical reasons.

Revenue Metering Data Communications

The Interconnection Customer is to, at its own expense, install, operate, test, and maintain any communications equipment required by DEV-ET to remotely retrieve revenue metering data from the Interconnection Customer’s Facility on a real-time or periodic basis as specified in the sections below for wholesale generation Facilities, transmission Facilities, and end user Facilities.  The communication capability of remote interrogation of the revenue data should be compatible with commonly used billing data systems such as MV-90 and Primestone.  The Interconnection Customer is to also be responsible for any high voltage isolation equipment that the local telecommunications company may require at the Interconnection Customer's Facility to protect their communications systems from damaging transient voltages that can occur in electrical substations and generation Facilities.

DEV-ET provides the Interconnection Customer access to bi-directional kWh and kVARh pulses from the DEV-ET revenue meters installed at Interconnection Customer Facilities. The pulses, which are provided upon request, is to be used as the source of the revenue metering data where applicable.  Alternatively, kWh and kVARh register accumulator data may be provided by other means, e.g., DNP, MODBUS or similar protocol, to the Interconnection Customer Facilities, in lieu of, or in addition to, analog kWh and kVARh pulses, if such arrangements are agreed upon by both Parties.

Operational Metering Data from Revenue Meters

Operational metering data (e.g., MW and MVAR) is generally not available from DEV-ET revenue meters that are provided by DEV-ET at Interconnection Customer Facilities. Except as may be otherwise provided for in applicable tariffs or agreements, or may be otherwise agreed by DEV-ET and the Interconnection Customer, the Interconnection Customer is to, at its own expense, install, operate, test, and maintain any metering and communications equipment necessary to provide operational metering data required from the Interconnection Customer's Facility by one or more of the Parties.

Revenue meters are to be capable of communicating with data acquisition system (“DAS”) equipment such as Remote Terminal Unit (“RTU”) to provide the following real-time bi-directional power and energy data for operational purposes:

- instantaneous power flows

- per phase and three-phase averaged Root-Mean-Squared (“RMS”) voltages

- per phase and three-phase averaged RMS currents with at least two decimal points

A continuous accumulating record of active and reactive energy flows are to be provided by means of the registers on the meters.  The revenue meter(s) are to be capable of providing bi-directional energy data flow in either KYZ pulse signals format, or accumulated counters to RTU. Energy data flow accumulator counters may also include register accumulator data delivered to RTU via DNP, MODBUS or similar protocol. All Parties are to share the same data register buffers regardless of the types of employed data communication methods. For generation Facilities that interconnect to DEV-ET generator interconnection substations, this revenue meter data is to be shared across serial data links established between the two facilities.  Further details regarding the requirements for this data exchange can be found in attachment 5 to this document - Generator Interconnection Data Communication and Data Exchange Requirements. This data is shared between facilities at GI substations. Requirements for this data exchange are provided in attachment 5. If the accumulation counter method is used, the owner of the meter is to be responsible for freezing the accumulator buffers and no other Party is to freeze them.  The accumulator freezing signals are to be synchronized to Universal Time Coordination (UTC) within 1/2 seconds.

The revenue meters’ internal clocks and real-time DAS equipment is to be synchronized with Universal Time Coordination (UTC) with 15 seconds resolution.

Revenue Metering Access, Security, and Testing

Where DEV-ET provides revenue metering equipment, the Interconnection Customer is to grant DEV-ET employees and authorized agents’ access to the equipment at all reasonable hours and for any reasonable purpose.  Regardless of meter ownership, the Interconnection Customer is to not permit unauthorized persons to have access to the revenue metering equipment.

The meters, test switches and any other secondary devices that could have an impact on the performance of the revenue metering is to be sealed and the seals are to be broken by the party responsible for the equipment only when tests, adjustments, and/or repairs are required.

The revenue metering is to be tested for accuracy as specified by the applicable interconnection service agreement, PJM requirements or regulatory commission regulations by the owner of the metering equipment.

Wholesale Generation Facilities

For the interconnection Facilities of Wholesale Generators, except as may be otherwise provided for in applicable tariffs or agreements, or as may be otherwise agreed by DEV-ET and the Interconnection Customer, the revenue metering equipment is to be located at the Interconnection Customer's Facility. The revenue metering is to be compensated for losses to the Point of Interconnection (POI) if the metering equipment is not located at the POI.

The revenue metering CTs and VTs are to be installed on the transmission voltage side of the Interconnection Customer’s generator step-up transformer(s) or Facility main step-up transformer and/or station service power transformers.

The specific revenue metering requirements for wholesale generation Facilities fall under one of the following categories:

DEV-ET Revenue Metering Requirements for Generation Facilities Connected                       69 kV and Higher:

The Interconnection Customer is to install, own, operate, test, and maintain the revenue metering equipment at the Interconnection Customer’s expense.  A redundant revenue meter and real-time Supervisory Control and Data Acquisition (SCADA) data is also required.  The SCADA data consists of analog MW and MVAR at all generation, load, and transmission line terminals; analog kV at all buses 69 kV and greater; circuit breaker open/close status for all breakers; other device status points (for example, automatic reclosing on/off).  It is preferred that the redundant meter have a different method of telecommunications than the primary meter.  DEV-ET provides revenue metering for station service power supply at a generation Facility if the supply is from the DEV distribution system.

DEV-ET Revenue Metering Requirements for Generation Facilities Connected Below 69 kV:

DEV-ET is to install own, operate, test and maintain the revenue metering at the Interconnection Customer’s expense.  A redundant revenue meter is also required.  It is preferred that the redundant meter have a different method of telecommunications than the primary meter.

DEV-ET Revenue Metering Requirements for Behind-The-Meter Generation Facilities Participating in the PJM or Wholesale Energy Markets:

DEV-ET is to own, operate, test, and maintain the revenue metering equipment at the POI, except as otherwise specified by the applicable retail tariff or interconnection service agreement.  The physical arrangements of such Facilities are often complex.  As such, DEV-ET makes a case-specific review of each installation and determines the revenue metering required.  Any additional metering equipment or metering data that one or more of the Parties may require for the generation equipment is the responsibility of the Interconnection Customer.

Specific Revenue Metering Requirements for Existing Non-Utility Generator Facilities That Are Ending Power Purchase Agreements with DEV-ET:

For an existing non-utility generator (NUG) that is ending its power purchase agreements with DEV-ET and will sell its power in the PJM energy market, DEV-ET is to continue to own, operate, test, and maintain the existing revenue metering equipment at the Interconnection Customer’s expense, except as otherwise specified by the applicable tariff or service agreement.  The customer is responsible for all PJM meter data reporting requirements; DEV-ET will not report the generation on behalf of the NUG to PJM. The Interconnection Customer’s RTU is to provide DEV-ET access to the operational and revenue metering data specified in Telecommunication Section.

Transmission Owner Facilities

For the interconnection Facilities of Transmission Owners, except as may be otherwise provided for in applicable tariffs or agreements, or as may be otherwise agreed by DEV-ET and the Interconnection Customer, the Interconnection Customer is to install, own, operate, test, and maintain the revenue metering equipment at its Facility. The revenue metering is to be compensated for losses to the POI if the metering equipment is not located at the POI.

The revenue metering CTs and VTs are to be installed at the point(s) where the Interconnection Customer's Facility connects to the DEV-ET System. The exact location of the revenue metering CTs and VTs are to be as determined by agreement between DEV-ET and the Interconnection Customer.

- The Interconnection Customer is to provide primary and redundant revenue meters with SCADA data. It is preferred that the redundant meter have a different method of telecommunications than the primary meter.

End-User Facilities

Except as may be otherwise provided for in applicable tariffs or agreements, or as may be otherwise agreed by DEV-ET and the Interconnection Customer, the provisions of this section apply to all end user revenue metering whether installed by DEV-ET or the interconnected end user.

For the interconnected Facilities of end users, the revenue metering is to be installed on either the primary side or the secondary side of the Interconnection Customer’s step-down transformer in accordance with the applicable interconnection agreements.  DEV-ET utilizes its best engineering judgment to determine the appropriate location for the revenue metering equipment if the interconnection agreement provides DEV-ET the option to choose either the primary side or the secondary side.

If the revenue metering is installed on the primary side of the Interconnection Customer’s step-down transformer, the DEV-ET’s CTs and VTs are to be located on the high side of the Interconnection Customer’s step-down transformer.  When revenue metering is installed by the Interconnection Customer, the proposed metering installation design must be reviewed and accepted by DEV-ET prior to installation.

If the revenue metering is installed on the secondary side of the Interconnection Customer’s step-down transformer, it is to be compensated for losses in the transformer.  The revenue metering is to also be compensated for losses in any significant length of conductors between the metering point, the step-down transformer, and the POI.

If Interconnection Customer revenue metering is compensated, the Interconnection Customer is to provide DEV-ET with the following information:

- Certified manufacturer test data for the step-down transformer including nameplate ratings, no-load losses, load losses, exciting current, and impedance.

- Primary side voltage tap setting planned for the step-down transformer if equipped with a no-load tap changer. The transformer test data specified above is to be provided for all available taps.

- Information regarding the conductors on the primary side of the Interconnection Customer’s step-down transformer, if applicable, and the secondary side including conductor type, number of conductors per phase, length, resistance, and reactance (in Ohms per conductor per 1000 feet or per mile).

- If DEV-ET specifies compensated revenue metering on the secondary side of a step-down transformer, the Interconnection Customer may install the CTs and VTs in any one of the following configurations after DEV-ET review and acceptance of the proposed design:

- An outdoor overhead metering structure with a visible break switches or disconnects on both the incoming and load sides.

- Pad mounted metering enclosure with dead-front disconnecting elbows on both the incoming and load sides.

- Switchgear metering compartment with a visible break switch or disconnect on both the incoming and load sides. The compartment must be sealable with doors on the front and back. The CTs and VTs can be picked up from the closest DEV-ET office to the interconnecting site.  The Interconnection Customer must provide DEV-ET with detailed metering compartment drawings (front, side, and rear views) that show the orientation of the CTs on the bus work and indicate electrical clearances. There must be adequate working clearances around the CT and VT secondary terminal boxes for DEV-ET meter personnel to install the secondary wires.

For end-user Interconnection Customer’s Facility with behind-the-meter generation, DEV-ET may require the Interconnection Customer to install, own, operate, test, and maintain additional revenue metering at the output of the generation equipment, which is to meet any requirement specified in the applicable tariffs or interconnection agreements.  If Interconnection Customer owned metering is installed, the Interconnection Customer is to also provide DEV-ET with the generation revenue metering data if required.

When the end user has non-conforming load, a primary revenue meter along with SCADA data is required.  Non-conforming load is load of more than 50 MW that exhibits one of more of the following characteristics:

- Expected load swings of approximately 50 MW or more and ramp rates of approximately 10 MW or more per minute

- Loads with expected daily reactive power ramp rates of 50 MVAR or more per minute

- Loads that may create voltage flicker exceeding the limits set out in the Institute of Electrical and Electronics Engineers (IEEE) Standard 1453

- Loads that may create harmonic current distortions exceeding the limits set out in IEEE Standard 519

Telecommunications

In recognition that the coordination of the system operations by the Parties may be facilitated by the sharing of power flow and other real-time information from meters and other equipment at the Interconnection Points, the Parties may agree to cooperate on the installation and operation of data acquisition system (“DAS”) equipment including, but not limited to, remote terminal units (“RTU”), meters, MW/MVAR and Volt transducers, telecommunication devices, lease lines, and any related equipment at points which from time to time are to be mutually agreed upon.

If a backup telemetry system or data is required by one Party for their own use, the requesting Party is to be responsible for installing and/or maintaining the field devices and associated telecommunication system at their cost.

The following real-time operational data is to be provided to all Parties as available:  three phase bi-directional energy flows (e.g., MWh, MVARh), three phase instantaneous power flows (e.g. MW, MVAR), per phase RMS voltages, and per phase RMS currents with at least two decimal points resolution is to be provided.  In addition to the real-time operational data, the status of all switching devices associated with the interconnection circuit(s) are to be provided.  The real-time data requirements defined in the PJM manuals, including PJM Manual 01 – Control Center and Data Exchange Requirements and PJM Manual 03 – Transmission Operations, is to be provided to PJM to fulfill its roles as Reliability Coordinator (RC), Balancing Authority (BA), and Transmission Operator (TOP).

Metering, Data, and Communications requirements between a generation Facility and PJM are resolved in the kickoff meeting between the PJM client manager and the generation owner, as described in §4.2.2 of PJM Manual 14D – Generator Operational Requirements.

For generation Facilities that interconnect to DEV-ET via generator interconnection stations, serial telemetry data exchange is required between the two facilities.  The Data Exchange and Communications requirements between a generation Facility and the DEV-ET interconnection station are specified in attachment 5 of this document, Generator Interconnection Data Communication and Data Exchange Requirements.

Grounding and safety issues

All electrical equipment, electrical components, fences, metal buildings, protective controls, and structures are to be properly grounded and bonded.  A safe grounding design must accomplish two basic functions:

- Personnel safety:  Ensure that Facility personnel, their contractors and the public are not exposed to harmful step-and-touch potentials.

- Current path to earth:  Provide a path for electric currents into the earth under normal and fault conditions. Under normal conditions currents do not exceed any operating and equipment limits. Under fault conditions the currents do not adversely affect the continuity of service.

Accordingly, each electrical Facility must have a grounding system or grid that solidly grounds all metallic structures and equipment in accordance with standards outlined in the latest revisions of IEEE 80, IEEE Guide for Safety in AC Substation Grounding, and IEEE C2, National Electrical Safety Code (NESC).

Designs must ensure that step and touch potentials and transferred voltages are limited to safe levels. Furthermore, testing must be performed to verify the integrity of the installed grounding system and ensure safe step and touch potential parameters have been met in accordance with the latest revision of IEEE 80.

When various switching devices are opened on an energized circuit, its ground reference may be lost if all sources are not effectively grounded. This situation may cause over voltages that can affect personnel safety and damage equipment. This is especially true when one phase becomes short-circuited to ground. Therefore, the interconnected transmission power system is to be effectively grounded from all sources. This is defined as:

Xo/X1  3

Ro/X1 1

This relationship assumes R1/X1 = 0, which is a worst-case condition.

Interconnected generators should provide for effective system grounding of the high-side transmission equipment by means of a grounded high-voltage generation step-up transformer.

Shield wires should be considered, where applicable, to protect conductors and equipment from lightning strikes.  A recommendation for maximum resistance values for all new stand-alone (not connected to a ground grid) structures carrying shield wires are as follows:  25 Ohms for structures supporting Facilities at or below 230kV, and 20 Ohms for structures supporting Facilities from above 230kV to 500kV.

Safety is of utmost importance.  Any work carried out within a Facility is to be performed in accordance with all applicable laws, rules, and regulations and in compliance with Occupational Safety and Health Administration (OSHA), NESC, and Good Utility Practice. Automatic and manual disconnect devices are to be provided as a means of removing all sources of current to any particular element of the power system. Only trained operators are to perform switching functions within a Facility under the direction of the responsible dispatcher or designated person as outlined in the NESC.  The Interconnection Customer and DEV-ET must agree to switching and Lock Out/Tag Out procedures that are adhered to for the safety of all personnel.  DEV-ET follows its own standard operating practices and grounding procedures for safety of personnel.

Insulation and insulation coordination

Insulation coordination is defined by IEEE 62.82.1 as “The selection of insulation strength of equipment in relation to the voltages, which can appear on the system for which equipment is intended and taking into account the service environment and the characteristics of the available protective devices”. Insulation coordination must be designed properly both for personnel safety and to protect the electrical equipment from the harmful over-voltages resulting from faults, lightning or switching transients. An insulation design must accomplish two basic functions:

- Electrical isolation:  Electrically isolate the maximum anticipated voltage of energized parts from supporting structures or ground.

- Mechanical support:  Mechanically support energized parts as intended.

Surge arresters and static wires are used to safeguard the electric power equipment against harmful over-voltages.  Basic Impulse Levels (BIL) for electrical equipment and high voltage substation buses are to meet or exceed DEV-ET’s standard listed below.

| Nominal KV (phase to phase) | Basic Impulse Level (BIL) |
| --- | --- |
| 115 | 550 |
| 138 | 650 |
| 230 | 900 |
| 500 | 1550 |

Equipment BIL shielding and surge protection is to be designed as determined by lightning and switching surge analysis to meet all applicable ANSI/IEEE standards and DEV-ET and substation engineering standards.

DEV-ET Specifications for Transmission Line Insulators include:

- TE VEP 1115 – Porcelain and Glass Insulators

- TE VEP 1117 – Suspension Type Non Ceramic Insulators

- TE VEP 1118 – Non-Ceramic Post Type Insulators

ANSI/IEEE standards include, but are not limited to:

- ANSI C29 collection of standards – Insulators for Electric Power Lines

Interconnection Facilities to be constructed in areas with salt spray contamination or other types of contamination are to be properly designed to meet or exceed the performance of Facilities in a non-contaminated area. Typically, this involves more insulation, higher leakage distances and/or non-standard insulating components and materials.

The following is to be submitted, as applicable, with the Customer Request Form (Attachment 2 of this document) for evaluation as part of the interconnection plan:

- Surge arrester ratings

- Basic switching surge levels

- Surge arrester, conductor spacing and gap application

- Substation and transmission line insulation strength

- Protection and/or shielding schemes

- Overhead static wire location

- Equipment BIL ratings

- Insulator BIL ratings

Voltage, Reactive Power, and power factor control

Generation Facilities

PJM is responsible for ensuring the stability and reliability of its electric transmission system. In turn, all generation Interconnection Customers are responsible for operating their units in a stable manner while those units are connected to DEV-ET’s Facilities. Generator excitation and prime mover controls are key elements in ensuring electric system stability and reliability. To meet its responsibility, PJM must have the ability to establish voltage and governor control requirements for all generators connected to its system, including units connected through DEV-ET’s Facilities. These requirements may vary depending on the location, size, and type of generation installed.

Generator Interconnection Customers are required, with oversight by PJM, to follow the current NERC and SERC standards and guides for generator operation, protection, and control.

- All synchronous generators connected to the interconnected transmission systems are to be operated with their excitation system in automatic voltage control mode unless approved otherwise by PJM.  PJM and DEV-ET is to be notified any time a generator control system is removed from service, or its logic is modified.  These control systems may include but are not limited to: voltage regulators, power system stabilizers, governor and prime mover controls.

- Generators are to maintain a network voltage or reactive power output as required by DEV-ET, with governance by PJM, within the reactive capability of the units. Generator step-up and auxiliary transformer are to have their tap settings coordinated with electric system voltage requirements.

- All new inverter-based resources (IBRs), such as wind and solar, connecting to the DEV-ET system must have the capability to provide leading and lagging reactive power including, but not limited to, nighttime VAR support. Duration that the generating Facility can operate in a VAR supporting mode is to not be limited by any other Facility component. Prior to Facility commissioning for IBRs, any logic associated with VAR capability must be enabled and turned on such that an operator can readily control the AVR voltage setpoint via the DEV-ET SCADA system. During commissioning, daytime and nighttime VAR testing, in addition to AVR test results, must be completed and documented. This testing must also include transitions from day-to-night and night-to-day, and charging/discharging/idle mode for battery storages. Both daytime and nighttime VAR and AVR testing results must be submitted to the DEV-ET System Operations Center. The requirements for the DEV-ET SCADA voltage setpoint control function are further detailed in attachment 5 to this document - Generator Interconnection Data Communication and Data Exchange Requirements. Control Narrative, explicit point definitions, and data communications requirements for this function are thoroughly established in attachment 5.

- Temporary excursions in voltage, frequency, and real and reactive power output that a generator is to be able to sustain is to be defined and coordinated on a regional basis.

- Voltage regulator controls and limit functions (such as over and under excitation and volts/hertz limiters) are to coordinate with the generator’s short duration capabilities and protective relays.

- Prime mover controls (governors) are to operate with appropriate speed/load characteristics to regulate frequency.

All interconnected generation must adhere to power factor requirements for new generator interconnection requests and increase to existing generators as documented in PJM Manual 14G – Generation Interconnection Requests, Section 4: Generator Interconnection Requirements, Rights and Obligations.  Asynchronous generators connected to the transmission systems are to be studied in the PJM System Impact Study to determine the reactive power compensation required.  All interconnected generation must meet the following criteria:

- All synchronous and asynchronous generators connected to the interconnected transmission systems are to maintain a power factor of at least 0.95 leading to 0.95 lagging measured at the Point of Interconnection.

- All new intermittent, asynchronous generators interconnecting to the transmission system that cannot provide control of real power output (wind, solar) are studied for reactive power capabilities in a manner that considers the variability of the entire intermittent generation fleet within the DEV-ET footprint; DEV-ET provides input and support these studies if deemed necessary, following these requirements.

- Voltages at the Point of Interconnection of any generating station should not vary more than 1.0% for expected changes in generation output caused by fluctuations in the prime mover output.

- The System Impact Study for asynchronous, intermittent generation considers the generator under study as well as variability of the entire intermittent generation fleet when determining if the voltage fluctuation criteria is met.

- New variable generation resources that cannot meet the 1% voltage deviation criteria provide dynamic reactive compensation as specified in the PJM System Impact Study, with DEV-ET support and studies incorporated.

Specific requirements for voltage regulators, power system stabilizers, governor controls, and remote control and telemetry of such devices are determined during the System Impact Study. These specific requirements for a generator will be part of the Interconnection Service Agreement. (PJM Manual 14A, Section 5: Summary of Agreements).

Transmission Facilities

The Transmission System must be capable of moving electric power from areas of generation to areas of load under a wide variety of expected system conditions. Adequate reactive power supplies are of paramount importance to the capability of the Transmission System to reliably support a wide variety of transfers. Transmission Facilities must be designed to minimize excessively high voltages during light transmission loading conditions yet have adequate reactive supplies to support system voltage during heavy transmission loading conditions.

End-User Facilities

The voltage variation limitations for interconnections with End-User Facilities are as stated in the applicable tariff or agreement. End-User Facilities connected directly to the Transmission System should plan and design their systems to operate at close to unity power factor to minimize the reactive power burden on the Transmission System.

Power quality impacts

Flicker Requirements

Flicker is assessed at the Point of Common Coupling (PCC) using an instrument in compliance with International Electro Technical (IEC) 6100-4-15.

The flicker measured at the PCC is to be 0.8 or less for the short-term flicker (Pst) and 0.6 or less for the long-term Flicker (Plt).  The Pst and Plt values measured are not to exceed more than 1% of the time based on a probability distribution calculated for a one-week period.

Harmonic and Inter-Harmonic Requirements

Harmonic levels are assessed at the PCC with an instrument that can take individual samples of voltage and current waveforms and determine the probability distribution of the individual harmonic levels for both the current and the voltage. Harmonic distortion levels at the PCC should meet the requirements contained in the latest revision of IEEE Standard 519.

In addition, the individual inter-harmonic currents are to be limited to 25% of the values in IEEE Standard 519 and the THD (Total Harmonic Distortion) and TDD (Total Demand Distortion) calculation is to include the inter-harmonic components.  The Inter-harmonics are to be calculated in 10 Hz increments.  The current distortion levels specified in IEEE Standard 519 is to not exceed more than 5% of the time based on a probability distribution calculated for a one-week period.

Equipment Ratings

Electrical equipment and associated interconnected Facilities are to be capable of safely interrupting the worst-case short circuit faults calculated for the protection zone.

All current-carrying equipment and devices are to be designed to carry the maximum loads that are predicted and used in load flow analysis, tested against all applicable NERC standards, PJM Transmission Planning Criteria and DEV-ET Planning Criteria. Loads exceeding nameplate or normal design capacities are acceptable only when allowed by manufacturers’ design documentation or standard industry practice or by DEV-ET’s Facility Rating Methodology (FRM).

Circuit breakers and disconnect switches are to be designed and tested according to the latest IEEE C37 collection of standards. Power transformer and Instrument transformers are to be designed and tested according of IEEE C57 standards.  Rigid bus structures are to be designed to meet the latest revision to IEEE 605. Current carrying conductors and tubing are to be braced and supported for the expected worst case, short circuit currents, ice loading and wind loading.  For overhead line Facilities, ground clearance is to be maintained according to the latest IEEE C2, National Electrical Safety Code (NESC).  All Facilities at voltages greater than 230kV should be considered Extra High Voltage (EHV) and designed accordingly.

Equipment BILs, shielding, and surge protective device application must meet requirements as determined by the latest IEEE C62 standards. DEV-ET provides the BIL for the system in the interconnection area. Also, equipment must meet all applicable ANSI/IEEE standards and specifications communicated by PJM and DEV-ET.  Basic Impulse Levels (BIL) for electrical equipment and high voltage substation buses are to meet or exceed DEV-ET’s standard listed below.

| Nominal KV (phase to phase) | Basic Impulse Level (BIL) |
| --- | --- |
| 115 | 550 |
| 138 | 650 |
| 230 | 900 |
| 500 | 1550 |

Synchronizing of Facilities

Synchronizing equipment consisting of potential devices and associated protective relay and controls is required on Facilities where energy can be sourced on both sides of an interconnection circuit breaker.  The Interconnection Customer is to not synchronize with the Transmission System prior to obtaining approval from DEV-ET.

The following explains the various synchronizing options.

Generation Facilities

Live line, dead bus (LLDB) control is used in the interconnection circuit breaker reclosing scheme when generation Facilities are connected to DEV-ET. The circuit breaker cannot be closed unless the generation side has zero voltage. The interconnection circuit breaker should not be used to synchronize a generator to the Transmission System. Instead, the generation Facilities should have their own synchronizing Facilities. In the event a generation Interconnection Customer’s Facility becomes disconnected from DEV-ET’s system, it is to remain disconnected until system voltage and frequency are within an established range.  In all scenarios, DEV-ET is to retain operational control of the interconnection breaker.

Interconnected and Separate Systems for Generators

The Interconnection Customer may elect to run its generator in parallel (interconnected) with DEV-ET or as a separate system with the capability of nonparallel load transfer between the two independent systems. The two methods of operation are outlined as follows:

Parallel system

A parallel system is one in which the Interconnection Customer’s generation equipment can be connected to DEV-ET’s system resulting in a transfer of power between the two systems. A consequence of such parallel operation is that the parallel generator becomes an electrical part of the DEV-ET system, which must be considered in the operation and protection of DEV-ET’s Facilities. The general and specific requirements for parallel generation installations are discussed in this document.

Synchronizing equipment consisting of potential transformers and associated protective relaying/controls is required on Facilities where energy can be sourced on both sides of an interconnection circuit breaker. This equipment serves the following purposes:

- Verifies the voltages on both sides of a circuit breaker fall within set tolerances, which must meet DEV-ET’s approval, as to the magnitude and phase angle established by system conditions

- Supervises the closing and automatic reclosing of the circuit breaker

- Prevents the closing of the circuit breaker when the two systems are out of sync

Voltage magnitudes, phase angles, and frequency constraints are to be determined on a case-by-case basis.

Separate system with nonparallel load transfer capability

A separate system is one in which there is no possibility of delivering energy to the DEV-ET system from the Interconnection Customer’s equipment. The Interconnection Customer may maintain the capability of transferring load between the two systems, but such transfer must be accomplished in an open-transition or nonparallel mode. This can be accomplished by either an electrically or mechanically interlocked switching arrangement that precludes both the switch connecting the load to DEV-ET’s system and the switch connecting the load to the Interconnection Customer’s generation being in the closed position simultaneously. If the Interconnection Customer has a separate system, the Interconnection Customer is to not operate the generation until DEV-ET has verified that the transfer scheme meets the nonparallel requirements.  This verification is accomplished by review and approval of drawings and equipment specifications by DEV-ET and, if DEV-ET so elects, by field inspection of the transfer scheme. DEV-ET is not responsible for approving the Interconnection Customer’s generation equipment and assumes no responsibility for its design or operation.

Maintenance coordination

Testing

DEV-ET requires interconnecting entities with protection systems which coordinate with DEV-ET network protection systems to have a documented maintenance program for those systems in accordance with NERC Standard PRC-005 requirements. Documentation of the maintenance program is to be supplied to DEV-ET upon request. Additionally, the interconnecting entity, on maintenance intervals identified within their documented program and following any apparent malfunction of the protection equipment, is to perform and document both calibration and functional trip tests of its protection equipment as outlined within its maintenance program. Customer is to maintain evidence of such activities and make them available to DEV-ET upon request.

Coordination

DEV-ET may remove its lines and associated equipment from service for testing of relays and maintenance of lines or substations in accordance with its maintenance program.  The Interconnection Customer, DEV-ET and PJM coordinate for these planned outages.

The interconnection parties agree to confer regularly to coordinate the planning, scheduling, and performance of preventative and corrective maintenance on the Interconnection Customer’s Facility, the Interconnection Facilities and associated Facilities owned by DEV-ET. The Interconnection Customer must coordinate its approach and schedule for maintenance and testing with DEV-ET to ensure the reliability of the bulk electric system.

Generator Interconnection

On occasion, the generation Interconnection Customer may not be allowed to operate in parallel with the DEV-ET or distribution system.  A generator Interconnection Customer with multiple interconnection points may be permitted to operate only in parallel with specific lines so DEV-ET can perform “live line maintenance” on the Facilities serving the generator Interconnection Customer. The generator Interconnection Customer, DEV-ET and, as needed, PJM, coordinate with these conditions and requests.

Operational issues (abnormal frequency and voltages)

PJM is the Transmission Operator for DEV-ET System. The interconnection is operated consistent with PJM requirements and procedures. Specific transmission conditions and procedures for operation of Transmission Facilities (defined by PJM) within PJM are found in PJM Manual 03 – Transmission Operations on the PJM website (www.pjm.com).

Load-shed program as required by PJM

The transmission system is designed to automatically activate a load-shed program as required by PJM in the event of an under-frequency system disturbance. A generation Interconnection Customer is to implement under-frequency and over-frequency relay set points for the generation Interconnection Customer as required by PJM to ensure ‘ride through’ capability of the transmission system. The generation Interconnection Customer Facility is to stay connected to and synchronized with the Transmission System during system disturbances within a range of under-frequency and over-frequency conditions, in accordance with Good Utility Practice. For more information on ride through requirements of inverter-based generation, see Attachment 4 of this document. In addition, additional information is found in PJM Manual 14D – Generator Operational Requirements. The response of a generation Interconnection Customer’s Facility to frequency deviations of predetermined magnitudes; both under-frequency and over-frequency deviations are studied and coordinated with PJM in accordance with Good Utility Practice. Additional information is found in PJM Manual 14D – Generator Operational Requirements. Inspection requirements for new or materially modified existing interconnections.

DEV-ET has established inspections as a component of its maintenance program for DEV-ET’s owned assets.  DEV-ET may require right of access to the Interconnection Customer’s Facility for purposes of conducting inspections: to include observing tests, visual inspections, and auditing maintenance and testing records.

Additionally, DEV-ET may require right of access to conduct initial (pre-operational) inspection and/or require copies of pre-operational procedures and test reports.

Each party is to, at its own expense, have the right to observe the testing of any of the other party’s metering equipment whose performance may reasonably be expected to affect the accuracy of the observing party’s telemetry and revenue. If requested, each party is to notify the other in advance of metering or other equipment testing and maintenance and may have a representative attend and be present during such testing.

If DEV-ET identifies any deficiencies, defects, or inconsistencies of the Interconnection Customer’s Facility that may adversely affect the reliability of the bulk power system and/or potentially constitute a compliance concern for DEV-ET, then DEV-ET is to provide notice to the Interconnection Customer outlining the concern and the suggested corrective action.  Customer is to provide DEV-ET with a corrective action plan resolving identified concern(s).

If Interconnection Customer observes any deficiencies, defects, or inconsistencies of its Interconnection Facility that may adversely affect the reliability of the bulk power system and/or potentially constitute a compliance concern for DEV-ET, then the Customer is to provide notice to DEV-ET outlining the identified concern and the corrective actions that are taken to resolve the concern.

Communications and procedures during normal and emergency operating conditions.

Complete, precise, and timely communication is an essential element for maintaining reliability and security of a power system. Under normal operating conditions, the major link of communication with various interconnects is to be by telephone lines.  DEV-ET and the Interconnection Customer is to maintain communications which are to include, but not be limited to exchanging up-to-date information regarding:

- Contact information for maintenance personnel

- Maintenance schedules

- Meter tests

- Relay tests

- System paralleling or separation

- Scheduled or unscheduled shutdowns

- Equipment clearances

- Periodic load reports

- Tagging of interconnection interrupting devices

- Billing

- Other routine communication

In case of emergency or abnormal operating conditions, various communication channels may be used depending on the interconnect category. Emergency telephone numbers should be agreed upon by both parties prior to the date of initial interconnection. Each interconnection party is to notify the other parties promptly when it becomes aware of an emergency condition that may reasonably be expected to affect operation of the Interconnection Customer’s Facility, the Interconnection Facilities, the DEV-ET Interconnection Facilities, or the Transmission System.

Generation and Transmission Interconnection Customer Obligations

Generation and transmission Interconnection Customers are to install and maintain satisfactory operating communications with PJM's system dispatcher or its other designated representative and with DEV-ET system dispatcher. Generation and transmission Interconnection Customers are to provide standard voice line, dedicated voice line, and facsimile communications at their Facility control room through use of the public telephone system. Generation and transmission Interconnection Customers also are to provide and maintain backup communication links as specified by both PJM and DEV-ET for use during abnormal conditions. Satellite phones compatible with PJM and DEV-ET equipment should be available for emergency communications. Generation and transmission Interconnection Customers further are to provide the dedicated data circuit(s) necessary to provide Interconnection Customer data to PJM and DEV-ET as necessary to conform to applicable technical requirements and standards.

Transmission Line Connections – Generation

Transmission Facilities may be used for providing service to generation developers when the use of distribution feeders is not practicable.  Generally, the use of transmission Facilities should be considered for the following conditions:

- All generating Facilities over 20 MW

- Locations remote from distribution Facilities

- Remote locations where distribution Facilities are not adequate

For interconnection to the 500kV network, the preferred minimum generation capability at a single point of connection is 500MW.  The interconnection of generating plants on the 500kV network below this level are permitted for cases where no other lower transmission voltage option is available.

The descriptions and diagrams in this section are typical from an interconnection standpoint; they are subject to further modification as necessary to comply with Attachment 3 of this document, Section 3 - Interconnection Protection Requirements.

Single circuit interconnections to a transmission line

A transmission line tap, as shown in Diagram 6.1, can generally be used to interconnect a proposed new generating Facility of any size located within one mile, or a generating Facility of 500 MW or less located at a distance greater than one mile to the Transmission System. With this arrangement, loss of generation does not interrupt flow on the Transmission System and loss of a transmission line does not result in loss of generation. However, final System Protection requirements along with interconnection substation requirements are to be based on the reliability impact conducted through the PJM Interconnection Queue process as defined in PJM Manual 14C – Generation and Transmission Interconnection Facility Construction.  The customer should reserve property for construction of the DEV-ET -owned interconnection station.

Diagram 4.2.1:  Line Tap – Generation adjacent to transmission line

Notes:

Specific violation of the criteria outlined in Section C of Attachment 1 of this document may require a four-breaker ring bus.

See Section 4.2.5 for additional acceptable breaker configurations.

Transmission interconnections located remote from a transmission line

If the proposed Generating Facility is greater than 500 MW and located more than one mile from an existing transmission line, then the proposed arrangement shown in Diagram 6.2.A or 6.2.B could be used.  With this arrangement, loss of generation does not interrupt flow on the Transmission System and loss of a transmission line does not result in loss of generation.  However, final System Protection requirements along with interconnection substation requirements are to be based on the reliability impact conducted through the PJM Interconnection Queue process as defined in PJM Manual 14C – Generation and Transmission Interconnection Facility Construction.

Diagram 4.2.2.A:  Line Tap – Large generation located remote from transmission line

As an alternative to constructing a switching station at the tap point, the transmission line can be cut and looped in and out to a switching station located adjacent to the generating station as shown in Diagram 6.2.B. This arrangement can have its advantages since acquiring land and permitting a new station at the tap point would not be required. The customer should reserve property for construction of the DEV-ET owned interconnection station.

Diagram 4.2.2.B:  Looped Tap – Large generation located remote from transmission line

Notes:

Specific violation of the criteria outlined in Section C of Attachment 1 of this document may require a four-breaker ring bus.

See Section 4.2.5 for acceptable arrangements for interconnection breaker.

Interconnection to Radial Transmission Line or Radial Transmission Tap

Connection to radial transmission lines

A proposed generating Facility may be connected to a radial transmission line.  A radial transmission line is defined as a single line that has one transmission source and does NOT tie to any other transmission network source (line or substation).

Diagram 4.2.3.1 – Connection to radial transmission line

Interconnection to radial transmission tap

A proposed generating Facility may be connected to a transmission tap line portion of a network transmission line, as shown in diagrams 6.3.2.A and 6.3.2.B, subject to Attachment 3 of this document, Section 3 Interconnection Protection Requirements.

Diagram 4.2.3.2.A – Connection to radial transmission tap line (single point)

Diagram 4.2.3.2.B – Connection to radial transmission tap line (ring bus)

Substation interconnection requirements

All generation interconnection substation designs include all switches and devices required to permit maintenance of all breakers and transmission lines without the loss of the ability to use the generation capacity when required.  Small units can be bussed together behind breakers unless reliability studies indicate issues.

Transmission interconnection breakers

If new transmission lines are required by the addition of generator capacity at a new or existing power station, the breaker arrangement at the existing substation determines both the number of breakers and the breaker arrangement required for the interconnection.  Line terminations that result in a four breaker or less ring bus are acceptable.  If more than a four-breaker ring bus is required, a breaker and a half arrangement would be used for reliability considerations.

Generation interconnection breakers

A customer owned interconnection breaker is required if the generating station is located remote from the interconnection station (See Diagrams 6.2.A and 6.2.B).  Small generating units totaling 500 MW or less, or all units of a combined-cycle set can be bused together behind this breaker as shown in Diagram 6.6.A or multiple breakers can be used as in Diagram 6.6.B.

Diagrams 4.2.6.A and 4.2.6.B – Multiple breakers

Diagram 6.6.A.		  			Diagram 6.6.B.

However, regardless of distance, final System Protection requirements along with interconnection substation requirements are to be based on the reliability impact conducted through the PJM Interconnection Queue process as defined in PJM Manual 14C – Generation and Transmission Interconnection Facility Construction.    Interconnection Requirements for Distribution Connected Generation

The Distribution Connected Generation is defined as a generator who is requesting connection to distribution Facilities serving retail customers (excluding the station service load for the respective generator).

Distribution connected generation resources where the aggregate nameplate rating of all the generating resources (dispersed generation resources) is greater than 100 MVA, require a three breaker ring at the point of connection to the transmission system.

Diagram 4.2.6.C Distributed Generation greater than 100MVA

Distribution connected generation resources where the aggregate nameplate rating of all the generating resources (dispersed generation resources) is less than 100MVA can be connected behind a single interrupting device (circuit breaker or circuit switcher).

Diagram 4.2.6.D Distributed Generation less than 100MVA

Load Criteria – End User

Transmission Facilities may be used for providing service to commercial, industrial, municipal, cooperative and cogeneration customers when the use of distribution feeders is not practicable.  Generally, the use of transmission Facilities should be considered for the following conditions:

- All loads over 20 MW

- Locations remote from distribution Facilities

- Remote locations where distribution Facilities are not adequate

- Loads with nonstandard voltage requirements

- Loads having large surge requirements

The following are minimum load levels within the ten year planning horizon for the direct interconnection of loads to existing transmission lines:

- 500 kV – Reserved for bulk power transfers

- 230 kV – 30 MW

- 138 kV – 20 MW

- 115 kV – 20 MW

The interconnection of loads below these levels are permitted after a thorough planning analysis concludes that the cost and reliability of distribution alternatives are clearly inferior to the overall cost and reliability of a transmission interconnection which includes, without limitation, considerations of any transmission reliability or operational concerns that may arise from adding the transmission interconnection. For consideration of an interconnection of loads below the specified levels, the requesting party is to prepare documentation explaining and supporting why distribution alternatives are inferior and must supply additional documentation which may require DEV-ET to undertake its own analysis.

The feasibility of serving customers direct from the transmission along with determining the final recommended transmission interconnection Facilities requires a comprehensive study and coordination.  Factors to be considered prior to agreeing on a customer connection are as follows:

- Economics of distribution versus transmission alternates

- Customer parallel generation

- Transmission line tap or loop length

- Economics of radial line versus looping even when typical thresholds (e.g., length, load level) are not met

- Mitigation of economic risk in the event actual load varies materially from planned load

- Customer transformer characteristics

- Customer switching

- Effect on protective relaying at remote terminals

- Problems of large through power on looped lines

- Extent of customer Facilities

In general, a tap line in excess of one mile are to require a terminal station.  If the tap line is long enough to require a terminal substation, a three-breaker or four -breaker ring bus may be required. With these arrangements, loss of line to the customer does not interrupt flow on the Transmission System and loss of a transmission line does not result in loss of service to the customer. The total projected load and MW-Mile exposure are also factors to be taken into consideration. The final number of breakers and breaker arrangement is however based on the specific interconnection request and reliability impact on Transmission System.

The following typical diagrams indicate the Facilities arrangement for normal service 100 kV and above.

Tapping line for loads below 100 MW

Diagram 4.3.A:  Tap line for less than 100MW, less than 1 mile

A transmission line tap, as shown in Diagram 4.3.A, can generally be used to interconnect a proposed customer Facility located within one mile or less to the nearest transmission line. With this arrangement, the company installs necessary system protection equipment and associated components at the customer’s Facility. The final System Protection and interconnection substation requirements communicated to the customer are to be based on the site-specific detailed reliability impact as determined by DEV-ET.  See Section 4.4 for additional options.

Diagram 4.3.B:  Tap line for less than 100MW, more than 1 mile, less than 700 MW-Mile

A transmission line tap, as shown in Diagram 4.3.B, can generally be used to interconnect a proposed customer Facility located more than one mile from to the nearest transmission line. A three-breaker or four-breaker ring bus may be required. With this arrangement, the company installs all necessary equipment at the interconnection substation at or near the transmission line.  The final System Protection and interconnection substation requirements communicated to the customer are to be based on the site-specific detailed reliability impact as determined by DEV-ET.

Diagram 4.3.C:  Tap line less than 100MW, more than 1 mile, two feeds

A transmission line tap, as shown in Diagram 4.3.C, can generally be used to interconnect a proposed customer Facility of less than 100 MW and when it is more economical to build double circuit rather than a single line. The customer may reserve property for the DEV-ET owned interconnection station if one is required.

The addition of breaker “C” may be required in order to limit the number of direct-connect loads (tapped Facilities) to four, or as otherwise required based on detailed System Protection and interconnection substation assessments.

- 4.3.2	Tapping lines for loads 100 MW and greater

The addition of customer load in excess of 100 MW should be connected to the Company’s Transmission System as shown below in Diagrams 4.3.D and 4.3.E. If available 230kV is the preferred voltage level to connect loads greater than 100MW.

Diagram 4.3.D:  Tapping line 100 MW load and greater, less than a mile

A 4-breaker ring bus arrangement as shown in Diagram 4.3.D can generally be used to interconnect a proposed customer Facility of 100 MW and greater having two customer transformers, or to address a specific violation of the NERC standard outlined in Section C of Attachment 1 of this document.  For cases in which there is only one customer transformer, a 3-breaker ring bus may be acceptable.  With either arrangement, loss of line to the customer does not interrupt flow on the Transmission System and loss of a transmission line does not result in loss of service to the customer. However, the final System Protection and interconnection substation requirements communicated to the customer are to be based on the site-specific detailed reliability impact as determined by DEV-ET.  The customer could reserve property for construction of the DEV-ET-owned interconnection station if customer parcel is adjacent to or in very close proximity of transmission right of way.

Diagram 4.3.E:  Tapping line 100 MW load and greater, more than a mile

As an alternative to constructing a switching station at the tap point, the transmission line can be cut and looped in and out to a switching station located adjacent to the customer station as shown in Diagram 4.3.E.  This arrangement can have its advantages since acquiring land and permitting a new station at the tap point would not be required. The customer should reserve property for construction of the DEV-ET owned interconnection station.

A 4-breaker ring bus arrangement as shown in Diagram 4.3.E can generally be used to interconnect a proposed customer Facility of 100 MW and greater having two customer transformers, or to address a specific violation of the NERC standard outlined in Section C of Attachment 1 of this document.  For cases in which there is only one customer transformer, a 3-breaker ring bus may be acceptable.  With either arrangement, loss of line to the customer does not interrupt flow on the Transmission System and loss of a transmission line does not result in loss of service to the customer.

Prohibited arrangements and allowable alternatives

DEV-ET does not allow by-pass switches around primary interrupting devices on the customer’s distribution transformer at the point of interconnection as shown in Diagram 4.4.A.  DEV-ET’s current system protection principles require that each system element, (line, transformer, bus, etc.) have primary relay protection in service at all times when the element is energized and placed in service. This ensures that all elements have adequate protection for safe and reliable operation of the Transmission System and are ready to remove the element from service should a fault occur. This is even more critical in cases like distribution tapped transformers where upstream line protection cannot provide backup coverage.  The use of an air-break bypass switch would expose customer’s personnel and equipment in an unprotected zone. This places risk to the Bulk Electric Systems integrity as well as impacting all other customers served by the same transmission line.

Diagram 4.4.A:  Prohibited by-pass switch

Allowable Sample Alternatives:  A parallel circuit switcher arrangement as shown in Diagram 4.4.B provides a fully redundant capability.  Another approach is the fused bypass as depicted in Diagram 4.4.C.  The exact design, system protection configuration and operating arrangement may be customized as necessary, subject to review and approval by both DEV-ET and the Customer.

Diagram 4.4.B:  Allowable sample alternative with interrupting devices

Diagram 4.4.C.: Allowable sample alternative with fused bypass

Tapping Company’s bus

The requirements for direct interconnection to company’s transmission bus is determined on case by case basis.

Generally, the following are preferred minimum load levels within the ten year planning horizon for the direct interconnection of loads to the existing substation busses:

230 kV – 75 MW

138 kV – 50 MW

115 kV – 50 MW

In those cases where it may be practicable to tap an existing transmission substation bus to serve a customer, Diagram 4.5 indicates the typical Facilities arrangement for normal service:

Diagram 4.5:  Tapping existing substation bus below 100 MW load

Definitions & Abbreviations

Definitions

Wherever used in this document with initial capitalization, the following terms are to have the meanings as specified below. Terms used in this document with initial capitalization not defined are to have the meanings specified in the PJM Open Access Transmission Tariff.

Capacity—The seasonal maximum generating capability of the generation Interconnection Customer’s Facility, measured in megawatts.

Distribution Facilities—The Facilities rated at less than 69 kV which are owned and operated by the Company, and which are necessary to connect the Interconnection Customer’s Facility to the Transmission System.

Emergency Condition(s)—A condition or situation (i) that in the judgment of either party is imminently likely to endanger life or property; (ii) that in the sole judgment of The Company is imminently likely to affect adversely or impair the Transmission System or imminently will affect or impair the transmission systems of others to which the Transmission System is directly or indirectly connected; or (iii) that in the sole judgment of the generation Interconnection Customer is imminently likely to adversely affect or impair the Facility.  Such a condition or situation includes, but is not limited to, overloading, or potential overloading of, excessive voltage drop, or other unusual operating conditions on the Transmission System or the generation Interconnection Customer’s Facility such that the output of the Facility must be shut down or curtailed to avoid damaging the Facility or the Transmission System.

Good Utility Practice— Any of the practices, methods, and acts engaged in or approved by a significant portion of the electric utility industry during the relevant time period, or any of the practices, methods and acts that, in the exercise of reasonable judgment in light of the facts known at the time the decision is made, could have been expected to accomplish the desired result at a reasonable cost consistent with good business practices, reliability, safety and expedition. Good Utility Practice is not intended to be limited to the optimum practice, method, or act to the exclusion of all others, but rather is intended to include acceptable practices, methods, or acts generally accepted in the region.

Governmental Authority—Any federal, state, local or other governmental, regulatory or administrative agency, court, commission, department, board, or other governmental subdivision, legislature, rulemaking board, tribunal, arbitrating body, or other governmental authority.

Interconnection Facilities—All structures, equipment, devices and apparatus owned or leased by, or under contract to each party presently in place or proposed to be installed, which are necessary to connect the Interconnection Customer’s Facility(ies) to the DEV Transmission System.

Interconnection Customer—A transmission, generation, or end user connected to, or seeking to connect to, the DEV Transmission System.

Interconnection Point—The point at which the Facilities are physically connected to the Transmission System (including any Distribution Facilities required to facilitate the interconnection).

Metering Equipment—All metering equipment currently installed at the Interconnection Customer’s Facility and/or any other metering equipment to be installed at the metering points designated in the Interconnection Facilities, including Revenue Meters.

RTO—A Regional Transmission Organization or any successor thereof which becomes responsible for operating the Company Transmission System to which the Interconnection Customer’s Facility is connected.  PJM Interconnection, L.L.C. is DEV’s RTO.

Transmission Element — Transmission elements are primary equipment (69kV and above) that constitutes, or interconnects with, the DEV Electric Transmission System. Examples include buses, lines, or transformers with lowside voltage 69kV or above, regardless of Bulk Electric System status.

Transmission System—The Facilities owned by DEV that are used to provide transmission service, including any Distribution Facilities required to provide Wholesale Distribution Service, under the PJM Open Access Transmission Tariff (OATT).

Wholesale Distribution Service—The provision of distribution service to wholesale customers, including generator Facilities, over Distribution Facilities as necessary to effectuate transmission service under the PJM OATT or Interconnection Service under this Agreement.

Abbreviations

ANSI—American National Standards Institute

IEEE—Institute of Electrical and Electronic Engineers

NERC—North American Electric Reliability Corporation

OATT—PJM Open Access Transmission Tariff

PCC—Point of Common Coupling

SERC— Southeastern Electric Reliability Council

Revision History

| Revision Date | Revision # | Description | Revised By | Effective Date |
| --- | --- | --- | --- | --- |
| 08/24/1999 | 0.0 | Original document created to meet the requirements of NERC Planning Standard I.C.S1.M1. | ET Planning staff | 08/24/1999 |
| 05/01/2001 | 1.0 | See Details for Revision 1.0 below | ET Planning staff | 05/01/2001 |
| 09/07/2005 | 2.0 | See Details for Revision 2.0 below | ET Planning staff | 09/07/2005 |
| 05/29/2007 | 3.0 | See Details for Revision 3.0 below | ET Planning staff | 05/29/2007 |
| 12/22/2009 | 4.0 | See Details for Revision 4.0 below | ET Planning staff | 12/22/2009 |
| 12/22/2011 | 5.0 | See Details for Revision 5.0 below | William F. Bigdely | 12/22/2011 |
| 10/10/2012 | 6.0 | See Details for Revision 6.0 below | William F. Bigdely | 10/10/2012 |
| 11/22/2013 | 7.0 | See Details for Revision 7.0 below | William F. Bigdely | 11/25/2013 |
| 03/31/2014 | 8.0 | See Details for Revision 8.0 below | William F. Bigdely | 03/31/2014 |
| 07/16/2014 | 9.0 | See Details for Revision 9.0 below | William F. Bigdely | 07/18/2014 |
| 01/09/2015 | 10.0 | See Details for Revision 10.0 below | William F. Bigdely | 01/15/2015 |
| 03/26/2015 | 11.0 | See Details for Revision 11.0 below | William F. Bigdely | 03/27/2015 |
| 12/15/2015 | 12.0 | See Details for Revision 12.0 below | William F. Bigdely | 01/01/2016 |
| 05/15/2017 | 13.0 | See Details for Revision 13.0 below | William F. Bigdely | 06/01/2017 |
| 03/29/2018 | 14.0 | See Details for Revision 14.0 below | William F. Bigdely | 04/01/2018 |
| 12/13/2018 | 15.0 | See Details for Revision 15.0 below | William F. Bigdely | 01/01/2019 |
| 03/11/2019 | 16.0 | See Details for Revision 16.0 below | William F. Bigdely | 03/15/2019 |
| 03/11/2020 | 17.0 | See Details for Revision 17.0 below | David Witt | 04/01/2020 |
| 06/30/2020 | 18.0 | See Details for Revision 18.0 below | David Witt | 07/08/2020 |
| 02/22/2021 | 19.0 | See Details for Revision 19.0 below | Hamidreza Sadeghian | 04/01/2021 |
| 03/10/2022 | 20.0 | See Details for Revision 20.0 below | Mark Gill | 04/01/2022 |
| 02/16/2023 | 21.0 | See Details for Revision 21.0 below | Amirreza Sahami | 04/01/2023 |

Details for Revision 1.0

- Revised to include information regarding Dominion’s generation interconnection procedures/process.

Details for Revision 2.0

- Revised to reflect transition from old NERC Planning Standards to NERC Reliability Standards, including changing the naming convention of all referenced standards throughout the document.

Details for Revision 3.0

Revised to reflect the following:

- Updates to NERC Reliability Standards

- Dominion’s PJM Membership

- References to new SERC regional studies processes

Details for Revision 4.0

Revised to reflect the following:

- PJM Generation Queue Changes Section 4

- General Revisions all sections

Details for Revision 5.0

Revised the following:

- Section 2.12: Clarified content regarding synchronizing of Facilities.

- Exhibit A: Changed loading criteria to not exceed emergency rating of transmission Facility.

- Various errata changes.

Details for Revision 6.0

- Comprehensive overhaul to better align with the numerical flow of NERC Reliability Standard FAC-001.

Details for Revision 7.0

Revised to reflect the following:

- Annual review of Facility Connection Requirement document.

- Updated titles for approval process on page 1.

- Incorporated changes to reflect FERC approval of FAC-001-1 effective 11/25/2013.

- Section 3.1.5 – Removed “Coordination and Compatibility” and “Performance Tracking and Compliance”; Added “Protection System Misoperations”.

- Section 3.1.13 – Added “Testing” paragraph

- Various errata changes.

Details for Revision 8.0

Revised Exhibit A – Transmission Planning Criteria R8 as listed below:

- Expanded description for Section G.1. TAPPING LINE BELOW 100 MW LOAD to emphasize the requirement of a fused bypass arrangement.

- Recreated diagrams throughout for consistency of style.

Details for Revision 9.0

Revised Exhibit A – Transmission Planning Criteria as listed below:

- Added Section C.2.8 – End of life criteria

- Reformatted headers to improve PDF navigation via bookmarks

Details for Revision 10.0

Revised Facility Connection Requirement document to reflect the following:

- Minor clarifications and annual review.

- Section 1 Purpose and Introduction: Added statement regarding applicability of document.

- Section 3.1.9 Voltage, Reactive Power, and power factor control; Generation Facilities subsection:

- Revised first bullet regarding generator control systems.

- Added new series of bullets regarding interconnected generation criteria.

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

Details for Revision 11.0

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

Details for Revision 12.0

- Made revisions to align with new version of the standard, FAC-001-2.

- Updated signature page to reflect personnel change.

- Relocated Section 3 content formerly associated with R3 in the prior version (FAC-001-1) to Section 3.3 Additional items per FAC-001 Application Guidelines and Technical Basis.

- Section 3.1 added bullet regarding distributed generation output for both conventional and alternative (solar, wind, etc.) sources

- Added sections 3.3.1 and 3.3.2 due to new information contained within Application Guidelines and Technical Basis of FAC-001-2.

- 3.3.5. Refined discussion of Protection System Design

- 3.3.6. Added reference to PJM Manual 01 – Control Center and Data Exchange Requirements

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

- Integrated prior content from Transmission Planning Criteria, refined drawings and associated discussions:

  - Section 5. TRANSMISSION LINE CONNECTIONS – GENERATION (previously Section F of Transmission Planning Criteria).  Established minimum generation MW level for interconnection to the Transmission System.

  - Section 6. LOAD CRITERIA – END USER (previously Section G of Transmission Planning Criteria)

- Added Exhibit C DVP Electric Transmission Generator Interconnection Protection Requirements.

- Altered capitalization throughout the document to ensure consistent application of defined terms.

Details for Revision 13.0

- Performed annual review of document and exhibits.

- Updated approval page per personnel change since prior version.

- Revised references for new Dominion Energy corporate identity.

- Removed references to registration as an “LSE” (deactivated through NERC December 2015)

- Added Section 5.6 Interconnection Requirements for Distribution Connected Generation.

- Section 3.3.6. Metering and telecommunications, subsection “Revenue Metering Data Communications”:  added reference to Primestone billing data system.

- Revised Exhibit A – Dominion Energy Electric Transmission Planning Criteria (for details, see Revision History within Exhibit A)

Details for Revision 14.0

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

Details for Revision 15.0

- Section 3.3:  Added new section per new NERC FAC-001-3 standard; content within Section 3.3 of prior versions of this document is now in Section 3.4.

- Section 3.4.5 System protection and coordination (Protection system design) - added content re: Breaker Failure Protection.

- Section 5:  Added reference to Exhibit C Protection Requirements; renumbered all sections and diagrams occurring after newly inserted section 5.3.

- Section 5.3:  Added new section regarding generation connected to transmission tap lines.

- Section 8.1: Added definition for Transmission Element.

- Made all remaining revisions for Dominion Energy corporate identity, in text and in images (Rev 13 included initial related changes along with a clarifying statement in Section 1).

- Revised Exhibit C – Dominion Energy Electric Transmission Generator Interconnection Protection Requirements_Rev3 (for details, see Revision History within Exhibit C)

Details for Revision 16.0

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

Details for Revision 17.0

- Performed annual review of document and exhibits.

- Updated approval page per personnel change since prior version.

- Section 1: Removed references to Section 3 for additional explanation.

- Section 3: Revised references to the FAC-001 R3 ‘Application Guidelines’ to ‘Supplemental Guidelines’.

- Section 3.2: Revised bullets for the subsequent changes list.

- Section 3.4.8: Revised reference and definition of ‘insulation coordination’.

- Section 3.4.10: Updated IEC standard reference to 6100-4-15 and removed reference to UIE 96-10.

- Section 5: The Notes listed for Diagrams 5.1 and 5.2.B were updated to reference Section C of Exhibit A of this FAC-001 NCP.

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

Details for Revision 18.0

- Revised Exhibit A – Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

Details for Revision 19.0

- Updated signature page.

- Updated Purpose to match Purpose in NERC standard

- Updated Dominion Energy to Dominion Energy Virginia

- Various grammatical and formatting changes

- Section 3 – Moved section from number 7 to 3 and updated wording on applicability.

- Updated section and diagram numbers accordingly.

- Section 5.4.9 – Added the nighttime var requirements.

- Section 5.4.14 – Added reference to Attachment 4

- Revised naming of attached Exhibits to Attachments

- Revised Attachment 1 – Dominion Energy Virginia Electric Transmission Planning Criteria (for details, see Revision History within Transmission Planning Criteria)

- Revised Attachment 3 - Dominion Energy Virginia Generator Interconnection Protection Requirements (for details, see Revision History within Generator Interconnection Protection Requirements)

- Added Attachment 4 – Dominion Energy Virginia Bulk Power System Generator Ride-Through Requirements

Details for Revision 20.0

- Section 2 – Added references to PJM manuals

- Section 4.1.9 – Updated references to PJM manuals

- Updated signature page

- Updated formatting throughout the document

- Combined Sections 4, 5, 6, 7 from Revision 19.0 into Section 4.0 – Procedure in this Revision

Details for Revision 21.0

- Updated Signature Page

- Minor wording update

- Section 4.0, Compliance Requirement R3.3 – Reworded to clarify

- Section 4.1.6 – Added reference to Attachment 5

- Section 4.1.9 – Added reference to Attachment 5

- Updated Attachment 1, to reflect TPL001-5.1

- Attachment 5, Added new attachment

Total length of the line in miles times the total projected load in MW. See Attachment 1 of this document, Section C.2.6 Radial transmission lines for details.