## NOTES
2019 RTEP Proposal Window 1 Results, Summer Case
| Revision History: | See Problem Statement for version history details
| Version of this file: | 12
Baseline Thermal Analysis:
Baseline thermal analysis is a thorough analysis of the reference power flow to ensure thermal adequacy based on normal and emergency thermal ratings specific to the Transmission Owner facilities being examined. It is based on a 50/50 load forecast from the latest available PJM Load Forecast Report. It encompasses an exhaustive analysis of all NERC category A, B and C events and the most critical common mode outages. Final results are supported with AC power flow solutions. The PJM Load Forecast uses a 50/50 distribution minus Energy Efficiency. Demand Response is not considered in the Load Forecast.
Basecase N-1 Voltage
Baseline voltage analysis parallels the thermal analysis. It uses the same power flow and examines voltage criteria for all the same NERC category A, B, and C events. Also, voltage criteria are examined for compliance. PJM examines system performance for both a voltage drop criteria (where applicable) and an absolute voltage criteria. The voltage drop is calculated as the decrease in bus voltage from the initial steady state power flow to the post-contingency power flow. The post-contingency power flow is solved with generators holding a local generator bus voltage to a pre-contingency level consistent with specific Transmission Owner specifications. In most instances this is the pre-contingency generator bus voltage. Additionally, all phase shifters, transformer taps, switched shunts, and DC lines are locked for the post-contingency solution. SVC’s are allowed to regulate and fast switched capacitors are enabled.
Generator Deliverability and Common Mode Outage Analysis:
The generator deliverability test ensures that the Transmission System is capable of delivering the aggregate system generating capacity at peak load with all firm transmission service modeled. The procedure ensures sufficient transmission capability in all areas of the system to export an amount of generation capacity at least equal to the amount of certified capacity resources in each “area”. Areas, as referred to in the generation deliverability test, are unique to each study and depend on the electrical system characteristics that may limit transfer of capacity resources. For generator deliverability areas are defined with respect to each transmission element that may limit transfer of the aggregate of certified installed generating capacity. The cluster of generators with significant impacts on the potentially limiting element is the “area” for that element. The cluster of generators with significant impacts on the potentially limiting element is the “area” for that element. The starting point power flow is the same power flow case set up for the baseline analysis. Thus the same baseline load and ratings criteria apply. The details of the generator deliverability procedure including methods of creating the study dispatch can be found in PJM Manual 14B Attachment C.
Load Deliverability Analysis:
The load deliverability tests are a unique set of analyses designed to ensure that the Transmission System provides a comparable transmission function throughout the system. These tests ensure that the Transmission System is adequate to deliver each load area’s requirements from the aggregate of system generation. The tests develop an “expected value” of loading after testing an extensive array of probabilistic dispatches to determine thermal limits. A deterministic dispatch method is used to create imports for the voltage criteria test. The Transmission System reliability criterion used is 1 event of failure in 25 years. This is intended to design transmission so that it is not more limiting than the generation system which is planned to a reliability criterion of 1 failure event in 10 years. Each load areas’ deliverability target transfer level to achieve the transmission reliability criterion is separately developed using a probabilistic modeling of the load and generation system. The load deliverability tests described here measure the design transfer level supported by the Transmission System for comparison to the target transfer level. Transmission upgrades are specified by PJM to achieve the target transfer level as necessary. Details of the load deliverability procedure can be found in Attachment C.
Thermal:
This test examines the deliverability under the stressed conditions of a 90/10 summer load forecast. That is, a forecast that only has a 10% chance of being exceeded. The transfer limit to the load is determined for system normal and all single contingencies (NERC category A and B criteria) under ten thousand load study area dispatches with calculated probabilities of occurrence. The dispatches are developed randomly based on the availability data for each generating unit. This results in an expected value of system transfer capability that is compared to the target level to determine system adequacy. As with all thermal transmission tests applied by PJM the applicable Transmission Owner normal and emergency ratings are applied. The steady state and single contingency power flows are solved consistent with the similar solutions described for the baseline thermal analyses.
Voltage:
This testing procedure is similar to the thermal load deliverability test except that voltage criteria are evaluated and that a deterministic dispatch procedure is used to increase study area imports. The voltage tests and criteria are the same as those performed for the baseline voltage analyses.
NERC Category C3 "N-1-1" Analysis
N-1-1 studies are conducted as part of the annual RTEP to determine if all monitored facilities can be operated: - Within normal thermal limits after N-1 (single) contingency assuming re-dispatch and system adjustments, and - Within the applicable emergency thermal ratings and voltage limits after an additional single contingency (N-1-1) condition. All violations of the applicable thermal ratings are recorded and reported and tentative solutions will be developed. These study results will be presented to and reviewed with stakeholders.Annually, the N-1-1 study is conducted on a 50/50 non-diversified summer peak caseThe case building details are defined in Attachment C (C7 3.0 Step 1: Develop Base Case). Non-firm Merchant Transmission withdrawals can be removed. All BES facilities in PJM and ties to PJM will be monitored. Areas of the system that become radial post-contingency will be excluded from monitoring, with the following exceptions: - If the radial system contains greater than 300 MW of load, or - Specific local TO Planning Criteria require that it be monitored.
N-1-1 Voltage
N-1-1 studies are conducted as part of the annual RTEP to determine if all monitored facilities can be operated: - Within normal thermal and voltage limits after N-1 (single) contingency assuming re-dispatch and system adjustments, and - Within the applicable emergency thermal ratings and voltage limits after an additional single contingency (N-1-1) condition.
Voltage Drop Test Methodology:
The N-1-1 Voltage Drop Test procedure follows a similar method as the thermal test method, except all monitored facilities are monitored for the emergency voltage drop limit after the second contingency (N-1-1 condition.) The calculation of voltage drop is defined in section 2.3.7.
Voltage Magnitude Test:
The N-1-1 Voltage Magnitude Test procedure follows a similar method as the thermal test method, except all monitored facilities are monitored for the emergency low limit after the second contingency (N-1-1 condition.)
Voltage Collapse:
Voltage collapse is considered to be a severe reliability violation, and consequently each N-1-1 condition that exhibits voltage collapse needs to be investigated, validated, and resolvedwith remedial actions, or network upgrades.
Contingencies Considered:
| Single: | NERC Category B: Event Resulting in the loss of a single element
| Bus: | NERC Category C: Event Resulting in the loss of a Bus
| Tower: | NERC Category C: Event Resulting in the loss of a Tower
| Line_FB: | NERC Category C: Line fault with stuck breaker
Contingencies Considered For N-1-1 analysis:
All BES single contingencies as defined in NERC category C.3 facilities that are monitored by PJM Operations will be included in the assessment. Non-BES contingencies, defined by Transmission Owners, need to be included to check for greater than 300 MW load loss. Non-BES facilities that are included in the assessment will also have corresponding contingencies defined. Please see the following link for individual Transmission Owner Criteria:
http://pjm.com/planning/planning-criteria/to-planning-criteria.aspx
Short Circuit Analysis
PJM performs short circuit analysis as part of the annual Regional Transmission Expansion Plan (RTEP) baseline assessment. This analysis includes a study of the entire PJM system based on its current configuration and equipment to determine if the short circuit current interrupting duty of circuit breakers is sufficient for the 2 year planning case. In addition, PJM also performs the analysis on the planned system configuration using a 5-year out case. Additional sensitivity studies are performed on years 3 and 4 as needed. The generation and merchant transmission interconnection process (see Manual 14A) also includes short circuit analysis for each requested new interconnection project. The addition of new sources and BES equipment drives most breaker replacements. PJM Planning conducts short circuit analysis to ensure the high-voltage circuit breakers on the transmission system are sufficiently rated to safely interrupt fault currents. These short circuit studies are also referred to as breaker interrupting studies. Since new sources only become committed with relative assurance a few years before scheduled commercial operation and since breaker replacement lead times are only a few years, these analysis are only conducted within the 5-year planning horizon.
Zone
| Flowgates | Count | Included
N-1 Thermal
N-1 Voltage, Low
N-1 Voltage, High
N-1 Load Drop
Gen Deliv
N-1-1 Thermal
N-1-1 Voltage, Low
N-1-1 Voltage Drop
Load Deliv
Light Load - Thermal
Light Load - Voltage, Low
Light Load - Voltage Drop
Light Load - Voltage, High
Winter, N-1 Thermal
Winter, N-1 Voltage High
| Winter, N-1 Voltage Low | 0
| Winter, N-1 Voltage Drop | 0
| Winter Gen Deliv | 43 | 7

## Sum Basecase Analysis Thermal
PJM N-1 Thermal Result (Summer 2024 Case)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals | Comments
N1-ST17 | 228115 | CORSON#2 | 228116 | COURT | 1 | 69/69 | 234/234 | 111 | 149.9099 | 179.54 | Line_FB | ACE_P5_CORSON' | N/A | No | Immediate Need
N1-ST30 | 228116 | COURT | 228114 | C-M-L TP | 1 | 69/69 | 234/234 | 112 | 111.25 | 131.18 | Line_FB | 'ACE_P5_CORSON' | N/A | No | Immediate Need
N1-ST31 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151 | 117.0861 | 119.57 | Tower | 'AEP_P7-1_#10915' | N/A | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N1-ST32 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151 | 109.4702 | 112.79 | Tower | 'AEP_P7-1_#10973' | N/A | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N1-ST42 | 228217 | DENNIS | 228185 | CORSON#1 | 1 | 69/69 | 234/234 | 358 | 90.4469 | 109.17 | Line_FB | 'ACE_P5_CORSON' | N/A | No | Immediate Need
N1-ST45 | 243566 | 05SAWMIL | 243499 | 05DUBLIN1 | 1 | 138/138 | 205/205 | 222 | 103.1982 | 107.02 | Line_FB | 'AEP_P4_#9608_05DAVIDS 138_AE' | N/A | No | Will be addressed by a baseline upgrade B3112 which was presented at the 3/25/2019 Western SRRTEP
N1-ST46 | 314170 | 6COHMIL | 314006 | 6ASHBURA | 1 | 230/230 | 345/345 | 719.1 | 106.6611 | 104.9362 | Single | 'DVP_P1-2: LN 274' | SN/SE=765/765 | No | The overload is also identified through the do no harm testing performed by PJM for M-3 Need DOM-2018-0012. Dominion Supplemental Project s1838, submitted as part of the Finalized Local Plan, mitigates the violation identified for this flowgate.
N1-ST50 | 214062 | WSTMLNDE | 213873 | PENCOYD2 | 1 | 69/69 | 230/230 | 103 | 98.1553 | 104.51 | Line_FB | 'PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK' | Conductor Rating is the same as basecase model | No | Radial facility below 200 kV
N1-ST51 | 213786 | MASTER 2 | 214062 | WSTMLNDE | 1 | 69/69 | 230/230 | 103 | 98.1553 | 104.49 | Line_FB | 'PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK' | Conductor Rating is the same as basecase model | No | Radial facility below 200 kV
Version: | 12
|  | Note: |  | Solved by existing RTEP project

## Sum Basecase Analysis Volt Mag
PJM N-1 Voltage Magnitude Result (Summer 2024 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Low Limit | Cont Type | Contingency | PJM Accepting Proposals | Comment
N1-SVM1 | 228113 | MIDDLE#1 | 138 | 234 | 0.6765 | 1.0166 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM2 | 228112 | MIDDLE#2 | 138 | 234 | 0.676 | 1.0188 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM3 | 228217 | DENNIS | 69 | 234 | 0.91 | 1.0316 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM4 | 228195 | SEA ISLE | 69 | 234 | 0.7961 | 1.0205 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM5 | 228192 | ROGRDTP2 | 69 | 234 | 0.6847 | 1.0282 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM6 | 228186 | MIDDLE#2 | 69 | 234 | 0.6875 | 1.03 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM7 | 228185 | CORSON#1 | 69 | 234 | 0.8063 | 1.0272 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM8 | 228180 | LAKE#4 | 69 | 234 | 0.6857 | 1.0431 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM9 | 228179 | ROGRDTP1 | 69 | 234 | 0.6846 | 1.0282 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM10 | 228146 | PEERMONT | 69 | 234 | 0.7302 | 1.0223 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM11 | 228140 | CAPE MAY | 69 | 234 | 0.6705 | 1.0193 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM12 | 228129 | SWAINTON | 69 | 234 | 0.7643 | 1.0232 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM13 | 228125 | RIO GRD1 | 69 | 234 | 0.6846 | 1.0282 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM14 | 228123 | S.I. ATP | 69 | 234 | 0.7941 | 1.0249 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM15 | 228122 | MIDDLE#1 | 69 | 234 | 0.6878 | 1.0303 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM16 | 228120 | LAKE #2 | 69 | 234 | 0.6829 | 1.0258 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM17 | 228116 | COURT | 69 | 234 | 0.7124 | 1.0216 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM18 | 228115 | CORSON#2 | 69 | 234 | 0.8059 | 1.0273 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVM19 | 228114 | C-M-L TP | 69 | 234 | 0.687 | 1.0283 | 0.94 | Line_FB | ACE_P5_CORSON | No | Immediate Need
Version: | 12

## Sum Basecase Analysis Volt Drop
PJM N-1 Voltage Drop Result (Summer 2024)
FG # | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Comment
N1-SVD1 | 206320 | 28NJT RED | 230 | 228 | 0.8233 | 1.009 | 18.57 | Tower | JC-P7-1-JCC-230-14A | No | The violation is related to the cancelation of the B1690 (MCRP) and Alternatives are under evaluation
N1-SVD2 | 206307 | 28RED BANK | 230 | 228 | 0.8233 | 1.009 | 18.57 | Tower | JC-P7-1-JCC-230-14A | No | The violation is related to the cancelation of the B1690 (MCRP) and Alternatives are under evaluation
N1-SVD3 | 228113 | MIDDLE#1 | 138 | 234 | 0.667 | 1.0166 | 34.96 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD4 | 228112 | MIDDLE#2 | 138 | 234 | 0.6667 | 1.0188 | 35.21 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD29 | 228217 | DENNIS | 69 | 234 | 0.9006 | 1.0315 | 13.09 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD30 | 228195 | SEA ISLE | 69 | 234 | 0.7934 | 1.0205 | 22.71 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD31 | 228192 | ROGRDTP2 | 69 | 234 | 0.6755 | 1.0282 | 35.27 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD32 | 228186 | MIDDLE#2 | 69 | 234 | 0.678 | 1.03 | 35.2 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD33 | 228185 | CORSON#1 | 69 | 234 | 0.8027 | 1.0271 | 22.44 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD34 | 228180 | LAKE#4 | 69 | 234 | 0.6797 | 1.043 | 36.33 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD35 | 228179 | ROGRDTP1 | 69 | 234 | 0.6755 | 1.0282 | 35.27 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD36 | 228146 | PEERMONT | 69 | 234 | 0.7258 | 1.0223 | 29.65 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD37 | 228140 | CAPE MAY | 69 | 234 | 0.6636 | 1.0193 | 35.57 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD38 | 228130 | TUCKAHOE | 69 | 234 | 0.9328 | 1.0341 | 10.13 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD39 | 228129 | SWAINTON | 69 | 234 | 0.7612 | 1.0232 | 26.2 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD40 | 228125 | RIO GRD1 | 69 | 234 | 0.6754 | 1.0281 | 35.27 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD41 | 228123 | S.I. ATP | 69 | 234 | 0.7911 | 1.0249 | 23.38 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD42 | 228122 | MIDDLE#1 | 69 | 234 | 0.6781 | 1.0302 | 35.21 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD43 | 228120 | LAKE #2 | 69 | 234 | 0.6757 | 1.0258 | 35.01 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD44 | 228116 | COURT | 69 | 234 | 0.709 | 1.0216 | 31.26 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD45 | 228115 | CORSON#2 | 69 | 234 | 0.8022 | 1.0273 | 22.51 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD46 | 228114 | C-M-L TP | 69 | 234 | 0.6791 | 1.0283 | 34.92 | Line_FB | ACE_P5_CORSON | No | Immediate Need
N1-SVD47 | 227919 | LENOX | 69 | 234 | 0.9216 | 1.0213 | 9.97 | Single | AE_P1-2 LEN-LEW | No | Not a valid violation.
N1-SVD48 | 227915 | EGG HRBR | 69 | 234 | 0.9257 | 1.017 | 9.13 | Single | AE_P1-2 LEN-LEW | No | Not a valid violation.
Version: | 12

## Sum Basecase Analysis Not Conv (hidden)
None

## Sum Gen Deliv
PJM Generation Deliverability 2024 RTEP Result (Summer)
FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals | Comment
GD-S10 | 243026 | 05KAMMER13 | 243012 | 05G WASHGTN1 | 1 | 138 | 205 | 446 | 456.1 | 449.7 | 102.26 | 100.82 | Base Case | Single | SN/SE = 471/642 | No | Below 200kV Exclusion
GD-S11 | 200920 | 26FRANKLNA | 200575 | 26MRGAN ST | 1 | 115 | 226 | 282 | 275.2 | 284 | 97.6 | 100.71 | PN-P1-2-PN-345-001 | Single | N/A | No | Will be addressed by upgraded B3082 identified for Eastlake #6, Kimberly Clark, Mansfield #1, #2, #3, Sammis #5, #6, #7 and Diesel units deactivation study, which was board approved in Feb. 2019
GD-S14 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138 | 205 | 151 | 149.1 | 151.3 | 98.73 | 100.2 | AEP_P1-2_#5805 | Single | N/A | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
GD-S302 | 243566 | 05SAWMIL | 243499 | 05DUBLIN1 | 1 | 138 | 205 | 222 | 229.1 | 237.6 | 103.18 | 107.04 | AEP_P4_#9608_05DAVIDS 138_AE | Breaker | N/A | No | Will be addressed by a baseline upgrade B3112 which was presented at the 3/25/2019 Western SRRTEP
GD-S315 | 214062 | WSTMLNDE | 213873 | PENCOYD2 | 1 | 69 | 230 | 103 | 101.1 | 107.6 | 98.16 | 104.5 | PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK | Breaker | Conductor Rating is the same as basecase model | No | Radial facility below 200 kV
GD-S316 | 213786 | MASTER 2 | 214062 | WSTMLNDE | 1 | 69 | 230 | 103 | 101.1 | 107.6 | 98.19 | 104.49 | PECO_P4_ROXBO215/* $ PHILLY $ PECO_P4_ROXBO215 $ STBK | Breaker | Conductor Rating is the same as basecase model | No | Radial facility below 200 kV
GD-S320 | 918350 | AA1-047 TAP | 235297 | 01HAZELT | 1 | 138 | 201 | 311 | 323.7 | 323.7 | 104.09 | 104.09 | AP-P2-3-PE-138-009A_A | Breaker | N/A | No | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
GD-S321 | 918350 | AA1-047 TAP | 235297 | 01HAZELT | 1 | 138 | 201 | 311 | 323.7 | 323.7 | 104.09 | 104.09 | AP-P2-3-PE-138-008A_A | Breaker | N/A | No | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
GD-S323 | 239070 | 02RICHLD | 239165 | 02WAUSEO | 1 | 138 | 202 | 190 | 197.1 | 196.1 | 103.74 | 103.2 | ATSI-P2-3-TE-138-010C | Breaker | N/A | No | Not a violation, Loading should be <100% without V2-006 (150 MW) suspended queue
GD-S325 | 239070 | 02RICHLD | 239165 | 02WAUSEO | 1 | 138 | 202 | 190 | 194.6 | 194.5 | 102.42 | 102.35 | ATSI-P2-3-TE-138-009 | Breaker | N/A | No | Not a violation, Loading should be <100% without V2-006 (150 MW) suspended queue
GD-S330 | 235297 | 01HAZELT | 235305 | 01 106 J | 1 | 138 | 201 | 311 | 313.7 | 313.7 | 100.87 | 100.87 | AP-P2-3-PE-138-008A_A | Breaker | N/A | No | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
GD-S331 | 235297 | 01HAZELT | 235305 | 01 106 J | 1 | 138 | 201 | 311 | 313.7 | 313.7 | 100.87 | 100.87 | AP-P2-3-PE-138-009A_A | Breaker | N/A | No | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
GD-S334 | 200920 | 26FRANKLNA | 200575 | 26MRGAN ST | 1 | 115 | 226 | 282 | 275 | 283.7 | 97.51 | 100.61 | PN-P2-3-PN-345-004J | Breaker | N/A | No | Will be addressed by upgraded B3082 identified for Eastlake #6, Kimberly Clark, Mansfield #1, #2, #3, Sammis #5, #6, #7 and Diesel units deactivation study, which was board approved in Feb. 2019
GD-S495 | 918350 | AA1-047 TAP | 235297 | 01HAZELT | 1 | 138 | 201 | 311 | 323.7 | 323.7 | 104.09 | 104.09 | AP-P2-2-PE-138-021B | Bus | N/A | No | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
GD-S496 | 239070 | 02RICHLD | 239165 | 02WAUSEO | 1 | 138 | 202 | 190 | 194.6 | 194.5 | 102.42 | 102.35 | ATSI-P2-2-TE-138-004 | Bus | N/A | No | Not a violation, Loading should be <100% without V2-006 (150 MW) suspended queue
GD-S498 | 235297 | 01HAZELT | 235305 | 01 106 J | 1 | 138 | 201 | 311 | 313.7 | 313.7 | 100.87 | 100.87 | AP-P2-2-PE-138-021B | Bus | N/A | No | Not a violation, Loading should be <100% without AA1-047 (69.1 MW) suspended queue
GD-S5 | 314170 | 6COHMIL | 314006 | 6ASHBURA | 1 | 230 | 345 | 719.1 | 815.2 | 801.9 | 113.37 | 111.51 | DVP_P1-2: LN 274 | Single | SN/SE=765/765 | No | The overload is also identified through the do no harm testing performed by PJM for M-3 Need DOM-2018-0012. Dominion Supplemental Project s1838, submitted as part of the Finalized Local Plan, mitigates the violation identified for this flowgate.
GD-S532 | 314554 | 3BTLEBRO | 304223 | 3ROCKYMT115T | 1 | 115 | 340/345 | 164 | 233.1 | 229.3 | 142.11 | 139.83 | DVP_P7-1: LN 2058-2181 | Tower | N/A | No | Tie Line to Non PJM facility. No reinforcement required at this time.
GD-S533 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138 | 205 | 151 | 179.4 | 183.2 | 118.81 | 121.31 | AEP_P7-1_#10915 | Tower | N/A | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
GD-S536 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138 | 205 | 151 | 166.1 | 171.2 | 110.03 | 113.36 | AEP_P7-1_#10973 | Tower | N/A | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
GD-S537 | 231215 | SILVERSD | 231205 | DARLEY | 1 | 69 | 235 | 175 | 203.8 | 196.9 | 116.45 | 112.52 | DPL_P7_1_DBL_5NC | Tower | Conductor Rating is the same as basecase model | Yes
GD-S538 | 231205 | DARLEY | 231211 | NAAMANS | 1 | 69 | 235 | 136 | 148.1 | 144.6 | 108.9 | 106.32 | DPL_P7_1_DBL_5NC | Tower | Conductor Rating is the same as basecase model | Yes
GD-S539 | 243026 | 05KAMMER13 | 243012 | 05G WASHGTN1 | 1 | 138 | 205 | 621 | 659.2 | 651.7 | 106.15 | 104.94 | AEP_P7-1_#11151 | Tower | SN/SE = 471/642 | No | Below 200kV Exclusion
GD-S544 | 238581 | 02BRBRTN | 239619 | 02ALCOA | 1 | 138 | 202 | 282 | 277.3 | 285 | 98.34 | 101.06 | ATSI-P7-1-OEC-345-003 | Tower | SN/SE= 310/357 | No | Substation Equipment Exclusion
GD-S7 | 314006 | 6ASHBURA | 314010 | 6BEAMEAD | 1 | 230 | 345 | 719.1 | 773.3 | 761.7 | 107.53 | 105.92 | DVP_P1-2: LN 274 | Single | SN/SE=765/765 | No | Dominion Supplemental Project s1838, submitted as part of the Finalized Local Plan for M-3 Need DOM-2018-0012 mitigates the violation identified for this flowgate.
GD-S9 | 239070 | 02RICHLD | 239060 | 02RDGVL | 1 | 138 | 202 | 179 | 183.1 | 184.3 | 102.3 | 102.97 | ATSI-P1-2-TE-138-001B | Single | SN/SE= 161/194 | No | Final AC loading should be 101.7% without V2-006 (150 MW) suspended queue; Substation Equipment Exclusion
Version: | 12
Note:
The final AC loading is due to contribution from Suspended, Deactivated, or Withdrawn generators and the loading on the circuit should be <100% without those generators.
Final AC loading should be less than what is listed, for loading information see comment
First limiting facility is a non-PJM facility and will require coordination with the neighboring entity prior to determining if proposals will be accepted
Solved by existing RTEP project
| * |  | Limiting facility is non PJM and should be addressed by coordinating with the neighboring entity

## Sum N-1-1 Thermal Results
PJM N-1-1 Thermal Result (2024 Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | Initial AC (%) | SCD AC (%) | Contingency 1 | Contingency 2 | Conductor Rating (MVA) | PJM Accepting Proposals | Comments
N2-ST1 | 235710 | 01WYLIE R | 235250 | 01SMITH | 1 | 138/138 | 201/201 | 229.0 | 116.79 | 104.02 | 'AEP_P1-2_#8598' | 'AP-P1-2-MP-345-520T' | SN/SE =243/297 | No | Substation equipment Exclusion
N2-ST2 | 235710 | 01WYLIE R | 235250 | 01SMITH | 1 | 138/138 | 201/201 | 229.0 | 116.80 | 104.04 | 'AP-P1-2-MP-345-520T' | 'AEP_P1-2_#8598' | SN/SE =243/297 | No | Substation equipment Exclusion
N2-ST3 | 238581 | 02BRBRTN | 239619 | 02ALCOA | 1 | 138/138 | 202/202 | 282.0 | 106.11 | 104.91 | 'ATSI-P1-2-SYS-345-713' | 'ATSI-P1-2-OEC-138-066' | SN/SE =310/357 | No | Substation equipment Exclusion
N2-ST4 | 238581 | 02BRBRTN | 239619 | 02ALCOA | 1 | 138/138 | 202/202 | 282.0 | 106.10 | 104.24 | 'ATSI-P1-2-OEC-138-066' | 'ATSI-P1-2-SYS-345-713' | SN/SE =310/357 | No | Substation equipment Exclusion
N2-ST5 | 239112 | 02LRCRQ1 | 239045 | 02PN Q-1 | 1 | 138/138 | 202/202 | 115.0 | 106.33 | 106.42 | 'ATSI-P1-2-CEI-138-061' | 'ATSI-P1-2-CEI-138-080' | Conductor Rating is the same as basecase model | No | Below 200kV Exclusion
N2-ST6 | 239112 | 02LRCRQ1 | 239045 | 02PN Q-1 | 1 | 138/138 | 202/202 | 115.0 | 106.33 | 106.39 | 'ATSI-P1-2-CEI-138-080' | 'ATSI-P1-2-CEI-138-061' | Conductor Rating is the same as basecase model | No | Below 200kV Exclusion
N2-ST7 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45.0 | 100.06 | 100.02 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' |  | No | Rating is set by NIPCO 's equipment, AEP side of rating 335/392/424/466 MVA for SN/SE/WN/WE.
N2-ST8 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45.0 | 100.06 | 100.02 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' |  | No | Rating is set by NIPCO 's equipment, AEP side of rating 335/392/424/466 MVA for SN/SE/WN/WE.
N2-ST9 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45.0 | 100.06 | 100.02 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' |  | No | Rating is set by NIPCO 's equipment, AEP side of rating 335/392/424/466 MVA for SN/SE/WN/WE.
N2-ST10 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45.0 | 100.06 | 100.02 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' |  | No | Rating is set by NIPCO 's equipment, AEP side of rating 335/392/424/466 MVA for SN/SE/WN/WE.
N2-ST11 | 242926 | 05MALIS | 243538 | 05MALISX | 1 | 765/138 | 205/205 | 926.0 | 123.97 | 109.02 | 'AEP_P1-3_#8072_05MARYSV 765_2' | 'AEP_P1-3_#7218_05VASSEL 765_1' | Transformer SN/SE =820/1054 | No | Not a violation. Mitigated by an existing Remedial Action Scheme (RAS).
N2-ST12 | 242926 | 05MALIS | 243538 | 05MALISX | 1 | 765/138 | 205/205 | 926.0 | 123.96 | 107.69 | 'AEP_P1-3_#7218_05VASSEL 765_1' | 'AEP_P1-3_#8072_05MARYSV 765_2' | Transformer SN/SE =820/1054 | No | Not a violation. Mitigated by an existing Remedial Action Scheme (RAS).
N2-ST13 | 243553 | 05POLARS | 243590 | 05WSTRV3 | 1 | 138/138 | 205/205 | 226.0 | 107.73 | 105.03 | 'AEP_SUBT_P1-3_#381_05GENOA 138_2' | 'AEP_P1-3_#7218_05VASSEL 765_1' |  | No | Will be addressed by a baseline upgrade B3104 which was presented at the 3/07/2019 TEAC
N2-ST14 | 243553 | 05POLARS | 243590 | 05WSTRV3 | 1 | 138/138 | 205/205 | 226.0 | 112.56 | 104.98 | 'AEP_P1-2_#5832' | 'AEP_P1-3_#7218_05VASSEL 765_1' |  | No | Will be addressed by a baseline upgrade B3104 which was presented at the 3/07/2019 TEAC
N2-ST15 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 107.29 | 106.04 | 'AEP_P1-2_#5849' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST16 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 111.95 | 106.82 | 'AEP_P1-2_#5805' | 'AEP_P1-2_#5853' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST17 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 110.45 | 104.47 | 'AEP_P1-2_#5805' | 'AEP_P1-3_#4756_05ROBRT2 345_2' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST18 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 110.45 | 104.47 | 'AEP_P1-2_#5805' | 'AEP_P1-2_#6227' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST19 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 109.86 | 103.88 | 'AEP_P1-2_#5805' | 'AEP_P1-3_#3235_05ROBRT1 345_1' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST20 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 109.86 | 103.88 | 'AEP_P1-2_#5805' | 'AEP_P1-2_#3233' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST21 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-3_#3235_05ROBRT1 345_1' | 'AEP_P1-3_#4756_05ROBRT2 345_2' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST22 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-3_#3235_05ROBRT1 345_1' | 'AEP_P1-2_#6227' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST23 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 109.86 | 109.19 | 'AEP_P1-3_#3235_05ROBRT1 345_1' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST24 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-2_#3233' | 'AEP_P1-3_#4756_05ROBRT2 345_2' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST25 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-2_#3233' | 'AEP_P1-2_#6227' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST26 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 109.86 | 109.19 | 'AEP_P1-2_#3233' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST27 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 112.61 | 112.44 | 'AEP_P1-2_#5853' | 'AEP_P1-2_#5756' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST28 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 111.95 | 111.38 | 'AEP_P1-2_#5853' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST29 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 101.04 | 100.48 | 'AEP_P1-2_#5853' | 'AEP_P1-2_#11377' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST30 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.57 | 119.16 | 'AEP_P1-2_#714' | 'AEP_P1-2_#727' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST31 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-2_#6227' | 'AEP_P1-3_#3235_05ROBRT1 345_1' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST32 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-2_#6227' | 'AEP_P1-2_#3233' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST33 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 110.45 | 109.78 | 'AEP_P1-2_#6227' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST34 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 105.57 | 104.81 | 'AEP_P1-2_#5850' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST35 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 101.04 | 100.47 | 'AEP_P1-2_#11377' | 'AEP_P1-2_#5853' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST36 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 112.61 | 112.44 | 'AEP_P1-2_#5756' | 'AEP_P1-2_#5853' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST37 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 102.05 | 101.51 | 'AEP_P1-2_#5756' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST38 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.57 | 116.10 | 'AEP_P1-2_#727' | 'AEP_P1-2_#714' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST39 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 112.24 | 105.45 | 'AEP_P1-2_#727' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST40 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 107.02 | 103.43 | 'AEP_P1-2_#727' | 'AEP_P1-2_#10137' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST41 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 107.03 | 106.36 | 'AEP_P1-2_#10137' | 'AEP_P1-2_#727' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST42 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-3_#4756_05ROBRT2 345_2' | 'AEP_P1-3_#3235_05ROBRT1 345_1' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST43 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 119.25 | 118.80 | 'AEP_P1-3_#4756_05ROBRT2 345_2' | 'AEP_P1-2_#3233' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST44 | 243566 | 05SAWMIL | 243479 | 05BROOKS | 1 | 138/138 | 205/205 | 151.0 | 110.45 | 109.78 | 'AEP_P1-3_#4756_05ROBRT2 345_2' | 'AEP_P1-2_#5805' |  | No | Will be addressed by a baseline upgrade B3109 which was presented at the 2/20/2019 Western SRRTEP
N2-ST45 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 104.46 | 103.53 | 'AEP_P1-2_#5495' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST46 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 104.46 | 103.53 | 'AEP_P1-2_#5495' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST47 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 121.05 | 117.40 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST48 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 121.05 | 117.40 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST49 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 104.35 | 101.17 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' | 'AEP_P1-2_#5495' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST50 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 121.05 | 117.40 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST51 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 121.05 | 117.40 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST52 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 104.35 | 101.17 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' | 'AEP_P1-2_#5495' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST53 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 120.75 | 119.77 | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST54 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 120.75 | 119.77 | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST55 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 120.75 | 119.77 | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST56 | 243412 | 05STURGI | 255331 | 17HOWE | 1 | 69/69 | 205/217 | 47.0 | 120.75 | 119.77 | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1_DUP1' |  | No | Not a violation after applying rating correction for Stubey Road - Sturgis 69 kV line.
N2-ST57 | 253993 | 15OAKLND | 253997 | 15PANHOL | 1 | 138/138 | 215/215 | 247.0 | 105.03 | 102.02 | 'DLC_P11_GEN_15CHSWK1' | 'DLC_P13_ARSENAL_138' |  | No | Will be addressed by a baseline upgrade B3084 which was presented at the 11/08/2018 TEAC
N2-ST58 | 253993 | 15OAKLND | 253997 | 15PANHOL | 1 | 138/138 | 215/215 | 247.0 | 105.16 | 102.22 | 'DLC_P13_ARSENAL_138' | 'DLC_P11_GEN_15CHSWK1' |  | No | Will be addressed by a baseline upgrade B3084 which was presented at the 11/08/2018 TEAC
N2-ST59 | 204558 | 27SMITH TP | 204557 | 27SMITH ST | 1 | 115/115 | 227/227 | 152.0 | 115.41 | 109.38 | 'ME-P1-3-ME-115-023' | 'ME-P1-2-ME-230-214T' | SN/SE =184/223 | No | Substation equipment Exclusion
N2-ST60 | 204558 | 27SMITH TP | 204557 | 27SMITH ST | 1 | 115/115 | 227/227 | 152.0 | 115.41 | 109.82 | 'ME-P1-2-ME-230-214T' | 'ME-P1-3-ME-115-023' | SN/SE =184/223 | No | Substation equipment Exclusion
N2-ST61 | 324509 | 2EASTVIEW | 342307 | 2STEPHENSBRG | 1 | 69/69 | 363/320 | 45.0 | 136.64 133.09 | 136.63 133.08 | 'EXT_324104 7DAVIESS 345 324106 7HARDIN CO 345 1' | 'EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1' |  | No | Line rating is limited by LGEE side. EKPC side rating is 57MVA for SE.
N2-ST62 | 324509 | 2EASTVIEW | 342307 | 2STEPHENSBRG | 1 | 69/69 | 363/320 | 45.0 | 114.46 112.71 | 114.26 112.51 | 'EXT_324308 4SHREWSBURY 138 324800 4MERE TVA 138 1' | 'EXT_324104 7DAVIESS 345 324106 7HARDIN CO 345 1' |  | No | Line rating is limited by LGEE side. EKPC side rating is 57MVA for SE.
N2-ST63 | 341563 | 2GREEN CO | 324554 | 2GRENSBRG KU | 1 | 69/69 | 320/363 | 66.0 | 136.08 132.55 | 136.12 132.6 | 'EKPC_P1-2_GRE-TAY-MAR161' | 'EXT_B-69-18' |  | No | The line rating is limited by LGEE side. LGEE side rating is 52/66 and EKPC side rating is 77/90 for SN/SE.
N2-ST64 | 341563 | 2GREEN CO | 324554 | 2GRENSBRG KU | 1 | 69/69 | 320/363 | 52.0 | 106.66 105.18 | 106.59 105.12 | 'EKPC_P1-2_GRE-TAY-MAR161' | 'BASE CASE' |  | No | The line rating is limited by LGEE side. LGEE side rating is 52/66 and EKPC side rating is 77/90 for SN/SE.
N2-ST65 | 341563 | 2GREEN CO | 324554 | 2GRENSBRG KU | 1 | 69/69 | 320/363 | 66.0 | 138.37 134.71 | 138.37 134.71 | 'EKPC_P1-2_TAYL J-KU TAYL 161' | 'EXT_B-69-18' |  | No | The line rating is limited by LGEE side. LGEE side rating is 52/66 and EKPC side rating is 77/90 for SN/SE.
N2-ST66 | 341563 | 2GREEN CO | 324554 | 2GRENSBRG KU | 1 | 69/69 | 320/363 | 52.0 | 137.83 134.2 | 137.83 134.19 | 'EKPC_P1-2_TAYL J-KU TAYL 161' | 'BASE CASE' |  | No | The line rating is limited by LGEE side. LGEE side rating is 52/66 and EKPC side rating is 77/90 for SN/SE.
N2-ST67 | 341563 | 2GREEN CO | 324554 | 2GRENSBRG KU | 1 | 69/69 | 320/363 | 66.0 | 138.37 | 138.37 | 'EXT_B-69-18' | 'EKPC_P1-2_GRE-TAY-MAR161' |  | No | The line rating is limited by LGEE side. LGEE side rating is 52/66 and EKPC side rating is 77/90 for SN/SE.
N2-ST68 | 341563 | 2GREEN CO | 324554 | 2GRENSBRG KU | 1 | 69/69 | 320/363 | 66.0 | 137.83 | 137.83 | 'EXT_B-69-18' | 'EKPC_P1-2_TAYL J-KU TAYL 161' |  | No | The line rating is limited by LGEE side. LGEE side rating is 52/66 and EKPC side rating is 77/90 for SN/SE.
N2-ST69 | 314170 | 6COHMIL | 314006 | 6ASHBURA | 1 | 230/230 | 345/345 | 765.0 | 126.98 | 103.68 | 'DVP_P1-2: LN 2172' | 'DVP_P1-2: LN 274' |  | No | The overload is also identified through the do no harm testing performed by PJM for M-3 Need DOM-2018-0012. Dominion Supplemental Project s1838, submitted as part of the Finalized Local Plan, mitigates the violation identified for this flowgate.
N2-ST70 | 314170 | 6COHMIL | 314006 | 6ASHBURA | 1 | 230/230 | 345/345 | 765.0 | 126.98 | 102.00 | 'DVP_P1-2: LN 274' | 'DVP_P1-2: LN 2172' |  | No | The overload is also identified through the do no harm testing performed by PJM for M-3 Need DOM-2018-0012. Dominion Supplemental Project s1838, submitted as part of the Finalized Local Plan, mitigates the violation identified for this flowgate.
N2-ST71 | 314170 | 6COHMIL | 314006 | 6ASHBURA | 1 | 230/230 | 345/345 | 765.0 | 124.02 | 100.86 | 'DVP_P1-2: LN 2095' | 'DVP_P1-2: LN 274' |  | No | The overload is also identified through the do no harm testing performed by PJM for M-3 Need DOM-2018-0012. Dominion Supplemental Project s1838, submitted as part of the Finalized Local Plan, mitigates the violation identified for this flowgate.
N2-ST72 | 243553 | 05POLARS | 243590 | 05WSTRV3 | 1 | 138/138 | 205/205 | 226 | 107.73 | 105.03 | 'AEP_SUBT_P1-3_#381_05GENOA 138_2' | 'AEP_P1-3_#7218_05VASSEL 765_1' |  | No | Will be addressed by a baseline upgrade B3104 which was presented at the 3/07/2019 TEAC
N2-ST73 | 243553 | 05POLARS | 243590 | 05WSTRV3 | 1 | 138/138 | 205/205 | 226 | 112.56 | 104.98 | 'AEP_P1-2_#5832' | 'AEP_P1-3_#7218_05VASSEL 765_1' |  | No | Will be addressed by a baseline upgrade B3104 which was presented at the 3/07/2019 TEAC
N2-ST74 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45 | 103.09 | 102.13 | 'AEP_P1-2_#5495' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' |  | No | The line rating is limited by NIPSCO side. AEP side rating is 335/392 for SN/SE
N2-ST75 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45 | 108.65 | 106.47 | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1' |  | No | The line rating is limited by NIPSCO side. AEP side rating is 335/392 for SN/SE
N2-ST76 | 243247 | 05AUBURN | 255125 | 17DEKALB | 1 | 138/138 | 205/217 | 45 | 109.56 | 108.57 | 'EXT_P12:138:NIPS:13887:17LAGRANGE:17NORTHPORT:1_DUP1' | 'EXT_P12:138:NIPS:13809:17HIPLE :17LAGRANGE:1' |  | No | The line rating is limited by NIPSCO side. AEP side rating is 335/392 for SN/SE
N2-ST77 | 341935 | 2N SPRINGFLD | 324736 | 2SPRINGFL KU | 1 | 69/69 | 320/363 | 50 | 104.53 | 104.54 | 'EXT_B-69-18' | 'EKPC_P1-2_TAYL J-KU TAYL 161' |  | No | The line rating is limited by LGEE side. EKPC side rating is 49/54 for SN/SE
N2-ST78 | 341935 | 2N SPRINGFLD | 324736 | 2SPRINGFL KU | 1 | 69/69 | 320/363 | 50 | 104.36 | 104.37 | 'EXT_B-69-18' | 'EKPC_P1-2_GRE-TAY-MAR161' |  | No | The line rating is limited by LGEE side. EKPC side rating is 49/54 for SN/SE
N2-ST79 | 341935 | 2N SPRINGFLD | 324736 | 2SPRINGFL KU | 1 | 69/69 | 320/363 | 50 | 103.78 | 103.87 | 'EKPC_P1-2_GRE-TAY-MAR161' | 'EXT_B-69-18' |  | No | The line rating is limited by LGEE side. EKPC side rating is 49/54 for SN/SE
N2-ST80 | 341935 | 2N SPRINGFLD | 324736 | 2SPRINGFL KU | 1 | 69/69 | 320/363 | 50 | 104.07 | 104.05 | 'EKPC_P1-2_TAYL J-KU TAYL 161' | 'EXT_B-69-18' |  | No | The line rating is limited by LGEE side. EKPC side rating is 49/54 for SN/SE
Version: | 12
|  | Note: |  | First limiting facility is a non-PJM facility and will require coordination with the neighboring entity prior to determining if proposals will be accepted
Solved by existing RTEP project
Limiting facility is non PJM and should be addressed by coordinating with the neighboring entity
Note on L3: CONTINGENCY 'AEP_P1-2_#8598' OPEN BRANCH FROM BUS 242946 TO BUS 253965 CKT 1 / 242946 05TIDD 345 253965 15COLLIE 345 1 END
Note on M3: CONTINGENCY 'AP-P1-2-MP-345-520T' /* WYLIE RIDGE - TORONTO 345KV APS-ATSI TIE DISCONNECT BRANCH FROM BUS 235707 TO BUS 239368 CKT 1 /* 01WYLIE R 345 02TORONTO 345 END
Note on L4: CONTINGENCY 'AP-P1-2-MP-345-520T' /* WYLIE RIDGE - TORONTO 345KV APS-ATSI TIE DISCONNECT BRANCH FROM BUS 235707 TO BUS 239368 CKT 1 /* 01WYLIE R 345 02TORONTO 345 END
Note on M4: CONTINGENCY 'AEP_P1-2_#8598' OPEN BRANCH FROM BUS 242946 TO BUS 253965 CKT 1 / 242946 05TIDD 345 253965 15COLLIE 345 1 END
Note on L5: CONTINGENCY 'ATSI-P1-2-SYS-345-713' /* LINE 02JUNIPE TO 02STAR 345 CK 1 DISCONNECT BRANCH FROM BUS 238850 TO BUS 239122 CKT 1 /* 02JUNIPE 345 02STAR 345 END
Note on M5: CONTINGENCY 'ATSI-P1-2-OEC-138-066' /* LINE 02STAR TO 02WADS 138 CK 1 DISCONNECT BRANCH FROM BUS 239123 TO BUS 239160 CKT 1 /* 02STAR 138 02WADS 138 END
Note on L6: CONTINGENCY 'ATSI-P1-2-OEC-138-066' /* LINE 02STAR TO 02WADS 138 CK 1 DISCONNECT BRANCH FROM BUS 239123 TO BUS 239160 CKT 1 /* 02STAR 138 02WADS 138 END
Note on M6: CONTINGENCY 'ATSI-P1-2-SYS-345-713' /* LINE 02JUNIPE TO 02STAR 345 CK 1 DISCONNECT BRANCH FROM BUS 238850 TO BUS 239122 CKT 1 /* 02JUNIPE 345 02STAR 345 END
Note on L7: CONTINGENCY 'ATSI-P1-2-CEI-138-061' /* Q-1-NF-JR LINE OUTAGE DISCONNECT BRANCH FROM BUS 239001 TO BUS 238840 CKT 1 /* 02NFLDQ1 138 02JNPRQ1 138 END
Note on M7: CONTINGENCY 'ATSI-P1-2-CEI-138-080' /* Q-1-EL-MF-X LINE OUTAGE - W/BKR DISCONNECT BRANCH FROM BUS 241921 TO BUS 239011 CKT 1 /* 02ELQ1 138 02NP Q-1 138 DISCONNECT BRANCH FROM BUS 239011 TO BUS 238956 CKT 1 /* 02NP Q-1 138 02MFLDQ1 138 END
Note on L8: CONTINGENCY 'ATSI-P1-2-CEI-138-080' /* Q-1-EL-MF-X LINE OUTAGE - W/BKR DISCONNECT BRANCH FROM BUS 241921 TO BUS 239011 CKT 1 /* 02ELQ1 138 02NP Q-1 138 DISCONNECT BRANCH FROM BUS 239011 TO BUS 238956 CKT 1 /* 02NP Q-1 138 02MFLDQ1 138 END
Note on M8: CONTINGENCY 'ATSI-P1-2-CEI-138-061' /* Q-1-NF-JR LINE OUTAGE DISCONNECT BRANCH FROM BUS 239001 TO BUS 238840 CKT 1 /* 02NFLDQ1 138 02JNPRQ1 138 END
Note on L13: CONTINGENCY 'AEP_P1-3_#8072_05MARYSV 765_2' OPEN BRANCH FROM BUS 242928 TO BUS 242939 CKT 2 / 242928 05MARYSV 765 242939 05MARYSV 345 2 END
Note on M13: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 / 246751 05VASSEL 765 247728 05VASSEL_XFL 345 1 END
Note on L14: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 / 246751 05VASSEL 765 247728 05VASSEL_XFL 345 1 END
Note on M14: CONTINGENCY 'AEP_P1-3_#8072_05MARYSV 765_2' OPEN BRANCH FROM BUS 242928 TO BUS 242939 CKT 2 / 242928 05MARYSV 765 242939 05MARYSV 345 2 END
Note on L15: CONTINGENCY 'AEP_SUBT_P1-3_#381_05GENOA 138_2' OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 / 243513 05GENOA 138 243537 05MALIS 138 2 OPEN BRANCH FROM BUS 243513 TO BUS 246613 CKT 2 / 243513 05GENOA 138 246613 05GENOA 69.0 2 OPEN BRANCH FROM BUS 246613 TO BUS 246622 CKT 1 / 246613 05GENOA 69.0 246622 05WESTERVL 69.0 1 OPEN BRANCH FROM BUS 246613 TO BUS 246643 CKT 1 / 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1 REMOVE SWSHUNT FROM BUS 246613 / 246613 05GENOA 69.0 END
Note on M15: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 / 246751 05VASSEL 765 247728 05VASSEL_XFL 345 1 END
Note on L16: CONTINGENCY 'AEP_P1-2_#5832' OPEN BRANCH FROM BUS 243513 TO BUS 243537 CKT 2 / 243513 05GENOA 138 243537 05MALIS 138 2 END
Note on M16: CONTINGENCY 'AEP_P1-3_#7218_05VASSEL 765_1' OPEN BRANCH FROM BUS 246751 TO BUS 247728 CKT 1 / 246751 05VASSEL 765 247728 05VASSEL_XFL 345 1 END
Note on L17: CONTINGENCY 'AEP_P1-2_#5849' OPEN BRANCH FROM BUS 243516 TO BUS 243526 CKT 1 / 243516 05GREIF 138 243526 05HYATT 138 1 END
Note on M17: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L18: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on M18: CONTINGENCY 'AEP_P1-2_#5853' OPEN BRANCH FROM BUS 243495 TO BUS 243560 CKT 1 / 243495 05DAVIDS 138 243560 05ROBERT 138 1 END
Note on L19: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on M19: CONTINGENCY 'AEP_P1-3_#4756_05ROBRT2 345_2' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 OPEN BRANCH FROM BUS 243460 TO BUS 243560 CKT 2 / 243460 05ROBRT2 345 243560 05ROBERT 138 2 END
Note on L20: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on M20: CONTINGENCY 'AEP_P1-2_#6227' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 END
Note on L21: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on M21: CONTINGENCY 'AEP_P1-3_#3235_05ROBRT1 345_1' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 OPEN BRANCH FROM BUS 243461 TO BUS 243560 CKT 1 / 243461 05ROBRT1 345 243560 05ROBERT 138 1 END
Note on L22: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on M22: CONTINGENCY 'AEP_P1-2_#3233' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 END
Note on L23: CONTINGENCY 'AEP_P1-3_#3235_05ROBRT1 345_1' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 OPEN BRANCH FROM BUS 243461 TO BUS 243560 CKT 1 / 243461 05ROBRT1 345 243560 05ROBERT 138 1 END
Note on M23: CONTINGENCY 'AEP_P1-3_#4756_05ROBRT2 345_2' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 OPEN BRANCH FROM BUS 243460 TO BUS 243560 CKT 2 / 243460 05ROBRT2 345 243560 05ROBERT 138 2 END
Note on L24: CONTINGENCY 'AEP_P1-3_#3235_05ROBRT1 345_1' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 OPEN BRANCH FROM BUS 243461 TO BUS 243560 CKT 1 / 243461 05ROBRT1 345 243560 05ROBERT 138 1 END
Note on M24: CONTINGENCY 'AEP_P1-2_#6227' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 END
Note on L25: CONTINGENCY 'AEP_P1-3_#3235_05ROBRT1 345_1' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 OPEN BRANCH FROM BUS 243461 TO BUS 243560 CKT 1 / 243461 05ROBRT1 345 243560 05ROBERT 138 1 END
Note on M25: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L26: CONTINGENCY 'AEP_P1-2_#3233' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 END
Note on M26: CONTINGENCY 'AEP_P1-3_#4756_05ROBRT2 345_2' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 OPEN BRANCH FROM BUS 243460 TO BUS 243560 CKT 2 / 243460 05ROBRT2 345 243560 05ROBERT 138 2 END
Note on L27: CONTINGENCY 'AEP_P1-2_#3233' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 END
Note on M27: CONTINGENCY 'AEP_P1-2_#6227' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 END
Note on L28: CONTINGENCY 'AEP_P1-2_#3233' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 END
Note on M28: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L29: CONTINGENCY 'AEP_P1-2_#5853' OPEN BRANCH FROM BUS 243495 TO BUS 243560 CKT 1 / 243495 05DAVIDS 138 243560 05ROBERT 138 1 END
Note on M29: CONTINGENCY 'AEP_P1-2_#5756' OPEN BRANCH FROM BUS 243471 TO BUS 243560 CKT 2 / 243471 05BETHEL 138 243560 05ROBERT 138 2 END
Note on L30: CONTINGENCY 'AEP_P1-2_#5853' OPEN BRANCH FROM BUS 243495 TO BUS 243560 CKT 1 / 243495 05DAVIDS 138 243560 05ROBERT 138 1 END
Note on M30: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L31: CONTINGENCY 'AEP_P1-2_#5853' OPEN BRANCH FROM BUS 243495 TO BUS 243560 CKT 1 / 243495 05DAVIDS 138 243560 05ROBERT 138 1 END
Note on M31: CONTINGENCY 'AEP_P1-2_#11377' OPEN BRANCH FROM BUS 247873 TO BUS 245242 CKT 1 / 247873 05BRITTON 138 245242 05DUBLIN3 138 1 END
Note on L32: CONTINGENCY 'AEP_P1-2_#714' OPEN BRANCH FROM BUS 244022 TO BUS 243457 CKT 1 / 244022 05COLE 345 243457 05HAYDEN 345 1 END
Note on M32: CONTINGENCY 'AEP_P1-2_#727' OPEN BRANCH FROM BUS 243457 TO BUS 243458 CKT 1 / 243457 05HAYDEN 345 243458 05HYATT 345 1 END
Note on L33: CONTINGENCY 'AEP_P1-2_#6227' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 END
Note on M33: CONTINGENCY 'AEP_P1-3_#3235_05ROBRT1 345_1' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 OPEN BRANCH FROM BUS 243461 TO BUS 243560 CKT 1 / 243461 05ROBRT1 345 243560 05ROBERT 138 1 END
Note on L34: CONTINGENCY 'AEP_P1-2_#6227' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 END
Note on M34: CONTINGENCY 'AEP_P1-2_#3233' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 END
Note on L35: CONTINGENCY 'AEP_P1-2_#6227' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 END
Note on M35: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L36: CONTINGENCY 'AEP_P1-2_#5850' OPEN BRANCH FROM BUS 243516 TO BUS 243525 CKT 1 / 243516 05GREIF 138 243525 05HUNTLEY1 138 1 END
Note on M36: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L37: CONTINGENCY 'AEP_P1-2_#11377' OPEN BRANCH FROM BUS 247873 TO BUS 245242 CKT 1 / 247873 05BRITTON 138 245242 05DUBLIN3 138 1 END
Note on M37: CONTINGENCY 'AEP_P1-2_#5853' OPEN BRANCH FROM BUS 243495 TO BUS 243560 CKT 1 / 243495 05DAVIDS 138 243560 05ROBERT 138 1 END
Note on L38: CONTINGENCY 'AEP_P1-2_#5756' OPEN BRANCH FROM BUS 243471 TO BUS 243560 CKT 2 / 243471 05BETHEL 138 243560 05ROBERT 138 2 END
Note on M38: CONTINGENCY 'AEP_P1-2_#5853' OPEN BRANCH FROM BUS 243495 TO BUS 243560 CKT 1 / 243495 05DAVIDS 138 243560 05ROBERT 138 1 END
Note on L39: CONTINGENCY 'AEP_P1-2_#5756' OPEN BRANCH FROM BUS 243471 TO BUS 243560 CKT 2 / 243471 05BETHEL 138 243560 05ROBERT 138 2 END
Note on M39: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L40: CONTINGENCY 'AEP_P1-2_#727' OPEN BRANCH FROM BUS 243457 TO BUS 243458 CKT 1 / 243457 05HAYDEN 345 243458 05HYATT 345 1 END
Note on M40: CONTINGENCY 'AEP_P1-2_#714' OPEN BRANCH FROM BUS 244022 TO BUS 243457 CKT 1 / 244022 05COLE 345 243457 05HAYDEN 345 1 END
Note on L41: CONTINGENCY 'AEP_P1-2_#727' OPEN BRANCH FROM BUS 243457 TO BUS 243458 CKT 1 / 243457 05HAYDEN 345 243458 05HYATT 345 1 END
Note on M41: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L42: CONTINGENCY 'AEP_P1-2_#727' OPEN BRANCH FROM BUS 243457 TO BUS 243458 CKT 1 / 243457 05HAYDEN 345 243458 05HYATT 345 1 END
Note on M42: CONTINGENCY 'AEP_P1-2_#10137' OPEN BRANCH FROM BUS 243453 TO BUS 244022 CKT 1 / 243453 05BEATTY 345 244022 05COLE 345 1 END
Note on L43: CONTINGENCY 'AEP_P1-2_#10137' OPEN BRANCH FROM BUS 243453 TO BUS 244022 CKT 1 / 243453 05BEATTY 345 244022 05COLE 345 1 END
Note on M43: CONTINGENCY 'AEP_P1-2_#727' OPEN BRANCH FROM BUS 243457 TO BUS 243458 CKT 1 / 243457 05HAYDEN 345 243458 05HYATT 345 1 END
Note on L44: CONTINGENCY 'AEP_P1-3_#4756_05ROBRT2 345_2' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 OPEN BRANCH FROM BUS 243460 TO BUS 243560 CKT 2 / 243460 05ROBRT2 345 243560 05ROBERT 138 2 END
Note on M44: CONTINGENCY 'AEP_P1-3_#3235_05ROBRT1 345_1' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 OPEN BRANCH FROM BUS 243461 TO BUS 243560 CKT 1 / 243461 05ROBRT1 345 243560 05ROBERT 138 1 END
Note on L45: CONTINGENCY 'AEP_P1-3_#4756_05ROBRT2 345_2' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 OPEN BRANCH FROM BUS 243460 TO BUS 243560 CKT 2 / 243460 05ROBRT2 345 243560 05ROBERT 138 2 END
Note on M45: CONTINGENCY 'AEP_P1-2_#3233' OPEN BRANCH FROM BUS 243457 TO BUS 243461 CKT 1 / 243457 05HAYDEN 345 243461 05ROBRT1 345 1 END
Note on L46: CONTINGENCY 'AEP_P1-3_#4756_05ROBRT2 345_2' OPEN BRANCH FROM BUS 243457 TO BUS 243460 CKT 2 / 243457 05HAYDEN 345 243460 05ROBRT2 345 2 OPEN BRANCH FROM BUS 243460 TO BUS 243560 CKT 2 / 243460 05ROBRT2 345 243560 05ROBERT 138 2 END
Note on M46: CONTINGENCY 'AEP_P1-2_#5805' OPEN BRANCH FROM BUS 243499 TO BUS 245230 CKT Z1 / 243499 05DUBLIN1 138 245230 05DUBLIN2 138 Z1 OPEN BRANCH FROM BUS 243499 TO BUS 243566 CKT 1 / 243499 05DUBLIN1 138 243566 05SAWMIL 138 1 END
Note on L47: CONTINGENCY 'AEP_P1-2_#5495' OPEN BRANCH FROM BUS 243241 TO BUS 255164 CKT 1 / 243241 05ALBION 138 255164 17NORTHPORT 138 1 END
Note on L48: CONTINGENCY 'AEP_P1-2_#5495' OPEN BRANCH FROM BUS 243241 TO BUS 255164 CKT 1 / 243241 05ALBION 138 255164 17NORTHPORT 138 1 END
Note on M51: CONTINGENCY 'AEP_P1-2_#5495' OPEN BRANCH FROM BUS 243241 TO BUS 255164 CKT 1 / 243241 05ALBION 138 255164 17NORTHPORT 138 1 END
Note on M54: CONTINGENCY 'AEP_P1-2_#5495' OPEN BRANCH FROM BUS 243241 TO BUS 255164 CKT 1 / 243241 05ALBION 138 255164 17NORTHPORT 138 1 END
Note on L59: CONTINGENCY 'DLC_P11_GEN_15CHSWK1' REMOVE UNIT 1 FROM BUS 254063 END
Note on M59: CONTINGENCY 'DLC_P13_ARSENAL_138' OPEN BRANCH FROM BUS 253998 TO BUS 253999 CKT 1 END
Note on L60: CONTINGENCY 'DLC_P13_ARSENAL_138' OPEN BRANCH FROM BUS 253998 TO BUS 253999 CKT 1 END
Note on M60: CONTINGENCY 'DLC_P11_GEN_15CHSWK1' REMOVE UNIT 1 FROM BUS 254063 END
Note on L61: CONTINGENCY 'ME-P1-3-ME-115-023' /* MIDDLETOWN JUNCTION 23/115KV TRANSFORMER #2 DISCONNECT BRANCH FROM BUS 204598 TO BUS 204595 CKT 1 /* 27MIDD JCT 115 27MJ2 REAC 115 DISCONNECT BRANCH FROM BUS 204504 TO BUS 204595 CKT 2 /* 27MIDD JCT 230 27MJ2 REAC 115 27MIDD J2 13.80 DISCONNECT BUS 204595 /* 27MJ2 REAC 115 END
Note on M61: CONTINGENCY 'ME-P1-2-ME-230-214T' /* MIDDLETOWN JUNCTION 230/115 KV TRANSFORMER #5 FAULT DISCONNECT BRANCH FROM BUS 204598 TO BUS 204596 CKT 1 /* 27MIDD JCT 115 27MJ5 REAC 115 DISCONNECT BRANCH FROM BUS 204709 TO BUS 204596 TO BUS 204592 CKT 5/* 27MIDDJCT8 230 27MJ5 REAC 115 27MIDD J5 13.80 DISCONNECT BUS 204592 /* 27MIDD J5 14 DISCONNECT BUS 204596 /* 27MJ5 REAC 115 END
Note on L62: CONTINGENCY 'ME-P1-2-ME-230-214T' /* MIDDLETOWN JUNCTION 230/115 KV TRANSFORMER #5 FAULT DISCONNECT BRANCH FROM BUS 204598 TO BUS 204596 CKT 1 /* 27MIDD JCT 115 27MJ5 REAC 115 DISCONNECT BRANCH FROM BUS 204709 TO BUS 204596 TO BUS 204592 CKT 5/* 27MIDDJCT8 230 27MJ5 REAC 115 27MIDD J5 13.80 DISCONNECT BUS 204592 /* 27MIDD J5 14 DISCONNECT BUS 204596 /* 27MJ5 REAC 115 END
Note on M62: CONTINGENCY 'ME-P1-3-ME-115-023' /* MIDDLETOWN JUNCTION 23/115KV TRANSFORMER #2 DISCONNECT BRANCH FROM BUS 204598 TO BUS 204595 CKT 1 /* 27MIDD JCT 115 27MJ2 REAC 115 DISCONNECT BRANCH FROM BUS 204504 TO BUS 204595 CKT 2 /* 27MIDD JCT 230 27MJ2 REAC 115 27MIDD J2 13.80 DISCONNECT BUS 204595 /* 27MJ2 REAC 115 END
Note on L65: CONTINGENCY 'EKPC_P1-2_GRE-TAY-MAR161' /* GREEN CO - KU TAYLOR CO - MARION CO OPEN BRANCH FROM BUS 342733 TO BUS 342817 CKT 1 /* 342733 5GREEN CO 161.00 342817 5TAYLOR CO J161.00 OPEN BRANCH FROM BUS 342805 TO BUS 342817 CKT 1 /* 342805 5SALOMA T 161.00 342817 5TAYLOR CO J161.00 OPEN BRANCH FROM BUS 342802 TO BUS 342805 CKT 1 /* 342802 5SALOMA 161.00 342805 5SALOMA T 161.00 OPEN BRANCH FROM BUS 342775 TO BUS 342805 CKT 1 /* 342775 5MARION IP T161.00 342805 5SALOMA T 161.00 OPEN BRANCH FROM BUS 342772 TO BUS 342775 CKT 1 /* 342772 5MARION IP 161.00 342775 5MARION IP T161.00 OPEN BRANCH FROM BUS 342769 TO BUS 342775 CKT 1 /* 342769 5MARION CO 161.00 342775 5MARION IP T161.00 END
Note on L66: CONTINGENCY 'EKPC_P1-2_GRE-TAY-MAR161' /* GREEN CO - KU TAYLOR CO - MARION CO OPEN BRANCH FROM BUS 342733 TO BUS 342817 CKT 1 /* 342733 5GREEN CO 161.00 342817 5TAYLOR CO J161.00 OPEN BRANCH FROM BUS 342805 TO BUS 342817 CKT 1 /* 342805 5SALOMA T 161.00 342817 5TAYLOR CO J161.00 OPEN BRANCH FROM BUS 342802 TO BUS 342805 CKT 1 /* 342802 5SALOMA 161.00 342805 5SALOMA T 161.00 OPEN BRANCH FROM BUS 342775 TO BUS 342805 CKT 1 /* 342775 5MARION IP T161.00 342805 5SALOMA T 161.00 OPEN BRANCH FROM BUS 342772 TO BUS 342775 CKT 1 /* 342772 5MARION IP 161.00 342775 5MARION IP T161.00 OPEN BRANCH FROM BUS 342769 TO BUS 342775 CKT 1 /* 342769 5MARION CO 161.00 342775 5MARION IP T161.00 END
Note on L67: CONTINGENCY 'EKPC_P1-2_TAYL J-KU TAYL 161' OPEN BRANCH FROM BUS 342817 TO BUS 325921 CKT 1 /* 342817 5TAYLOR CO J 325921 5TAYLOR CO END
Note on L68: CONTINGENCY 'EKPC_P1-2_TAYL J-KU TAYL 161' OPEN BRANCH FROM BUS 342817 TO BUS 325921 CKT 1 /* 342817 5TAYLOR CO J 325921 5TAYLOR CO END
Note on M69: CONTINGENCY 'EKPC_P1-2_GRE-TAY-MAR161' /* GREEN CO - KU TAYLOR CO - MARION CO OPEN BRANCH FROM BUS 342733 TO BUS 342817 CKT 1 /* 342733 5GREEN CO 161.00 342817 5TAYLOR CO J161.00 OPEN BRANCH FROM BUS 342805 TO BUS 342817 CKT 1 /* 342805 5SALOMA T 161.00 342817 5TAYLOR CO J161.00 OPEN BRANCH FROM BUS 342802 TO BUS 342805 CKT 1 /* 342802 5SALOMA 161.00 342805 5SALOMA T 161.00 OPEN BRANCH FROM BUS 342775 TO BUS 342805 CKT 1 /* 342775 5MARION IP T161.00 342805 5SALOMA T 161.00 OPEN BRANCH FROM BUS 342772 TO BUS 342775 CKT 1 /* 342772 5MARION IP 161.00 342775 5MARION IP T161.00 OPEN BRANCH FROM BUS 342769 TO BUS 342775 CKT 1 /* 342769 5MARION CO 161.00 342775 5MARION IP T161.00 END
Note on M70: CONTINGENCY 'EKPC_P1-2_TAYL J-KU TAYL 161' OPEN BRANCH FROM BUS 342817 TO BUS 325921 CKT 1 /* 342817 5TAYLOR CO J 325921 5TAYLOR CO END
Note on L71: CONTINGENCY 'DVP_P1-2: LN 2172' OPEN BRANCH FROM BUS 313863 TO BUS 314171 CKT 1 /* 6YARDLEY 230.00 - 6BRAMBL 230.00 END
Note on M71: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 END
Note on L72: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 END
Note on M72: CONTINGENCY 'DVP_P1-2: LN 2172' OPEN BRANCH FROM BUS 313863 TO BUS 314171 CKT 1 /* 6YARDLEY 230.00 - 6BRAMBL 230.00 END
Note on L73: CONTINGENCY 'DVP_P1-2: LN 2095' OPEN BRANCH FROM BUS 313805 TO BUS 313863 CKT 1 /* 6SHELLHORN1 230.00 - 6YARDLEY 230.00 END
Note on M73: CONTINGENCY 'DVP_P1-2: LN 274' OPEN BRANCH FROM BUS 314004 TO BUS 314010 CKT 1 /* 6ASHBURN 230.00 - 6BEAMEAD 230.00 OPEN BRANCH FROM BUS 314004 TO BUS 314072 CKT 1 /* 6ASHBURN 230.00 - 6PL VIEW 230.00 OPEN BUS 314004 /* ISLAND: 6ASHBURN 230.00 OPEN BUS 314354 /* ISLAND: 6ASHBURN_2 230.00 OPEN BUS 314359 /* ISLAND: 6ASHBU_1 230.00 END

## Sum N-1-1 Voltage Mag
PJM N-1-1 Voltage Magnitude Results (2024 Summer)
FG# | Bus # | Bus Name | Base kV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | Orig Case Cont Volt | Base Volt | Cont Volt | PJM Accepting Proposals | Comment
N2-SVM1 | 237320 | 01VANVL | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9338 | 0.9629 | 0.8988 | Yes
N2-SVM2 | 235499 | 01OPEQUN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9294 | 0.975 | 0.8994 | Yes
N2-SVM3 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9619 | 0.9632 | 0.9046 | Yes
N2-SVM4 | 235477 | 01INWOOD | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9438 | 0.961 | 0.9047 | Yes
N2-SVM5 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-042 | 0.9674 | 0.9632 | 0.9117 | Yes
N2-SVM6 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-020 | 0.9604 | 0.9632 | 0.9174 | Yes
N2-SVM7 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-018 | AP-P1-2-PE-138-041 | 0.9634 | 0.9631 | 0.9179 | Yes
N2-SVM8 | 237320 | 01VANVL | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.9629 | 0.9338 | 0.8989 | Yes
N2-SVM9 | 235499 | 01OPEQUN | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.975 | 0.9294 | 0.8994 | Yes
N2-SVM10 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-020 | AP-P1-2-PE-138-018 | 0.9632 | 0.9604 | 0.9175 | Yes
N2-SVM11 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.9632 | 0.9619 | 0.901 | Yes
N2-SVM12 | 235471 | 01GORE | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-041 | AP-P1-2-PE-138-018 | 0.9631 | 0.9634 | 0.9151 | Yes
N2-SVM13 | 235512 | 01STONEW | 138 | 201 | 0.92 | 1.05 | AP-P1-2-PE-138-042 | AP-P1-2-PE-138-018 | 0.9632 | 0.9674 | 0.9161 | Yes
N2-SVM14 | 244745 | 05BABBITT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.963 | 0.9758 | 0.8999 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM15 | 244745 | 05BABBITT | 138 | 205 | 0.92 | 1.05 | AEP_P1-3_#8593_05JUG ST 345_5 | AEP_P1-2_#11360 | 0.9758 | 0.963 | 0.8999 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM16 | 243789 | 05FACEBOOK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.963 | 0.9758 | 0.8999 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM17 | 243789 | 05FACEBOOK | 138 | 205 | 0.92 | 1.05 | AEP_P1-3_#8593_05JUG ST 345_5 | AEP_P1-2_#11360 | 0.9758 | 0.963 | 0.8999 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM18 | 246383 | 05FOXGLOVE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.9646 | 0.9781 | 0.8985 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM19 | 246383 | 05FOXGLOVE | 138 | 205 | 0.92 | 1.05 | AEP_P1-3_#8593_05JUG ST 345_5 | AEP_P1-2_#11360 | 0.9781 | 0.9646 | 0.8985 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM20 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.9646 | 0.9781 | 0.8985 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM21 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-3_#8593_05JUG ST 345_5 | AEP_P1-2_#11360 | 0.9781 | 0.9646 | 0.8985 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM22 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.9646 | 0.9781 | 0.8985 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM23 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-3_#8593_05JUG ST 345_5 | AEP_P1-2_#11360 | 0.9781 | 0.9646 | 0.8985 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVM24 | 243334 | 05MAGLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#8002 | AEP_SUBT_P1-3_#786_05JAY 138_1 | 0.9813 | 0.9815 | 0.9076 | No | Will be addressed by a baseline upgrade B3103 which was presented at the 2/20/2019 Western SRRTEP
N2-SVM25 | 243334 | 05MAGLEY | 138 | 205 | 0.92 | 1.05 | AEP_SUBT_P1-3_#786_05JAY 138_1 | AEP_P1-2_#8002 | 0.9815 | 0.9813 | 0.9077 | No | Will be addressed by a baseline upgrade B3103 which was presented at the 2/20/2019 Western SRRTEP
N2-SVM26 | 243237 | 05ADAM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#8002 | AEP_SUBT_P1-3_#786_05JAY 138_1 | 0.9739 | 0.9876 | 0.9053 | No | Will be addressed by a baseline upgrade B3103 which was presented at the 2/20/2019 Western SRRTEP
N2-SVM27 | 243237 | 05ADAM | 138 | 205 | 0.92 | 1.05 | AEP_SUBT_P1-3_#786_05JAY 138_1 | AEP_P1-2_#8002 | 0.9876 | 0.9739 | 0.9053 | No | Will be addressed by a baseline upgrade B3103 which was presented at the 2/20/2019 Western SRRTEP
N2-SVM28 | 242792 | 05SCOTSV | 138 | 205 | 0.92 | 1.05 | DVP_P1-2: LN 1030 | DVP_P1-3: 6BREMO-TX#9 | 0.9893 | 0.9913 | 0.8806 | No | Not a valid violation.
N2-SVM29 | 242792 | 05SCOTSV | 138 | 205 | 0.92 | 1.05 | DVP_P1-3: 6BREMO-TX#9 | DVP_P1-2: LN 1030 | 0.9916 | 0.9893 | 0.8806 | No | Not a valid violation.
Version: | 12
|  | Note: |  | Solved by existing RTEP project

## Sum N-1-1 Voltage Drop
PJM N-1-1 Voltage Drop Results (2024 Summer)
FG# | Bus # | Bus Name | Base kV | Area | %Vdrop Limit | Contingency 1 | Contingency 2 | Orig Case Cont Volt | Base Volt | Cont Volt | %Vdrop | PJM Accepting Proposals | Comment
N2-SVD1 | 206307 | 28RED BANK | 230 | 228 | 8 | JC-P1-2-JCC-230-005 | JC-P1-2-JCC-230-006 | 1.0075 | 1.0046 | 0.8387 | 16.586 | No | The violation is related to the cancelation of the B1690 (MCRP) and Alternatives are under evaluation
N2-SVD2 | 206307 | 28RED BANK | 230 | 228 | 8 | JC-P1-2-JCC-230-006 | JC-P1-2-JCC-230-005 | 1.0059 | 1.0074 | 0.828 | 17.939 | No | The violation is related to the cancelation of the B1690 (MCRP) and Alternatives are under evaluation
N2-SVD3 | 246383 | 05FOXGLOVE | 138 | 205 | 8 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.9644 | 0.9781 | 0.8949 | 8.314 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVD4 | 242670 | 05HOLST2 | 138 | 205 | 8 | AEP_P1-2_#5684 | AEP_P1-2_#5700 | 0.9527 | 1.0086 | 0.9258 | 8.274 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD5 | 242670 | 05HOLST2 | 138 | 205 | 8 | AEP_P1-2_#5689 | AEP_P1-2_#5700 | 0.9527 | 1.0015 | 0.8409 | 16.064 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD6 | 242670 | 05HOLST2 | 138 | 205 | 8 | AEP_P1-2_#5662 | AEP_P1-2_#5700 | 0.9527 | 0.9984 | 0.9101 | 8.835 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD7 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.9644 | 0.9781 | 0.8949 | 8.316 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVD8 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#11360 | AEP_P1-3_#8593_05JUG ST 345_5 | 0.9644 | 0.9781 | 0.8949 | 8.314 | No | The violation is caused by the new load which is part of AEP-2018-OH002, the AEP-2018-OH002 solution will solve this issue
N2-SVD9 | 242722 | 05MORLAN | 138 | 205 | 8 | AEP_P1-2_#5662 | AEP_P1-2_#5700 | 0.9533 | 0.9973 | 0.9122 | 8.513 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD10 | 244508 | 05RIGGS | 138 | 205 | 8 | AEP_P1-2_#5689 | AEP_P1-2_#5700 | 0.9582 | 1.0049 | 0.8501 | 15.476 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD11 | 242819 | 05SULVN | 138 | 205 | 8 | AEP_P1-2_#5689 | AEP_P1-2_#5700 | 0.9585 | 1.0051 | 0.8507 | 15.443 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD12 | 245222 | 05W.KINGS_BP | 138 | 205 | 8 | AEP_P1-2_#5662 | AEP_P1-2_#5700 | 0.9571 | 0.9984 | 0.9183 | 8.012 | No | Will be addressed by a baseline upgrade B3099 which was presented at the 2/20/2019 Western SRRTEP
N2-SVD13 | 243237 | 05ADAM | 138 | 205 | 8 | AEP_P1-2_#8002 | AEP_SUBT_P1-3_#786_05JAY 138_1 | 0.9732 | 0.9876 | 0.9029 | 8.468 | No | Will be addressed by a baseline upgrade B3103 which was presented at the 2/20/2019 Western SRRTEP
Version: | 12
|  | Note: |  | Solved by existing RTEP project

## Sum Load Deliv
None

## Sum N-1-1 Not Converged (hidden)
N-2 AC Analysis Not Converged
Date & Time: Tue May 21 15:18:07 2019
Base Case: T:\rtep\Base2024\N-1-1\Thermal\2019RTEP 2024SUM Non-FSA_05142019.sav
Subsystem: T:\rtep\Base2024\N-1-1\Thermal\2019 Series 2024_Rev7 N-1-1.sub
None