## Sum
2022 Multi-Driver Proposal Window 1 PJM Generator Deliverability Result (Summer)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rating | DC Final Flow | AC Final Flow | Final DC %LD | Final AC %LD | Cont Name | ContType | Conductor Rating (MVA) | PJM Accepting Proposals | Comments
MDW1-GD-S1620 | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 1075 | 1143.2 | 1143.4 | 106.34 | 106.36 | AEP_P4_#2978_05DUMONT 765_B_SRT-A | Breaker | 1408/1887/1780/2143 for SN/SE/WN/WE for PJM side | Yes | Limited by PJM side