## Win
2022 Multi-Driver Proposal Window 1 PJM Generator Deliverability Result (Winter)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rating | DC Final Flow | AC Final Flow | Final DC %LD | Final AC %LD | Cont Name | ContType | WSTE Rating (MVA) | Conductor Ratings (MVA) | PJM Accepting Proposals | Comments
MDW1-GD-W172 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1917.6 | 1984.6 | 115.7% | 119.7% | AEP_P1-2_#695_1681_SRT-A | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W171 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1917.6 | 1983.1 | 115.7% | 119.6% | 765-L11215__-S_SRT-A | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W188 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1768.6 | 1800.1 | 106.7% | 108.6% | COMED_P4_112-65-BT4-5___SRT-A | Breaker | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W190 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1768.4 | 1799.9 | 106.7% | 108.6% | COMED_P4_112-65-BT3-4___SRT-A | Breaker | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W185 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1767.6 | 1799.2 | 106.6% | 108.5% | AEP_P4_#2978_05DUMONT 765_B_SRT-A | Breaker | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W332 | 270728 | E FRANKFO; B | 274750 | CRETE EC ;BP | 1 | 345 | 222 | 1658 | 1748.8 | 1788.4 | 105.5% | 107.9% | AEP_P1-2_#695_1681_SRT-A | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list.
MDW1-GD-W331 | 270728 | E FRANKFO; B | 274750 | CRETE EC ;BP | 1 | 345 | 222 | 1658 | 1748.8 | 1787.8 | 105.5% | 107.8% | 765-L11215__-S_SRT-A | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list.
MDW1-GD-W309 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1310 | 1448.4 | 1495.4 | 110.6% | 114.2% | Base Case | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W404 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1650.1 | 1705.5 | 99.52% | 102.9% | COMED_P1-2_345-L17703_R-S_SRT-A | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W419 | 274750 | CRETE EC ;BP | 255112 | 17STJOHN | 1 | 345 | 217/222 | 1658 | 1627.8 | 1675.2 | 98.18% | 101% | 765-L11216__-S_SRT-A | Single | 1658 | WN/WLTE/WSTE = 1310/1557/1658 for PJM; WN/WE = 1310/1772 for MISO | Yes | For this FG, WSTE is applied. Exelon owned facilities are included in Exelon's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2631.
MDW1-GD-W392 | 274804 | UNIV PK N;RP | 243229 | 05OLIVE | 1 | 345 | 205/222 | 1234 | 1227.1 | 1258.1 | 99.44% | 102% | AEP_P1-2_#695_1681_SRT-A | Single |  | SN/SE/WN/WE = 971/1418/1234/1584 for AEP owned portion. WN/WLTE/WSTE = 1310/1557/1658 for ComEd owned portion. WN/WLTE/WSTE = 1310/1310/1373 for NEET owned portion. | Yes | Exelon owned facilities are included in Exelon's EOL candidate list. AEP owned facilities are included in AEP's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2509.
MDW1-GD-W393 | 274804 | UNIV PK N;RP | 243229 | 05OLIVE | 1 | 345 | 205/222 | 1234 | 1227.1 | 1257.5 | 99.44% | 101.9% | 765-L11215__-S_SRT-A | Single |  | SN/SE/WN/WE = 971/1418/1234/1584 for AEP owned portion. WN/WLTE/WSTE = 1310/1557/1658 for ComEd owned portion. WN/WLTE/WSTE = 1310/1310/1373 for NEET owned portion. | Yes | Exelon owned facilities are included in Exelon's EOL candidate list. AEP owned facilities are included in AEP's EOL candidate list. NEET owned facilities are being rebuilt/reconductored through supplemental project s2509.