## Slide 1: Single Line Diagram (SLD) Guidance for Open Window Submittals
Jeffrey Goldberg, PE, Senior Engineer, Transmission Planning
Transmission Expansion Advisory Committee
June 06, 2023

## Slide 2: SLD - Guidance for Open Window Submittals
PJM typically receives many project proposals whenever a competitive window is open. The process of selecting a winning proposal includes PJM Transmission Planning modeling each project and subsequently performing reliability analysis.
Single Line Diagrams are critical for communicating the proposal:
  Validating the modeling (idv files) for accurate incorporation to the study case
    Facilities to be Removed, Added, Modified
  Validating changes to the Contingency Sets
    Contingency Definitions to be Removed, Added, Modified
  Understanding the sequencing of project phases
    Existing System Topology - showing those facilities relevant to the proposed project
    Post In-service Topology – resultant topology after each project phase

## Slide 3
230 kV
115 kV
115 kV
115 kV
Grape
Filbert
Apple
Existing Conditions
To BANANA
To CARROT
To DILL
To EGGPLANT
230 kV
To CARROT
To Be Removed

## Slide 4
230 kV
115 kV
115 kV
Grape
Filbert
Apple
Phase 1
To BANANA
To CARROT
To DILL
To EGGPLANT
230 kV
230 kV
To CARROT
Common Tower
115 kV

## Slide 5
230 kV
115 kV
115 kV
115 kV
Grape
Filbert
Apple
Phase 2
To BANANA
To CARROT
To DILL
To EGGPLANT
230 kV
230 kV
NO*
To CARROT
Common Tower
*Normally Open

## Slide 6
230 kV
115 kV
115 kV
115 kV
Grape
Filbert
Apple
Phase Final
To BANANA
To CARROT
To DILL
To EGGPLANT
230 kV
230 kV
NO*
To CARROT
Common Tower
*Normally Open

## Slide 7: SLD Guidance - Conclusion
Proposing entities may use their own graphics on submitted SLDs
For optimal communication and clarity:
  SLD of Existing System
    Only show facilities relevant to the project.
    Identify facilities to be removed in the subsequent project phase. These facilities will be missing in subsequent SLD
  SLD of Intermediate Project Phase
    All facilities installed from a previous project phase should be represented the same as existing facilities (Normal Weight)
    Ensure all facilities identified for removal from a previous project phase are missing
    Identify all facilities added in the current project phase (Heavy Weight)
    Identify facilities to be removed in the subsequent project phase.
    Include graphic to facilitate validation of Contingency definitions (i.e. Common Tower, breaker diagrams, etc.)
  SLD of Final Project Phase
    Identify all facilities added for all project phases (Heavy Weight)

## Slide 8: Contingency Naming Convention
Sang Hoang, Engineer
System Planning Modeling & Support
Transmission Expansion Advisory Committee
June 06, 2023

## Slide 9: What we need from TOs
For each RTEP study year, six (6) contingency files are required. The common names of these six contingency files and the associated NERC TPL contingency definitions are shown in the table below:
PJM File Name | TPL-001-5 Contingencies
Single | P1 (All)
P_2-1 | P2.1
Bus | P2.2
Line_FB | P2.3, P2.4 P4 (All)
P5 | P5
Tower | P7(All)

## Slide 10: Contingency Title Naming Convention
1. Standard Format
  PJM has identified a specific naming standard convention to contingencies. This is necessary to be able to sort on contingencies that apply to certain seasons and assist in the consolidation of all contingency files into one (1) yearly set per contingency type.
  Below is an example of the standard format:
  “Company Name” _ “TPL Number” - “Sub Number Remainder of Contingency Title” _ “Sort” - ”Seasonal Restricted”
Notes: Contingency naming (where it states “Sub Number Remainder of Contingency Title”) is largely up to the transmission owner. PJM requires that the contingency name begins with the submitting company’s acronym (ID as defined in the ERAG MMWG Procedure Manual), followed by the contingency type in a consistent manner.
Additional considerations:
Contingency title names are limited to 128 characters
Special characters (@,$,%,*,commas, etc.) should not be used
Duplicate contingency names are not allowed and will be flagged as an error which must be corrected
Contingency names are enclosed in single quotes (aka apostrophes) (‘). Apostrophes are not allowed within the contingency name, as the name will be truncated

## Slide 11: Contingency Title Naming Convention
2. Seasonal Consideration and Sorting
  To maintain all different seasonal contingencies within a yearly contingency case, contingency titles will require a standard adder to providing sorting capability.
Command for Cont. | Command for Cont.
_SRT-A | _SORT-ALL
_SRT-S | _SORT-SUM
_SRT-W | _SORT-WIN
_SRT-L | _SORT-LL
_SRT-SL | _SORT-SUM & LL
_SRT-WL | _SORT-WIN & LL
_SRT-SW | _SORT-SUM & WIN
Notes: Contingency naming (where it states “Sub Number Remainder of Contingency Title”) is largely up to the transmission owner. PJM requires that the contingency name begins with the submitting company’s acronym (ID as defined in the ERAG MMWG Procedure Manual), followed by the contingency type in a consistent manner.
Additional considerations:
Contingency title names are limited to 128 characters
Special characters (@,$,%,*,commas, etc.) should not be used
Duplicate contingency names are not allowed and will be flagged as an error which must be corrected
Contingency names are enclosed in single quotes (aka apostrophes) (‘). Apostrophes are not allowed within the contingency name, as the name will be truncated

## Slide 12: Contingency Title Naming Convention
3. Contingency File Naming Convention
  Below are several examples of valid contingency names:
    AP_P1-1_MP-138-513_SRT-S
    ATSI_P1-2_OEC-69-010_SRT-A
    AEP_P1-2_#5522_SRT-L
    CE_P4_207-38-L4606N_SRT-A
    DVP_P7-1_LN 46-74_SRT-SW
    ME_P2-2_ME-115-022T_SRT-W
Notes: Contingency naming (where it states “Sub Number Remainder of Contingency Title”) is largely up to the transmission owner. PJM requires that the contingency name begins with the submitting company’s acronym (ID as defined in the ERAG MMWG Procedure Manual), followed by the contingency type in a consistent manner.
Additional considerations:
Contingency title names are limited to 128 characters
Special characters (@,$,%,*,commas, etc.) should not be used
Duplicate contingency names are not allowed and will be flagged as an error which must be corrected
Contingency names are enclosed in single quotes (aka apostrophes) (‘). Apostrophes are not allowed within the contingency name, as the name will be truncated

## Slide 13: Contingency Title Naming Convention
4. Contingency File Naming Convention
  PJM requires consistent naming of the .con files to assist when compiling the various contingency files from the different members together. Below is the standard for naming contingency files.
RTEP-SSSS_YYYY_ CCCC_TTTT_RR
Legend for the format above where:
 S = RTEP Series Year
 Y = Case Year
 C = Company
 T = Type (Tower, Single, Line_FB, Bus, P_2-1, P5)
 R = Revision (Start at Revision 0)
Notes: Contingency naming (where it states “Sub Number Remainder of Contingency Title”) is largely up to the transmission owner. PJM requires that the contingency name begins with the submitting company’s acronym (ID as defined in the ERAG MMWG Procedure Manual), followed by the contingency type in a consistent manner.
Additional considerations:
Contingency title names are limited to 128 characters
Special characters (@,$,%,*,commas, etc.) should not be used
Duplicate contingency names are not allowed and will be flagged as an error which must be corrected
Contingency names are enclosed in single quotes (aka apostrophes) (‘). Apostrophes are not allowed within the contingency name, as the name will be truncated

## Slide 14: Contingency Change & Idev File Submissions
Julia Spatafore, Sr. Engineer
Transmission Planning
Transmission Expansion Advisory Committee
June 06, 2023

## Slide 15: Contingency Changes
Currently, PJM receives contingency changes in multiple formats:
  Text file, excel, word
  Deletions, additions, modifications
  All in one file vs. separate files
PJM is looking to standardize the submission of contingency changes to minimize confusion and any potential errors:
  Submit contingency changes using the provided “Contingency Change Submission” template
  Follow the contingency naming convention as described in previous section
  Use unique contingency names (i.e. no duplicate contingencies)
  Use ‘delete’ and ‘add’ methodology in template to represent contingency modifications

## Slide 16: Contingency Changes
New Contingencies
Deleted Contingencies
Modified Contingencies – 1:1 Replacements
Delete | Add
N/A | CONTINGENCY 'PJM_P1-2_BUS1_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####2 CKT 1 /* BUS 1 138 TO BUS 2 138 END
Delete | Add
CONTINGENCY 'PJM_P1-2_BUS1_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####2 CKT 1 /* BUS 1 138 TO BUS 2 138 END | N/A
Delete | Add
CONTINGENCY 'PJM_P1-2_BUS1_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####1TO BUS #####2 CKT 1 /* BUS 1 138 TO BUS 2 138 END | CONTINGENCY 'PJM_P1-2_BUS1_BUS3_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####3 CKT 1 /* BUS 1 138 TO BUS 3 138 END

## Slide 17: Contingency Changes
Modified Contingencies – 1:2 (or more) Replacements  Merge the “Delete” cells
Modified Contingencies – 2 (or more):1 Replacements  Merge the “Add” cells
Delete | Add
CONTINGENCY 'PJM_P1-2_BUS1_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####2 CKT 1 /* BUS 1 138 TO BUS 2 138 END | CONTINGENCY 'PJM_P1-2_BUS1_BUS3_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####3 CKT 1 /* BUS 1 138 TO BUS 3 138 END
 | CONTINGENCY 'PJM_P1-2_BUS3_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####3 TO BUS #####2 CKT 1 /* BUS 3 138 TO BUS 2 138 END
Delete | Add
CONTINGENCY 'PJM_P1-2_BUS1_BUS3_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####3 CKT 1 /* BUS 1 138 TO BUS 3 138 END | CONTINGENCY 'PJM_P1-2_BUS1_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####1 TO BUS #####2 CKT 1 /* BUS 1 138 TO BUS 2 138 END
CONTINGENCY 'PJM_P1-2_BUS3_BUS2_SRT-A' DISCONNECT BRANCH FROM BUS #####3 TO BUS #####2 CKT 1 /* BUS 3 138 TO BUS 2 138 END | 

## Slide 18: Idev Files
PJM is looking to standardize the submission of idev files to minimize confusion and any potential errors:
  Add comments inside the idev file to clearly show/explain the changes being made
  Include only commands that change the model (i.e. no BAT_GEXMBUS, BAT_FDNS, etc.)
  In the first line of the idev, add the following:
    Idev creations date
    RTEP case year
  Include the applicable season that the idev is applicable to in the file name (WIN, SUM, LL, or All)
Only commands that change the model, with comments explaining the change
Include RTEP year
Include creation date
Applicable season in file name

## Slide 19: Contact
Facilitator: David Souder, David.Souder@pjm.com
Secretary: Tarik Bensala, Tarik.Bensala@pjm.com
SME/Presenter: Jeffrey Goldberg, Jeffrey.Goldberg@pjm.com
Sang Hoang, Sang.Hoang@pjm.com
Julia Spatafore, Julia.Spatafore@pjm.com
Member Hotline
(610) 666 – 8980
(866) 400 – 8980
custsvc@pjm.com

## Slide 20: Revision History
V1 – 06/02/2023 – Original slides posted