7/02/2025

- TO Area update:

  - APS:

    - The following two NEET contingency modification files include three Line FB CON updates for 2030 and two line FB CON updates for 2032 RTEP cases:

      - Contingency Change_NEET_06262025_2030_all_seasons.xlsx

      - Contingency Change_NEET_06262025_2032_all_seasons.xlsx

  - AEP:

    - Flowgate # 2025W1-GD-S210 is caused by the contribution from deactivated generators, therefore it is removed from competitive window.

    - AEP provided updated ratings for Genoa transformer, see Correct_Genoa_TR1_Ratings_SUM_LL.idv and Correct_Genoa_TR1_Ratings_WIN.idv. With the correction, the following flowgates will be removed:

      - 2025-W1-N1-ST9, 2025-W1-N1-ST10, and 2025-W1-N1-ST18 through ST22

      - 2025-W1-N1-WT13 through WT15

    - AEP provided updated ratings for Harrison – Zuber 138kV line, see Correct_Harrison-Zuber_138kV_Ratings_SUM_LL.idv and Correct_Harrison-Zuber_138kV_Ratings_WIN.idv. With the correction, the following flowgates will be removed:

      - 2025W1-GD-S460, 2025W1-GD-S176, 2025W1-GD-S179, and 2025W1-GD-S471

    - Per AEP, the failure of B1 at Marysville is correctly defined as the contingency “AEP_P4_#707_05MARYSV 765_B1_SRT-A”, thus the 2032 case contingency “AEP_P4_#707_05MARYSV 765_B1-2_SRT-A” will be removed. No flowgate removed.

    - AEP provided an update of the ratings for RP Mone-Maddox 345kV, see RP Mone-Maddox 345kV Winter Rating Update.idv. the following FG was removed:

      - 2025-W1-GD-W234

    - Per NextEra Energy initiated, AEP confirmed, a contingency regarding a 2nd transformer was added 'AEP_P1-3_#05VASSEL 765_2_SRT-A'. No flowgate added.

  - PEPCO / DOM

    - PEPCO provided updated conductor ratings on their end of the Tie Line from Possum – Burches Hill in the 2032 Case, the following flowgates will be removed:

      - 2025W1-32GD-S80, 2025W1-32GD-S102, and 2025W1-32GD-S116

    - DOM provided the following updates for both the 2030 & 2032 Cases that are applicable to all seasons: Updated impedance values for the Goose Creek Transformer #1, updated impedance values for the Bristers – Yeat & Yeat – Ox 500kV lines, updated ratings for the Yeat – Vint Hill 500kV line, updated impedance values for the Joshua Falls – Yeat 765kV line, updated contingencies for Kraken 230kV, and removal of a P-4 Contingency

      - DOM_Bristers_Yeat_Ox_ImpedanceCorrection.idv, DOM_Contingency Change Submission - Kraken 230kV_2030.xlsx, DOM_Contingency Change Submission - Kraken 230kV_2032.xlsx, DOM_GooseCreek_TX1_ ImpedanceCorrection_all_seasons.idv, DOM_Yeat-Vint Hill 500kV LL.idv, DOM_Yeat-Vint Hill 500kV SUM.idv, DOM_Yeat-Vint Hill 500kV WIN.idv, Dominion_Contingency_Edits_SUM_WIN_LL_062025.xlsx, Joshua Falls-Yeat-765kV line_Impedance Update_LL v2.idv, Joshua Falls-Yeat-765kV line_Impedance Update_SUM v2.idv, Joshua Falls-Yeat-765kV line_Impedance Update_WIN v2.idv

    - DOM provided the following updates for the 2032 Case: Updated ratings and impedance values for Carson – Rogers Road 500kV, Updated contingencies for only the SUM season

      - DOM_Carson-Rogers Road 500kV LL 2032.idv, DOM_Carson-Rogers Road 500kV SUM 2032.idv, DOM_Carson-Rogers Road 500kV WIN 2032.idv, Dominion_Contingency_Edits_SUM_2032_062425.xlsx

    - The following flowgates will be removed:

      - 2025W1-32GD-S88, 2025W1-32GD-S105, 2025W1-32GD-S118, 2025W1-32GD-S129, 2025W1-32GD-S142, 2025W1-32GD-S144, 2025W1-32GD-S155

    - The following flowgates have been added:

      - 2025W1-32GD-S1NEW, 2025W1-32GD-S2NEW, 2025W1-32GD-S3NEW, 2025W1-32GD-S4NEW, 2025W1-32GD-S5NEW, 2025W1-32GD-S6NEW, 2025W1-32GD-S7NEW, 2025W1-32GD-S8NEW, 2025W1-GD-LL1NEW, 2025W1-N1-LLVM1NEW, 2025W1-N1-LLVM2NEW

  - PSEG

    - PJM incorrectly labeled Hillsdale as N-1-1 Voltage Drop violations, these have been corrected and removed the following flowgate:

      - 2025W1-N11-SVD217013

    - PJM incorrectly labeled Prospect – North Pat 69kV Summer IPD violations as excluded for “Substation Equipment Exclusion”. This has been updated to be “Reliability Violations on Transmission Facilities Below 200 kV exclusion”

  - General:

    - A number of winter and light load seasonal specific contingencies were missing from the original 2032 line stuck breaker contingency files. These have been appended at the end of the file in a section called “6/30/2025 Additional contingencies”. The following flowgates have been added to the 2032 LL gen deliv results:

      - 2025W1-32GD-LL63 through 2025W1-32GD-LL76

    - The 2032 Winter P2-1 Contingency file was updated due to a Syntax error.

    - The 2030 IPD first layer contingency files are added.

    - All the changes mentioned in this document are applicable to 2032 Scenario 4 cases too.