## Notes
Thermal analysis column headings
Column Heading | Title | Description
Reserved(FG# assinged by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Fr Bus | From Bus Number | PSSE model bus number corresponding to the FROM bus of a facility identified as a potential violation
Fr Name | From Bus Name | PSSE model bus name corresponding to the FROM bus of a facility identified as a potential violation
To Bus | To Bus Number | PSSE model bus number corresponding to the TO bus of a facility identified as a potential violation
To Name | To Bus Name | PSSE model bus name corresponding to the TO bus of a facility identified as a potential violation
Tert Bus | Tertiary Bus Number | PSSE model bus number corresponding to the tertiary bus of a facility identified as a potential violation
Tert Name | Tertiary Bus Name | PSSE model bus name corresponding to the tertiary bus of a facility identified as a potential violation
CKT | Circuit | Circuit number of identified potential violation
KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Rating | Facility Rating | Applicable thermal rating (MVA) of facility
DC Ld(%) | Direct Current Loading percentage | Percentage above Line Rating determined from DC testing
AC Ld(%) | Alternating Current Loading percentage | Percentage above Line Rating determined from AC testing
Cont Type | Contingency Type | N-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Conductor Rating (MVA) | Conductor Rating | Normal/Long Term Emergency/Short Term Emergency/Load Dump ratings of conductor
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Magnitude analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Upper/Lower Limit | High/Low Voltage Limit (P.U.) | Threshold of Per Unit High/Low voltage, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Type | Contingency 2 Type | N-1-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower)
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Drop analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Vdrop (%) | Voltage Drop | The percentage that the voltage has dropped as a result of the contingency
Delta Voltage Limit | Voltage Drop Limit | Threshold of percentage drop, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Short Circuit analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | Short Circuit model bus number where breaker is located
Bus Name | Bus Name | Aspen bus name and voltage where breaker is located
Bus KV | BUS Voltage | Nominal BUS voltage
Area | Area Number | Area number of bus identified as potential violation
Breaker | Breaker Name | Breaker name as given by Transmission Owner
Rating Type | Type of Breaker | Symmetrical (S) or Total (T) rated type of breaker
DUTY_P | Duty Percentage | The percentage of the asymmetrical fault current divided by breaker capacity
DUTY_A | Asymmetrical Fault Current | The combination of the symmetrical component and the direct current component of the current.
BKR_CAPA (A) | Breaker Capacity | Breaker’s derated interrupting capability, (A)
Pre-fault Voltage (KV) | Pre-fault KV | Voltage on the bus prior to fault event
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Stability analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis dynamics case info. | Analysis dynamics case info. | Dynamics case year, loading condition, MMWG Series. For example, MMWG 2018 Series 2023 SLL case.
Stability issue category | Stability issue category | Stability issue category: transient stability or damping or dynamic voltage recovery or voltage ride through
Bus # | Bus number | Bus number of the identified plant or station in the analysis power flow model.
Bus Name | Bus name | Bus name of the identified plant or station in the analysis power flow model.
Area | Area | Area number of the identified plant or station.
Stability Contingency description | Contingency description | Detailed contingency description that causes the identified potential stability issue including sequence and fault clearing times.
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Other analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Facility Name | Facility Name | Facilities such as line, substation, generator, etc.
Violations details | Violations details | TO to describe the details of the violation
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Purpose of FERC FORM 715 VIOLATION SUBMISSIONS:
PJM seeks Transmission Owner (TO) criteria violation submissions on facilities in accordance with Local TO criteria. This would also include violations which are not power flow violations of criteria.
Criteria applied by Transmission Owner:
FERC Form 715 Analysis (Thermal/Voltage Magnitude/Voltage Drop/Short Circuit/Stability/Other)
TERMINOLOGY USED IN TEMPLATE:
Descriptions of the column headings used in each Excel tab are provided below.
ANALYSIS PROCEDURE:
Transmission Owners are expected to identify FERC Form 715 violations. All violations are to be captured and recorded in the applicable Excel tab. Please use the corresponding tabs based on the type of violation below:
  * FERC Form 715 Thermal tab should be used to enter thermal violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Magnitude tab should be used to enter voltage magnitude violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Drop tab should be used to enter voltage drop/rise violations associated with FERC Form 715 criteria
  * FERC Form 715 Short Circuit tab should be used to enter short circuit violations associated with FERC Form 715 criteria
  * FERC Form 715 Stability tab should be used to enter stability violations associated with FERC Form 715 criteria
  * FERC Form 715 Other tab should be used to enter violations associated with FERC Form 715 criteria which can not be included in the other tabs
TRANSMISSION OWNER CRITERIA:
In addition to the NERC and PJM criteria included in RTEP studies, PJM also considers Transmission Owner specific criteria. Individual TO criteria can be found at the following link:
http://pjm.com/planning/planning-criteria/to-planning-criteria.aspx

## Case Defintion
Case Name | Description
2030_SUM_B0_S00 | 2025 Series RTEP 2030 Summer Case Preliminary 3 with existing Belle Haven STATCOM Offline
2030_WIN_B0_S00 | 2025 Series RTEP 2030 Winter Case Preliminary 3 with existing Belle Haven STATCOM Offline
2025_JAN_G_B0_S00 | Study case reflecting the January 23, 2025 Winter Event with the existing Belle Haven STATCOM Offline derived from WIN 2030 case, this case represents the gross loads
2025_JAN_G_B1_S00 | Study case reflecting the January 23, 2025 Winter Event with the existing Belle Haven STATCOM Online derived from WIN 2030 case, this case represents the gross loads
2025_JAN_N_B0_S00 | Study case reflecting the January 23, 2025 Winter Event, with the NRBTMG Generation online and with existing Belle Haven STATCOM Offline derived from WIN 2030 case, this case represents the net loads
2025_JAN_N_B1_S00 | Study case reflecting the January 23, 2025 Winter Event, with the NRBTMG Generation online and with existing Belle Haven STATCOM Online derived from WIN 2030 case, this case represents the net loads
* Note that all Capbank Binit values were set to max prior to any analysis being run.
** The study results were generated with PSS/E 35.6 software.
*** For administrative purposes, only the unique facilities were posted with Flowgates to minimize the amount of flowgates submitted during submission. Details for each can be viewed in the detailed tabs

## FERC Form 715 Thermal Unique
**It was observed through analysis that many contingency pairs run resulted in Non Convergances. Those contingency pairs are tabulated in the 'FERC Form 715 Non Converged' tab. The non converged contingencies are primarily associated with voltage collapse or failure to solve due to iteration limit exceedance. These thermal results were derived manually and mentioned below.
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Cont 2 Name | Conductor Rating (MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025-W1-ODEC-T1 | 2025_JAN_G_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 103.47 | NCN (>95%) | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/129/129/134 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T2 | 2025_JAN_G_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 92.97 | NCN (>103%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T3 | 2025_JAN_G_B0_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/105/105/105 | 67.54 | 109.19 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T4 | 2025_JAN_G_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 103.23 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/129/129/134 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T5 | 2025_JAN_G_B1_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 92.94 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T6 | 2025_JAN_G_B1_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/105/105/105 | 67.43 | 109.16 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T7 | 2025_JAN_N_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | <60% | 104.43 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T8 | 2025_JAN_N_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 80.53 | 131.3 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T9 | 2025_JAN_N_B0_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/105/105/105 | 67.39 | 106.09 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T10 | 2025_JAN_N_B0_S00 | 232284 | TASLEY | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 129/135/135/142 | 74.2 | 121.27 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T11 | 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | <60% | 101.48 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T12 | 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 83.36 | NCN (>98%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T13 | 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 82.08 | 131.19 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T14 | 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/105/105/105 | 67.33 | 106.05 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T15 | 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 66.52 | 110.05 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T16 | 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 77.48 | 127.7 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T17 | 2030_SUM_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 87/114/114/119 | 101.29 | 116.27 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 87/114/114/119 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T18 | 2030_SUM_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 114/135/135/142 | 82.21 | 88 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 114/151/151/163 | No | This result was determined manually as it was below the threshold set for reporting in the N-1-1 run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T19 | 2030_SUM_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 87/114/114/119 | 94.18 | 112.73 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 87/114/114/119 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T20 | 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 101.57 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/129/129/134 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T21 | 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 91.27 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 | No | This result was determined using the PSS®E GUI because the contingency pair failed to converge during the ACCC run. | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T22 | 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 85.8 | 138.98 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T23 | 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 67.03 | 111.91 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-T24 | 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/129/129/134 | 82.3 | 136.33 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/129/129/134 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Volt Mag Unique
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025-W1-ODEC-VM1 | 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.7851 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM2 | 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.6263 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM3 | 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.4861 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM4 | 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.509 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM5 | 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.8875 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM6 | 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8082 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM7 | 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.811 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM8 | 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.5678 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM9 | 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.5279 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM10 | 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8118 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM11 | 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.5279 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM12 | 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.7852 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM13 | 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.6266 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM14 | 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.4865 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM15 | 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.5094 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM16 | 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9003 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM17 | 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8084 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM18 | 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8147 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM19 | 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.5681 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM20 | 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.5283 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM21 | 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.867 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM22 | 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.5283 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM23 | 2025_JAN_N_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 1.012 | 0.9321 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM24 | 2025_JAN_N_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0145 | 0.935 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM25 | 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.5413 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM26 | 2025_JAN_N_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0163 | 0.937 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM27 | 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5024 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM28 | 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4244 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM29 | 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4463 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM30 | 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8547 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM31 | 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.5358 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM32 | 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.5959 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM33 | 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4828 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM34 | 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4644 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM35 | 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5082 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM36 | 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4644 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM37 | 2025_JAN_N_B1_S00 | 232282 | CHINCOTG | 69 | 235 | 1.0102 | 0.9396 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM38 | 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5447 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM39 | 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.502 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM40 | 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4755 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM41 | 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.477 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM42 | 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.809 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM43 | 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5947 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM44 | 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.6043 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM45 | 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4827 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM46 | 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4785 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM47 | 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5159 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM48 | 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4785 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM49 | 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.838 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM50 | 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.8583 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM51 | 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8306 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM52 | 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8306 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM53 | 2030_SUM_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.009 | 0.9323 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM54 | 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.8469 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM55 | 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8307 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM56 | 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.8614 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM57 | 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.8676 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM58 | 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.8578 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM59 | 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.8676 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM60 | 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9174 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM61 | 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9239 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM62 | 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5211 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM63 | 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.9263 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM64 | 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5038 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM65 | 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4891 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM66 | 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.491 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM67 | 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7839 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM68 | 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5637 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM69 | 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.7973 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM70 | 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.495 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM71 | 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4921 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM72 | 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5063 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VM73 | 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4921 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Volt Drop Unique
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Vdrop(%) | Delta Voltage Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025-W1-ODEC-VD1 | 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.4861 | -49.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD2 | 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.509 | -47.42% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD3 | 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.5279 | -45.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD4 | 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.5279 | -45.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD5 | 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.5678 | -42.08% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD6 | 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.6263 | -37.38% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD7 | 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.7851 | -21.4% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD8 | 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8118 | -19.07% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD9 | 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8082 | -18.8% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD10 | 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.811 | -18.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD11 | 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.8875 | -11.69% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD12 | 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.4865 | -49% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD13 | 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.5094 | -46.86% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD14 | 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.5283 | -45.1% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD15 | 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.5283 | -45.1% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD16 | 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.5681 | -41.37% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD17 | 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.6266 | -36.57% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD18 | 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.7852 | -20.9% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD19 | 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8084 | -18.35% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD20 | 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8147 | -17.91% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD21 | 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.867 | -12.71% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD22 | 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9003 | -10.16% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD23 | 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4244 | -56.59% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD24 | 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4463 | -54.62% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD25 | 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4644 | -52.98% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD26 | 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4644 | -52.98% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD27 | 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4828 | -51.5% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD28 | 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5024 | -50.68% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD29 | 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5082 | -50.35% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD30 | 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.5358 | -46.91% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD31 | 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.5413 | -46.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD32 | 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.5959 | -40.98% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD33 | 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8547 | -15.6% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD34 | 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4785 | -50.56% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD35 | 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4785 | -50.56% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD36 | 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.477 | -50.54% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD37 | 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4755 | -50.48% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD38 | 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4827 | -50.48% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD39 | 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.502 | -49.69% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD40 | 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5159 | -48.5% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD41 | 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5447 | -45.61% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD42 | 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5947 | -40.47% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD43 | 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.6043 | -39.61% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD44 | 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.809 | -19.85% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD45 | 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8306 | -17.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD46 | 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8306 | -17.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD47 | 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8307 | -17.26% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD48 | 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.838 | -16.92% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD49 | 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.8578 | -16.12% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD50 | 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.8583 | -15.95% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD51 | 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.8469 | -15.52% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD52 | 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.8614 | -15.03% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD53 | 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.8676 | -14.14% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD54 | 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.8676 | -14.14% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD55 | 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4891 | -51.22% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD56 | 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.491 | -51.21% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD57 | 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4921 | -51.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD58 | 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4921 | -51.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD59 | 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.495 | -51.16% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD60 | 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5038 | -50.86% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD61 | 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5063 | -50.7% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD62 | 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5211 | -47.97% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD63 | 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5637 | -43.14% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD64 | 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7839 | -21.67% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-VD65 | 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.7973 | -19.89% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | No |  | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Non Converged
**It was observed through analysis that certain contingencies in the DPL system resulted in non convergences. Several examples are reported below, but this list does not comprehensively detail all DPL related contingencies and their impacts on the ODEC system.
Reserved(FG# assigned by PJM) | AREA | Cont 1 Name | Cont 2 Name | Non Converge Cases | PJM Accepting Proposals | Justification for applicable exclusion from receiving competitive proposals | Comments
2025-W1-ODEC-NC1 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232905 CHERITON_25 24.9 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC2 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC3 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC4 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC5 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC6 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC7 | ODEC | NF_232284 TASLEY 69 232286 KELLAM 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC8 | ODEC | NF_232284 TASLEY 69 232286 KELLAM 69 1 | P12_TASLEY_KELLAM_6703 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC9 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC10 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC11 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC12 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC13 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC14 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC15 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC16 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC17 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC18 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC19 | ODEC | P12_OAKHILL_TASLEY_6790 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC20 | ODEC | P12_OAKHILL_TASLEY_6790 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC21 | ODEC | P12_OAKHILL_TASLEY_6790 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC22 | ODEC | P12_OAKHILL_TASLEY_6790 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC23 | ODEC | P12_OAKHILL_TASLEY_6790 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC24 | ODEC | P12_OAKHILL_TASLEY_6790 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC25 | ODEC | P12_OAKHILL_TASLEY_6790 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC26 | ODEC | P12_OAKHILL_TASLEY_6790 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC27 | ODEC | P12_OAKHILL_TASLEY_6790 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC28 | ODEC | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC29 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC30 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC31 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC32 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC33 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC34 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC35 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC36 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC37 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC38 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC39 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC40 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC41 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC42 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC43 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC44 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC45 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC46 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC47 | ODEC | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC48 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC49 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC50 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC51 | ODEC | P12_OAKHILL_TASLEY_6778 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC52 | ODEC | P12_OAKHILL_TASLEY_6778 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC53 | ODEC | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC54 | ODEC | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC55 | ODEC | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC56 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC57 | ODEC | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC58 | ODEC | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC59 | ODEC | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC60 | ODEC | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC61 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC62 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC63 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC64 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC65 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC66 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC67 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC68 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC69 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC70 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC71 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC72 | ODEC | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC73 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC74 | ODEC | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC75 | ODEC | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC76 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC77 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC78 | ODEC | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC79 | ODEC | P12_DPL_CKT 6750_RTEP | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC80 | ODEC | P12_DPL_CKT 6750_RTEP | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC81 | ODEC | P12_KELLAM_CHERITON_6750 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC82 | ODEC | P12_KELLAM_CHERITON_6750 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC83 | ODEC | P12_KELLAM_CHERITON_6750 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC84 | ODEC | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC85 | ODEC | P12_OAKHILL_TASLEY_6778 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC86 | ODEC | P12_OAKHILL_TASLEY_6778 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC87 | ODEC | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC88 | ODEC | P12_OAKHILL_TASLEY_6790 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC89 | ODEC | G-232905 CHERITON_25 24.9 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC90 | ODEC | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC91 | ODEC | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC92 | ODEC | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC93 | ODEC | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC94 | ODEC | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC95 | ODEC | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC96 | ODEC | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC97 | ODEC | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC98 | ODEC | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC99 | ODEC | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC100 | ODEC | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC101 | ODEC | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC102 | ODEC | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC103 | ODEC | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC104 | ODEC | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC105 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC106 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC107 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC108 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC109 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC110 | ODEC | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC111 | ODEC | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC112 | ODEC | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC113 | ODEC | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC114 | ODEC | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC115 | ODEC | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC116 | ODEC | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC117 | ODEC | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC118 | ODEC | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC119 | ODEC | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC120 | ODEC | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC121 | ODEC | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC122 | ODEC | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC123 | ODEC | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC124 | ODEC | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC125 | ODEC | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC126 | ODEC | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC127 | ODEC | NF_232284 TASLEY 69 232286 KELLAM 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC128 | ODEC | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC129 | ODEC | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC130 | ODEC | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC131 | ODEC | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC132 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | BLANK | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC133 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC134 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC135 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC136 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC137 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC138 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC139 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC140 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC141 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC142 | ODEC | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC143 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC144 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC145 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC146 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC147 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC148 | ODEC | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC149 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | BLANK | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC150 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_G_B0_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC151 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B1_S00 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC152 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC153 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC154 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC155 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC156 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC157 | ODEC | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC158 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC159 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC160 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC161 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC162 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC163 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC164 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC165 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC166 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC167 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC168 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC169 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC170 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC171 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC172 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC173 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC174 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC175 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC176 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC177 | ODEC | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC178 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC179 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC180 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC181 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC182 | ODEC | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC183 | ODEC | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC184 | ODEC | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC185 | ODEC | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC186 | ODEC | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC187 | ODEC | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC188 | ODEC | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC189 | ODEC | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC190 | ODEC | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC191 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC192 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC193 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC194 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | P12_OAKHILL_TASLEY_6790 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC195 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC196 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC197 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC198 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC199 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC200 | ODEC | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC201 | ODEC | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC202 | ODEC | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC203 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC204 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC205 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC206 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC207 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC208 | ODEC | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC209 | ODEC | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC210 | ODEC | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC211 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC212 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC213 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC214 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC215 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC216 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC217 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC218 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC219 | ODEC | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC220 | ODEC | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC221 | ODEC | P12_DPL_CKT 6750_RTEP | BLANK | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC222 | ODEC | P12_DPL_CKT 6750_RTEP | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC223 | ODEC | P12_DPL_CKT 6750_RTEP | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC224 | ODEC | P12_DPL_CKT 6750_RTEP | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC225 | ODEC | P12_DPL_CKT 6750_RTEP | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC226 | ODEC | P12_DPL_CKT 6750_RTEP | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC227 | ODEC | P12_DPL_CKT 6750_RTEP | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC228 | ODEC | P12_DPL_CKT 6750_RTEP | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC229 | ODEC | P12_KELLAM_CHERITON_6750 | BLANK | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC230 | ODEC | P12_KELLAM_CHERITON_6750 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC231 | ODEC | P12_KELLAM_CHERITON_6750 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC232 | ODEC | P12_KELLAM_CHERITON_6750 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC233 | ODEC | P12_KELLAM_CHERITON_6750 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC234 | ODEC | P12_KELLAM_CHERITON_6750 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC235 | ODEC | P12_KELLAM_CHERITON_6750 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC236 | ODEC | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | 2025_JAN_G_B0_S00 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC237 | ODEC | P12_OAKHILL_TASLEY_6778 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC238 | ODEC | P12_OAKHILL_TASLEY_6790 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC239 | ODEC | P12_OAKHILL_TASLEY_6790 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC240 | ODEC | P12_OAKHILL_TASLEY_6790 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC241 | ODEC | P12_TASLEY_KELLAM_6703 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC242 | ODEC | S-P14:232280 OAKHL_69 69.0 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC243 | ODEC | S-P14:232280 OAKHL_69 69.0 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC244 | ODEC | S-P14:232280 OAKHL_69 69.0 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC245 | ODEC | S-P14:232281 WATTSVIL 69.0 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC246 | ODEC | S-P14:232281 WATTSVIL 69.0 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC247 | ODEC | S-P14:232284 TASLEY 69.0 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC248 | ODEC | S-P14:232284 TASLEY 69.0 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC249 | ODEC | S-P14:232286 KELLAM 69.0 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC250 | ODEC | S-P14:232286 KELLAM 69.0 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC251 | ODEC | S-P14:232287 CHERITON_69 69.0 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC252 | ODEC | S-P14:232287 CHERITON_69 69.0 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC253 | ODEC | S-P14:232287 CHERITON_69 69.0 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC254 | ODEC | S-P14:232648 WATTSVL1 12.5 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC255 | ODEC | S-P14:232648 WATTSVL1 12.5 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC256 | ODEC | S-P14:232648 WATTSVL1 12.5 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC257 | ODEC | S-P14:232649 WATTSVL2 12.5 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC258 | ODEC | S-P14:232649 WATTSVL2 12.5 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC259 | ODEC | S-P14:232649 WATTSVL2 12.5 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC260 | ODEC | S-P14:232903 BELLHAVN 69.0 | P12_DPL_CKT 6750_RTEP | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC261 | ODEC | S-P14:232903 BELLHAVN 69.0 | P12_KELLAM_CHERITON_6750 | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC262 | ODEC | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC263 | ODEC | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_G_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC264 | ODEC | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC265 | ODEC | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC266 | ODEC | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC267 | ODEC | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC268 | ODEC | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC269 | ODEC | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 2025_JAN_G_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC270 | ODEC | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC271 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_G_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC272 | ODEC | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | P12_OAKHILL_TASLEY_6778 | 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC273 | ODEC | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC274 | ODEC | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 2030_WIN_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC275 | ODEC | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC276 | ODEC | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC277 | ODEC | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC278 | ODEC | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC279 | ODEC | 232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC280 | ODEC | P12_DPL_CKT 6750_RTEP | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | 2025_JAN_G_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC281 | ODEC | P12_OAKHILL_TASLEY_6778 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC282 | ODEC | S-P14:232286 KELLAM 69.0 | 232543 KELLAM 1 24.9 232286 KELLAM 69 1 | 2025_JAN_N_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC283 | DPL | NF_232274 PINEY_69 69 232839 M OLIVE1 69 1 | P12_DPL_CKT 6712_SRT-A | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC284 | DPL | NF_232277 KENNEY 69 232839 M OLIVE1 69 1 | P12_DPL_CKT 6712_SRT-A | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC285 | DPL | 232646 POCMOKE2 12.5 232130 POCOMOKE 138 1 | P12_DPL_CKT 6712_SRT-A | 2025_JAN_N_B0_S00 2025_JAN_N_B1_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC286 | DPL | NF_230912 PINEYCAP 69 232274 PINEY_69 69 1 | P11_DPL_OH 1-3 NUG_SRT-A | 2030_SUM_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC287 | DPL | NF_232272 M HERMON 69 232274 PINEY_69 69 1 | P11_DPL_OH 1-3 NUG_SRT-A | 2030_SUM_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC288 | DPL | 232274 PINEY_69 69 232128 PINEY138 138 1 | P11_DPL_OH 1-3 NUG_SRT-A | 2030_SUM_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC289 | DPL | NF_232274 PINEY_69 69 232839 M OLIVE1 69 1 | P11_DPL_OH 1-3 NUG_SRT-A | 2030_SUM_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC290 | DPL | NF_232277 KENNEY 69 232278 STOCKTON 69 1 | P11_DPL_OH 1-3 NUG_SRT-A | 2030_SUM_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-ODEC-NC291 | DPL | NF_232277 KENNEY 69 232839 M OLIVE1 69 1 | P11_DPL_OH 1-3 NUG_SRT-A | 2030_SUM_B0_S00 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Thermal Detailed
**It was observed through analysis that many contingency pairs run resulted in Non Convergances. Those contingency pairs are tabulated in the 'FERC Form 715 Non Converged' tab. The non converged contingencies are primarily associated with voltage collapse or failure to solve due to iteration limit exceedance. These thermal results were derived manually and mentioned below.
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Cont 2 Name | Conductor Rating (MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.13 | 109.09 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9 | 139/177/177/193
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.54 | 109.19 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193
| 2025_JAN_G_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 92.97 | NCN (>103%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2025_JAN_G_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 103.47 | NCN (>95%) | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.13 | 109.09 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9 | 139/177/177/193
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.43 | 109.16 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193
| 2025_JAN_G_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 103.23 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2025_JAN_G_B1_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 92.94 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2025_JAN_N_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 68.28 | 100.14 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9 | 100/128/128/134
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | <60% | 101.48 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 100/128/128/134
| 2025_JAN_N_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | <60% | 104.43 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 100/128/128/134
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.11 | 105.08 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9 | 139/177/177/193
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.39 | 106.09 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 129/135/135/142 | 74.2 | 121.27 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 129/135/135/142 | 74.2 | 121.27 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 139/177/177/193
| 2025_JAN_N_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 80.53 | 131.3 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193
| 2025_JAN_N_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 80.53 | 131.3 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 139/177/177/193
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | <60% | 101 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | <60% | 103.61 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.11 | 104.13 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9 | 139/177/177/193
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232286 | KELLAM | N/A | N/A | 1 | 69 | 235 | 99/104/104/104 | 67.33 | 106.05 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703 | 139/177/177/193
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 65.56 | 109.97 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 65.56 | 110 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 66.52 | 110.02 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 66.52 | 110.02 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 66.52 | 110.05 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 66.52 | 110.05 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 78.64 | 127.6 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 78.64 | 127.6 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 78.65 | 127.65 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 78.65 | 127.65 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 77.48 | 127.65 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 77.48 | 127.7 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 84.31 | 130.9 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 84.31 | 130.9 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 84.34 | 130.97 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 84.34 | 130.97 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 82.08 | 131.04 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 82.08 | 131.19 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2025_JAN_N_B1_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 83.36 | NCN (>98%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2030_SUM_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 114/135/135/142 | 82.21 | 88 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 114/150/150/163 |  | This result was determined manually as it was below the threshold set for reporting in the N-1-1 run.
| 2030_SUM_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 87/114/114/118 | 94.18 | 112.73 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 87/114/114/118
| 2030_SUM_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 87/114/114/118 | 94.18 | 112.73 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 87/114/114/118
| 2030_SUM_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 87/114/114/118 | 101.29 | 116.27 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 87/114/114/118
| 2030_SUM_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 87/114/114/118 | 101.29 | 116.27 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 87/114/114/118
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 101.57 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232846 | PERDUE | N/A | N/A | 1 | 69 | 235 | 135/135/135/142 | 91.27 | NCN (>100%) | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | G-232921 TASLEY2G 13.2 | 139/177/177/193 |  | This result was determined manually as this contingency pair resulted in a non-converge result.
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 85.8 | 138.98 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 85.8 | 138.98 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 88.31 | 138.79 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 88.31 | 138.79 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 88.41 | 138.47 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2030_WIN_B0_S00 | 232280 | OAKHL_69 | 232844 | HALLWOOD | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 88.41 | 138.47 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 82.3 | 136.33 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 82.3 | 136.33 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 80.9 | 135.86 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 80.9 | 135.86 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 82.33 | 135.6 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 82.33 | 135.6 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 67.03 | 111.91 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 67.03 | 111.91 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134
| 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 65.85 | 110.98 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 65.85 | 110.98 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778 | 100/128/128/134
| 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 67.04 | 110.4 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2 | 100/128/128/134
| 2030_WIN_B0_S00 | 232284 | TASLEY | 232845 | PARKSLEY | N/A | N/A | 1 | 69 | 235 | 100/128/128/134 | 67.04 | 110.4 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 100/128/128/134

## FERC Form 715 Volt Mag Detailed
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8118 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.814 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8635 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8641 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8647 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8909 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8909 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8935 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8935 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8937 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8939 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.894 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8976 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8991 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9001 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9009 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9051 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9057 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9071 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9071 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9093 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9093 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9138 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9141 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9141 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9148 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9158 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9163 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9163 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9166 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9181 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9183 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9199 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9215 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9238 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9244 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9249 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9252 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9258 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9258 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9266 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9273 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9278 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9278 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.928 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9284 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9297 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9297 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9298 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9298 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.934 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9345 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9345 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9345 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9345 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.935 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.935 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9363 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9392 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9393 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9393 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9397 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.4861 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.4877 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.7348 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.7857 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.7918 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8003 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8037 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8167 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8204 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8204 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8234 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8234 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8254 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8306 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8311 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8325 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.835 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8385 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8446 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8502 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8539 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8539 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8545 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8545 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.855 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8565 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8565 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8625 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8675 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8801 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8821 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8839 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.884 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8861 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8864 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8868 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8869 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.887 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8881 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8894 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8919 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8921 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8931 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8932 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8953 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8954 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.896 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8961 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8962 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8971 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8971 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8971 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8971 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8971 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8977 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8981 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8981 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8981 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8981 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9015 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9015 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9024 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9025 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9025 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9029 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9031 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9031 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9031 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9032 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9033 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9037 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.904 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9041 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9041 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9047 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9059 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.907 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.907 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9071 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9077 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9077 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9084 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9087 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9097 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9101 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9101 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9143 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9158 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9168 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9187 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9188 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9189 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9191 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9192 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9195 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.92 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9206 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9207 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9212 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9212 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9221 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9222 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9226 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9241 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9241 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9241 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9241 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9267 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.928 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9285 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9285 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9286 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9291 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9291 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9291 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9291 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9301 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9301 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9301 | 1.07/.94 | N-1-1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9302 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9304 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9305 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9339 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9341 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9341 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9343 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9343 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9344 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9345 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9345 | 1.07/.94 | N-1-1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9348 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9355 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9382 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9389 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.9389 | 1.07/.94 | N-1-1 | 232556 TASLEY 1 24.9 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.5279 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.5294 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.7577 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.7997 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8031 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8059 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8117 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8158 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8295 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8339 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8391 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8391 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.842 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.842 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8434 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8438 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8489 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8506 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8528 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8533 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8534 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8553 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8553 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8561 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8674 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8709 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8718 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8828 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8853 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8854 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8874 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8903 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8916 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8918 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8962 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8981 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8998 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8998 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8999 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9019 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9021 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9025 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9025 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9027 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.905 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9054 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9054 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9061 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9061 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9068 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9071 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9075 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9077 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.908 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9085 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9085 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9108 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9109 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9115 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9115 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9117 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9126 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9131 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.914 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.915 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.917 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.917 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9172 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9174 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9174 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9176 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9176 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9177 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9178 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9181 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9182 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9183 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9183 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9184 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9184 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9184 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9188 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9188 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.919 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9191 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9195 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9195 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9199 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9203 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9204 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9209 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9211 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9221 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9223 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9223 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9224 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9224 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9267 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9283 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9283 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9287 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9299 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9304 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9304 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9321 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9322 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9322 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9323 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9324 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9324 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9325 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.933 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9336 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.9395 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.509 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.5106 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.7474 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.7968 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8027 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8033 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8161 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8299 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8306 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8306 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8336 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8336 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8344 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8355 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8409 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8424 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8439 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8481 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8533 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8538 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8538 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8558 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8558 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8596 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8632 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8642 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8736 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8784 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8859 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.886 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8889 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8893 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8909 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8922 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8924 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8926 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8927 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8948 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.895 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8956 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8979 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9004 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9006 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9006 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9007 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9031 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9031 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9038 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9039 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9045 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9045 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9047 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9056 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9056 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9056 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9056 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9056 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9061 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9061 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9062 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9066 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9066 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9066 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9066 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9067 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9068 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9075 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9078 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9088 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9092 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9092 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9108 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9109 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9109 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9112 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9114 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9115 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9115 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9116 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9116 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.912 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9123 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.913 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9134 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9143 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9148 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9153 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9158 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9177 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9178 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9179 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9182 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9182 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9184 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.919 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9196 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9197 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9202 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9202 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9211 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9212 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9216 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.923 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.923 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9231 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9231 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9275 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.928 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.928 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.928 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.928 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.929 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9291 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9291 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9295 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9295 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9314 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9315 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9329 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.933 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.933 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9333 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9333 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9334 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9338 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9344 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.9371 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.938 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.938 | 1.07/.94 | N-1-1 | 232557 TASLEY 4 24.9 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.8875 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.8971 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9003 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9006 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9202 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9252 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9329 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.6263 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.6275 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8092 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8125 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8151 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8243 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8375 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.842 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8511 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8569 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8604 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8609 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8609 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.862 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8629 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8629 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8865 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8865 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8891 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8892 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8905 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8918 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8919 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8945 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8966 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.898 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8982 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9009 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9032 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9062 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9062 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9084 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9084 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9114 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9114 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9116 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.912 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.912 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9128 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.913 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9137 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9142 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9142 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9143 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.915 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9184 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9195 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9205 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9225 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9225 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9227 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9229 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9229 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.923 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9238 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9244 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9244 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9249 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9249 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9259 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9261 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9264 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9277 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9277 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9278 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9278 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9319 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.932 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9336 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9336 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9372 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9374 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9374 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9375 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9376 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9376 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9378 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9381 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9384 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.9392 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.5279 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.5294 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.7577 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.7997 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8031 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8059 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8117 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8158 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8295 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8339 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8391 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8391 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.842 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.842 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8434 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8438 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8489 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8506 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8528 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8533 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8534 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8553 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8553 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8561 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8674 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8709 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8718 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8828 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8853 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8854 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8874 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8903 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8916 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8918 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8962 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8981 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8998 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8998 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8999 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9019 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9021 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9025 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9025 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9027 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.905 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9054 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9054 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9061 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9061 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9068 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9071 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9075 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9077 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.908 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9085 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9085 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9108 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9109 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9115 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9115 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9117 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9125 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9126 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9131 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.914 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.915 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.917 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.917 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9172 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9174 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9174 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9176 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9176 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9177 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9178 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9181 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9182 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9183 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9183 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9184 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9184 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9184 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9188 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9188 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.919 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9191 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9195 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9195 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9199 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9203 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9204 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9209 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9211 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9221 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9223 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9223 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9224 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9224 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9267 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9273 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9283 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9283 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9287 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9299 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9304 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9304 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9321 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9322 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9322 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9323 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9324 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9324 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9325 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.933 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9336 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.9395 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8082 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8088 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8317 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8417 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8637 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8711 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8787 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8853 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8909 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8912 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8964 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8965 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8976 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8976 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9005 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9055 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9103 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9128 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9128 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9146 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9151 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9151 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9152 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9152 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9163 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9165 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9169 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9178 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9187 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9188 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9195 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9202 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9204 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9204 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9222 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9223 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9232 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9236 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9252 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9252 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9263 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9284 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9286 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9306 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9308 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9313 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9313 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9313 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9313 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9317 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.932 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.932 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9352 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9353 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9353 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9354 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9354 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9354 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9355 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9356 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9359 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.936 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.936 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9361 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9362 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9364 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9381 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.9391 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.811 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8146 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8151 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8226 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8652 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8818 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8959 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.896 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9011 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9011 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9018 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.905 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9084 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9091 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9131 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9138 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9164 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9164 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9166 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9169 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9184 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9184 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9187 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9187 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9199 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.92 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.92 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9212 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9218 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9219 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9234 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9234 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9235 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9257 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9262 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9262 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9262 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9262 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9262 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9264 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9266 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9266 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9266 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9266 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9268 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9295 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9307 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9308 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9308 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9311 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9315 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9334 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9337 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9337 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9345 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9346 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9348 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9348 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.938 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.938 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9382 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9382 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9387 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.9387 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.7851 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.7857 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8149 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8264 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8583 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8689 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8693 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8737 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8805 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8896 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8896 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8908 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8908 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8917 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8918 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8975 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.898 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9053 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9053 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9053 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.907 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9077 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9077 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9104 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9107 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9107 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9113 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9118 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9119 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9125 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9125 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9144 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9146 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9147 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9164 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9165 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9172 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9177 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9182 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9201 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9203 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9209 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9212 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9215 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9237 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9239 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9251 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9251 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9252 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9252 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9279 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9291 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9292 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9295 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9295 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9297 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9297 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9297 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9297 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9297 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9304 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9317 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9329 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9332 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9333 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9335 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9335 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9341 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9341 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9341 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9342 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9342 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9346 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9346 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9349 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9372 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.938 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.9394 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.5678 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.5691 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.7797 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.7996 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8029 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8153 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8252 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8288 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8307 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8333 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8427 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8521 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8526 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8526 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8545 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8545 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8569 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8569 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8597 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8597 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8613 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.866 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8678 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8728 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8839 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8842 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8843 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.887 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8879 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8905 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8907 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8924 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8988 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8988 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9012 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9012 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9018 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9042 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9042 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9048 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9048 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9055 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9058 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.906 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9067 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9072 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9072 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9113 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9114 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9126 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9133 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9136 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9147 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.915 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9156 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9156 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9158 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9159 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.916 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9161 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9168 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9169 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.917 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9175 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9175 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9176 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.918 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.918 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.919 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9191 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9195 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9198 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9209 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9209 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9209 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9209 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9224 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9226 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9253 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9255 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9256 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9258 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9258 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9258 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9258 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9261 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9262 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9264 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9268 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9268 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9272 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9272 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9278 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9282 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9282 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9282 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9282 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9306 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9306 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9307 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9308 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9309 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9309 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9311 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9315 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9318 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9319 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9321 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9322 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9322 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9323 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9323 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9326 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9327 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9327 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9328 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9328 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9329 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9332 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9335 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9341 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9342 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9343 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9348 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9355 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9364 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9386 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9386 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.939 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9391 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9391 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9396 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9396 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9397 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.9397 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.4865 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.4877 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.5094 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.5106 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.5283 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.5283 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.5294 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.5294 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.5681 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.5691 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.6266 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.6275 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.7852 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.7857 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.7921 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8028 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8084 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8088 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8117 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8117 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8147 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8151 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8168 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8173 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8173 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8177 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8183 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8258 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.829 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8296 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8296 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8301 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8304 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8307 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8334 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.834 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.834 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8344 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8351 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8376 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8421 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8426 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8434 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8434 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8439 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8446 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8498 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8511 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8526 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8526 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8533 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8533 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8534 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8534 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8538 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8538 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8545 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8545 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8546 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8546 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8548 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8555 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8555 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8555 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8555 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.856 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.856 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8561 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8563 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8566 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8567 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8567 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.857 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.857 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8575 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8583 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8585 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8592 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8595 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8609 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8609 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8614 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8618 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8618 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8622 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8628 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8628 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8628 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8628 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8634 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8639 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8642 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8642 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8642 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8643 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8655 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8659 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8669 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8669 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.867 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8694 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8698 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8711 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.8713 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8715 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8715 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8716 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8716 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8719 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8719 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8721 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8725 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8728 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8732 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8732 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8733 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8735 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8735 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8737 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8762 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8774 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8787 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8787 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8805 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8808 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8808 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8811 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8819 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8833 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8849 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8853 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8863 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8882 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8893 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8895 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8896 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8896 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8898 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8898 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.891 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.891 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8912 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8929 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8936 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8936 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8947 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8964 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8965 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8967 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.897 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.897 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8972 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8977 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8977 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9001 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9001 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9001 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9001 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9003 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9003 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9005 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9006 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9008 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9013 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9013 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9016 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9016 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9023 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9033 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9034 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9048 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9048 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9048 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9048 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9056 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9057 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9074 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9083 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.909 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9091 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9091 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9091 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9092 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.91 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9108 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9109 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.912 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.912 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.912 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9126 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9126 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9129 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9134 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9134 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9136 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9136 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9138 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9138 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9141 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9143 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9143 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9147 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9147 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.915 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.915 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9151 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9152 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9152 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9156 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9156 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9158 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9158 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9159 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9159 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9159 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9161 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9165 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9166 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9167 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9167 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9167 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9168 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9169 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.917 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.917 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9178 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9182 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9188 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.919 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9192 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9192 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9192 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9192 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9199 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9199 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9205 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9207 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9209 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.921 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.921 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9214 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9214 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9215 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9218 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.922 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9222 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9225 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9225 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9225 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9225 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9225 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9225 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9225 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9226 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9226 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9228 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9228 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9229 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9229 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9229 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9229 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9229 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.923 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9233 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9233 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9234 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9235 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9236 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9237 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9237 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9237 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9237 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9239 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9242 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9242 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9242 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9243 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9243 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9243 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9244 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9244 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9244 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9244 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9247 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9247 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9248 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9248 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9248 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9251 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9252 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.926 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.926 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9261 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9262 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9262 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9262 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9263 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9269 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9273 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9273 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9274 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9274 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9276 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9276 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9278 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9278 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9278 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9278 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9278 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9279 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9279 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.928 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.928 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.928 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9282 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9282 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9282 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9282 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9287 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9287 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9287 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9289 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9289 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.929 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.929 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.929 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.929 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9292 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9292 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9292 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9292 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9294 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9294 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9294 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9294 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9294 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9294 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9294 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9295 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9295 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9298 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9298 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9298 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9299 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.93 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.93 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9302 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9302 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9302 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9302 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9302 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9304 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9304 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9305 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9306 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9306 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9308 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.931 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9311 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9311 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9311 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9312 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9313 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9313 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9313 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9313 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9313 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9313 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9313 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9313 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9314 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9314 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9315 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9315 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9316 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9316 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9317 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9317 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9317 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9319 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9319 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.932 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.932 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9321 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9321 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9321 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9322 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9323 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9323 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9324 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9324 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9328 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9328 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9328 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.933 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.933 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.933 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.933 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.933 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9334 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9334 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9336 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9336 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9336 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9336 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9339 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9342 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9343 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9343 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9343 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9343 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9348 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9348 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9349 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.935 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9351 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9352 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9352 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9357 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9357 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9359 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9359 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.936 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.936 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.936 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.936 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9361 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9361 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9364 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9364 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9364 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9364 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9366 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9367 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9367 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9367 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9369 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9369 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9371 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9373 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9374 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9374 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9374 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9376 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9376 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9376 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9376 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.9377 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9378 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9378 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9378 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9378 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9379 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9379 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.938 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9381 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9381 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9381 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9381 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9381 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9382 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9382 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9383 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9384 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9386 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9388 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.9388 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.9389 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.9389 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.939 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.939 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9392 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9392 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9392 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9392 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9394 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9394 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9394 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9394 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.9397 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.9398 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.9399 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.9399 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.9399 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.9399 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4244 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4463 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4644 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4644 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4752 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4752 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.476 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4768 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4768 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4776 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4785 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4785 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4785 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4785 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4793 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4793 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4828 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4828 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4837 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5024 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5024 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.5025 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5033 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5082 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5082 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.5353 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.5358 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.5358 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.5413 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.5414 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.5461 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.5569 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5591 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.5674 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5686 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.5749 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.5749 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.5849 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.5849 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.5959 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.5959 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.6047 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.6095 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.6128 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.622 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.627 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.6624 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.6688 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.6772 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.6782 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.7833 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.7833 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.7943 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.7944 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.7963 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8034 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8034 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8035 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8035 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8072 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8147 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8147 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8149 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8162 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8162 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8196 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8228 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8228 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8251 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8251 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8337 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8337 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8337 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8337 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8352 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8365 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8406 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8413 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8453 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8517 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8517 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.854 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8545 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8546 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8547 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8594 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8594 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8618 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8622 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8629 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8632 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8634 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8637 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8637 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8641 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8642 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8648 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8665 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8691 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8697 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.87 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.87 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8705 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.871 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8712 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8712 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8712 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8713 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8715 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8719 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8732 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8756 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.876 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.876 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8764 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8764 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8766 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8766 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8769 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8769 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8769 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8769 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8771 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8771 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8772 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8775 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8775 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8778 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8781 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8781 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8782 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8782 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8786 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8786 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8787 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8787 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8791 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8791 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8795 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8806 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8806 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8808 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8816 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8816 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8836 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8836 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8837 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8839 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8839 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8847 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8847 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8849 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8852 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8855 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8856 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8859 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.886 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8862 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8862 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8862 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8862 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8872 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8875 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8881 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8881 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8882 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8882 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8883 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8884 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8888 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8897 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8899 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8914 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8924 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8933 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8944 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8946 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8947 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8948 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8951 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8961 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8963 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8966 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8973 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8973 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8979 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8984 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8988 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8996 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8996 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9001 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9001 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9015 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9015 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9018 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.902 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9029 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9032 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9032 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9035 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9036 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9037 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9039 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9041 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9041 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9045 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9048 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9048 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9053 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9057 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9071 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9079 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9079 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9079 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9083 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9087 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9088 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9088 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.909 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9093 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9093 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9093 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9099 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9101 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9102 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9105 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9105 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9122 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9122 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9128 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9128 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9132 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9139 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9139 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9147 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9151 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9155 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9155 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9157 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9159 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9159 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9159 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9163 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9163 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9165 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9165 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.917 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9181 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9182 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9183 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9183 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9184 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9188 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9193 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9197 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9204 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9205 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9208 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9209 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.921 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9212 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9214 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9214 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9216 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9221 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9224 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.923 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9237 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9237 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9237 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9241 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9245 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9247 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9248 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9249 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.925 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9251 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9251 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9252 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9254 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9255 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9256 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9257 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9258 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9259 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9262 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.9263 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9271 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9271 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9271 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9272 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9272 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9272 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9272 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9272 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9272 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9273 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9273 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9273 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9274 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9274 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9275 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9276 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9276 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9276 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9278 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9279 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9281 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9281 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9282 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9283 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9284 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9287 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9288 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9289 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.929 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9291 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9292 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9293 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9294 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9296 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9296 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9296 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9296 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9298 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9298 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9298 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9301 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9301 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9301 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9304 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9304 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9306 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9311 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9311 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9311 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9315 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9315 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9317 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9318 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 1.012 | 0.9321 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 1.012 | 0.9321 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9324 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9324 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9325 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9326 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9327 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9328 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9328 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9329 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.933 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9331 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9331 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9331 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9332 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9334 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9335 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6790
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9337 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9339 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9339 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9341 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9341 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9341 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9341 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9343 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9343 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9345 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9345 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9345 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9346 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9346 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9347 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9347 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9348 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9349 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0145 | 0.935 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0145 | 0.935 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.935 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9351 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9351 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9351 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9351 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9351 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9352 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9352 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9353 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9353 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9353 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9353 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9353 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9353 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9354 | 1.07/.94 | N-1-1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9355 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9355 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9356 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9356 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9356 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9356 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9356 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9356 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9357 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9357 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9357 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9357 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9358 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9359 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9359 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9359 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9359 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.936 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9362 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9362 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9362 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9362 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9364 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9364 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9365 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9365 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9365 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9365 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9366 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9367 | 1.07/.94 | N-1-1 | 232553 OAKHALL1 24.9 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9368 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9368 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0163 | 0.937 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0163 | 0.937 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.937 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.937 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9371 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9373 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.9373 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9375 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9375 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9376 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9376 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.938 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9381 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9381 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.9382 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9388 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9388 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9388 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9388 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9389 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9389 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9391 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9391 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9393 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9393 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9393 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9393 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9394 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9394 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9394 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9394 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9395 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9395 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9395 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9395 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9397 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.9397 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9398 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9398 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6790 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4755 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.477 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4785 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4785 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4811 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.482 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4827 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4829 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4829 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.483 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4839 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4847 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4847 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4848 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4848 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4852 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4852 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4857 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4857 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4865 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4865 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4865 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4865 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4871 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4871 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4889 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4889 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4889 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4889 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4896 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4904 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4911 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4911 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4936 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4936 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.502 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5096 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5104 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5111 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5111 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5136 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5136 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5159 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5166 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5173 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5173 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5198 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5198 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.5357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5447 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5454 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.546 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.546 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5484 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5484 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.5559 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.5574 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.5753 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.5753 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.5767 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.594 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.594 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5947 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5953 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5958 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5958 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5981 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5981 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.6043 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.6091 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.6132 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.6304 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.6623 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.6692 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.6847 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.7734 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.7848 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.7941 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.7941 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.809 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8094 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8097 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8097 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8099 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8116 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8116 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.814 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8151 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.82 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8211 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8211 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.822 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8221 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8239 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8284 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8284 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8312 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8312 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8321 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8322 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.834 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8357 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8367 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8396 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8396 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8396 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8396 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8404 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8404 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8405 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8405 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8414 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8438 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8445 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8455 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.846 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8464 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8491 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8518 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8519 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8519 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8536 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8536 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8551 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8572 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8573 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.858 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.858 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8631 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8639 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8639 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8643 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.865 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8654 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8689 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8691 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8698 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8698 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8703 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8707 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.871 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8713 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8749 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8752 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8755 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8758 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8758 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8762 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8762 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8763 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8768 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8769 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8769 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.877 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8771 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8776 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8779 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8779 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8779 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8779 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8782 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8784 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8785 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8792 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8792 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8805 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8828 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8831 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8843 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8846 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8847 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.885 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.885 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8853 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8853 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8856 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8856 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8859 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.886 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8864 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8864 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8864 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8864 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8866 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8866 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8867 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8868 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8868 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.887 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.887 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8873 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8873 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8874 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8875 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8875 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8876 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8884 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.889 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.889 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8898 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.89 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8904 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8916 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8916 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.892 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8922 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8922 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8934 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8936 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8936 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8937 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8937 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8937 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8955 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8961 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8961 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8963 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8963 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8973 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8973 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8976 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8977 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8979 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8983 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8985 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8985 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8988 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8993 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9008 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9009 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9013 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9014 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.9025 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9032 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9032 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9035 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.9036 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.904 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9052 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9052 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.906 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9067 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.907 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9074 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9074 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9078 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9078 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9083 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9084 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9086 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9087 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9091 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9097 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9097 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9098 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9098 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9101 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9102 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9106 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9107 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9109 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9109 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.912 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.912 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9127 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9128 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9128 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9139 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9139 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.915 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9153 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9153 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9155 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9164 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9164 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9164 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9165 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9166 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9174 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9177 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9177 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9178 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9182 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.9183 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9187 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9187 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9188 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.92 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9224 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.9228 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9233 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9241 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9241 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9245 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9252 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9254 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9254 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9255 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9255 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9256 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.9257 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9258 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9259 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9262 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9267 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9272 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9274 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9278 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9282 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9282 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9283 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9286 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.929 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9292 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9293 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9298 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9298 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9301 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9301 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9306 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9311 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9317 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9321 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9324 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9325 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.9327 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.9333 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9334 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9335 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9335 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9337 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9338 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9338 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.9345 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.9349 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9358 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9359 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9362 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9362 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9363 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9363 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9369 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9375 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9383 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9384 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9385 | 1.07/.94 | N-1-1 | NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9386 | 1.07/.94 | N-1-1 | NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9387 | 1.07/.94 | N-1-1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9387 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9388 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232280 OAKHL_69 69.0
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232648 WATTSVL1 12.5
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232649 WATTSVL2 12.5
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | S-P14_232280 OAKHL_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | S-P14_232648 WATTSVL1 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9391 | 1.07/.94 | N-1-1 | S-P14_232649 WATTSVL2 12.5 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9394 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9395 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.9395 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B1_S00 | 232282 | CHINCOTG | 69 | 235 | 1.0102 | 0.9396 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232282 | CHINCOTG | 69 | 235 | 1.0102 | 0.9397 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232282 | CHINCOTG | 69 | 235 | 1.0102 | 0.9399 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232282 | CHINCOTG | 69 | 235 | 1.0102 | 0.9399 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9399 | 1.07/.94 | N-1-1 | NF_232283 WALLOPS 69 232285 WALLOPST 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9399 | 1.07/.94 | N-1-1 | 232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9399 | 1.07/.94 | N-1-1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9399 | 1.07/.94 | N-1-1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.9399 | 1.07/.94 | N-1-1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.9399 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.9399 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.9399 | 1.07/.94 | N-1-1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8306 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8306 | 1.07/.94 | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8306 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8306 | 1.07/.94 | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8307 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8307 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.838 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.838 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.8469 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.8469 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.8578 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.8578 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.8583 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.8583 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.8614 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.8614 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8629 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8629 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8658 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8658 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.8676 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.8676 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.8676 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.8676 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8899 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8899 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8955 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8993 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.9018 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.9022 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.903 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.9037 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.9037 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.9055 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.9059 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.906 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9107 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9112 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.9121 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.9122 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9134 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9134 | 1.07/.94 | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.9308 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.009 | 0.9323 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.009 | 0.9323 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.933 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.9331 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.935 | 1.07/.94 | N-1-1 | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.9354 | 1.07/.94 | N-1-1 | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.9354 | 1.07/.94 | N-1-1 | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.9363 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.9363 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.9373 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.9374 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.9376 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.9396 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.9396 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4891 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4891 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.491 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.491 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4921 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4921 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4921 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4921 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4927 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4927 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.4946 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.4946 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.495 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.495 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4957 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4957 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4957 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4957 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.4987 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.4987 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4989 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4989 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.5009 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.5009 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.5019 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.5019 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.5019 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.5019 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5038 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5038 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.505 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.505 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5063 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5063 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5075 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5075 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.51 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.51 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5139 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5139 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5164 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5164 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5211 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5211 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5258 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5258 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5313 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5313 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5637 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5637 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5692 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5692 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5736 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5736 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.7818 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.7832 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7839 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7839 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.7839 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.7839 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.7858 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7912 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7912 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.792 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7926 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7926 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.7973 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8045 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8146 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8204 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8207 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8238 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.824 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.824 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8272 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8272 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8287 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8289 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8295 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8309 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8338 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8348 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8353 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8364 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8364 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8368 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.837 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.837 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8375 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8379 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.838 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.838 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8385 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8385 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8385 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8398 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8401 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8406 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8424 | 1.07/.94 | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8424 | 1.07/.94 | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8432 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.844 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8448 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8452 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8455 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8463 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8463 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8463 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8466 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8473 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8475 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8483 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8485 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8494 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8494 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8503 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8503 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8515 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8538 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8555 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8565 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8568 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8568 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8584 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8585 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8616 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8644 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8657 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8668 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8695 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8701 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8723 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8734 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8752 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8761 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8766 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8766 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8771 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8779 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8785 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8785 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8792 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.88 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8819 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8829 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8845 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8855 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 138 | 235 | 1.0008 | 0.8856 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8902 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8906 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8909 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8952 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8953 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.896 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.8962 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8966 | 1.07/.94 | N-1-1 | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8967 | 1.07/.94 | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8967 | 1.07/.94 | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8968 | 1.07/.94 | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8968 | 1.07/.94 | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8969 | 1.07/.94 | N-1-1 | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.897 | 1.07/.94 | N-1-1 | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8975 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8981 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8981 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8988 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8988 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.899 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.899 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8997 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8997 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8999 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9002 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9004 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9004 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9005 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9005 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9006 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9006 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.901 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.901 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.901 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.901 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9014 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9014 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9016 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9019 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9019 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9019 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9019 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9022 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9022 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9022 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9026 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9029 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9029 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9031 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9031 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9047 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9054 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9054 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9057 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9062 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9064 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9069 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9069 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9069 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9071 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9071 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9072 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9075 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9075 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9078 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9078 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9082 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9082 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9084 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9085 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9086 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9088 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9098 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9098 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9098 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9098 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.91 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.91 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9101 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9101 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9101 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 138 | 235 | 1.0008 | 0.9103 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9107 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9107 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9108 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9109 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9109 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9109 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9109 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9109 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.911 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9114 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9114 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9114 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9114 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9116 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9116 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9117 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9121 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9125 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9125 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9125 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9126 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9126 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9126 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9126 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9126 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9126 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9127 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9128 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9128 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9128 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9131 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9131 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9133 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9133 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9134 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9134 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9134 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 138 | 235 | 1.0008 | 0.9135 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9135 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9135 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9135 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9138 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9138 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9138 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9138 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.914 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.914 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.914 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.914 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9142 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9145 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9145 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9147 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9149 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9149 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.915 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9152 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9152 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9153 | 1.07/.94 | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9157 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9157 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9158 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9158 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9161 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9161 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9161 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9161 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9162 | 1.07/.94 | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9166 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9167 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9167 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9167 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9168 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9168 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9168 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9168 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9168 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9169 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9169 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.917 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.917 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.917 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9171 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9171 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9171 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9173 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9173 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9173 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9173 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9173 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9173 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9174 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9174 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9174 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9174 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9174 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9174 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9175 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9176 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9177 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9177 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9177 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9177 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9179 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9181 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9182 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9182 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9184 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9185 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9186 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232287 CHERITON_69 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9186 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9186 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9187 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9187 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9187 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9187 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9188 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9189 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9189 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9189 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9191 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9193 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9193 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9193 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9193 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9193 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9193 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9194 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9194 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9197 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9197 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9197 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9198 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9198 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9202 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9202 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9202 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9202 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9209 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9209 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9209 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.921 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9216 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9216 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9216 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9217 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9217 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9218 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9219 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9221 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9221 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9221 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9224 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9226 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9227 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9228 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9228 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9229 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.923 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.923 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9232 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9232 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9232 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9232 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9234 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9236 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9237 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9237 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9238 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9238 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9239 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9239 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9239 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.924 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.924 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9242 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232282 | CHINCOTG | 69 | 235 | 0.9966 | 0.9242 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9242 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9243 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9244 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9244 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9244 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9245 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9251 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9251 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9252 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9255 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9256 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9257 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9257 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9257 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9259 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9259 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.926 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9262 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.9263 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.9263 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9265 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232287 CHERITON_69 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9267 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9267 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9267 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9269 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.927 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.927 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9271 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9272 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9274 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9275 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9275 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9275 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9277 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9277 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9277 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9278 | 1.07/.94 | N-1-1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9279 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9282 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9282 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9282 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9282 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9282 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9282 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9282 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9283 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9283 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9284 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9284 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9286 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9287 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9287 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9287 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9287 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9287 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9287 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9288 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.929 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.929 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.929 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9291 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9291 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9292 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9292 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9292 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9292 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9292 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9294 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9295 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9295 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9295 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9297 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9297 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9299 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9299 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9299 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9299 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9299 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.93 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9301 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9303 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9303 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9303 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9303 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9305 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9305 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9306 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232283 | WALLOPS | 69 | 235 | 1.0024 | 0.9306 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9306 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9306 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9306 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9306 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9306 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9307 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9309 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9311 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9311 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9311 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232287 CHERITON_69 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9311 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9311 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232287 CHERITON_69 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9312 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9312 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9314 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9317 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.932 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9321 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9322 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9323 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9324 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.9326 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.9326 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9326 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9326 | 1.07/.94 | N-1-1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9326 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9326 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9327 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9327 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9328 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9329 | 1.07/.94 | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.933 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232285 | WALLOPST | 69 | 235 | 1.0045 | 0.933 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.933 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9333 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9334 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9334 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9335 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9336 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9336 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9336 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9337 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.934 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.934 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9341 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9341 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9342 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9342 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9343 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9343 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9343 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9343 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9344 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9345 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9347 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9347 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9347 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9347 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9348 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.935 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9352 | 1.07/.94 | N-1-1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9352 | 1.07/.94 | N-1-1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9353 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9353 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9353 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9354 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9354 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232132 OAK HALL 138 232133 WATTSVILLE 138 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9354 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9354 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9355 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9355 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9357 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9357 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9357 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9358 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9359 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9361 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9361 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9362 | 1.07/.94 | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9363 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9363 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232648 WATTSVL1 12.5 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9364 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9364 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9367 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | ODEC_P1-4_BELLHAVENSTATCOM_SRT-A
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9367 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232280 OAKHL_69 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9367 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232648 WATTSVL1 12.5
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9367 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232649 WATTSVL2 12.5
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9368 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9368 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9369 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.937 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9373 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9375 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9377 | 1.07/.94 | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9379 | 1.07/.94 | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9381 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9381 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9381 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232649 WATTSVL2 12.5 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9382 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9385 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9385 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9385 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.9385 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.9385 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9386 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9386 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9386 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9387 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9387 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9387 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9387 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9388 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232544 KELLAM 2 24.9 232286 KELLAM 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9388 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9388 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9388 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232647 WALLOPS1 12.5 232283 WALLOPS 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9389 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9389 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 1
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.9391 | 1.07/.94 | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9391 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9391 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9392 | 1.07/.94 | N-1-1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9393 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9393 | 1.07/.94 | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9393 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9393 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9393 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9393 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9393 | 1.07/.94 | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9394 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9394 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232287 CHERITON_69 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9394 | 1.07/.94 | N-1-1 | 232133 WATTSVILLE 138 232281 WATTSVIL 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9395 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9395 | 1.07/.94 | N-1-1 | G-232921 TASLEY2G 13.2 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9395 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | 232280 OAKHL_69 69 232132 OAK HALL 138 2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9395 | 1.07/.94 | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | S-P14_232281 WATTSVIL 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9396 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9397 | 1.07/.94 | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9397 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.9397 | 1.07/.94 | N-1-1 | S-P14_232287 CHERITON_69 69.0 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9398 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9398 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9398 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.9399 | 1.07/.94 | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9399 | 1.07/.94 | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0

## FERC Form 715 Volt Drop Detaild
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Vdrop(%) | Delta Voltage Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.7851 | -21.4% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.7857 | -21.34% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8149 | -18.42% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8264 | -17.27% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8583 | -14.08% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8689 | -13.02% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8693 | -12.98% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8737 | -12.54% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8805 | -11.86% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8896 | -10.95% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8896 | -10.95% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8908 | -10.83% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8908 | -10.83% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8917 | -10.74% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8918 | -10.73% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.8975 | -10.16% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232284 | TASLEY | 69 | 235 | 0.9991 | 0.898 | -10.11% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.6263 | -37.38% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.6275 | -37.26% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8092 | -19.09% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8125 | -18.76% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8151 | -18.5% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8243 | -17.58% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8375 | -16.26% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.842 | -15.81% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8511 | -14.9% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8569 | -14.32% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8604 | -13.97% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8609 | -13.92% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8609 | -13.92% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.862 | -13.81% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8629 | -13.72% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8629 | -13.72% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8865 | -11.36% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8865 | -11.36% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8891 | -11.1% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8892 | -11.09% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8905 | -10.96% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8918 | -10.83% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8919 | -10.82% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8945 | -10.56% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8966 | -10.35% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.898 | -10.21% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0001 | 0.8982 | -10.19% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.4861 | -49.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.4877 | -49.32% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.7348 | -24.61% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.7857 | -19.52% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.7918 | -18.91% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8003 | -18.06% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8037 | -17.72% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8167 | -16.42% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8204 | -16.05% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8204 | -16.05% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8234 | -15.75% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8234 | -15.75% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8254 | -15.55% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8306 | -15.03% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8311 | -14.98% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8325 | -14.84% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.835 | -14.59% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8385 | -14.24% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8446 | -13.63% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8502 | -13.07% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8539 | -12.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8539 | -12.7% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8545 | -12.64% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8545 | -12.64% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.855 | -12.59% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8565 | -12.44% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8565 | -12.44% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8625 | -11.84% | 10% | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8675 | -11.34% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9809 | 0.8801 | -10.08% | 10% | N-1-1 | S-P14_232281 WATTSVIL 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.509 | -47.42% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.5106 | -47.26% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.7474 | -23.58% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.7968 | -18.64% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8 | -18.32% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8027 | -18.05% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8033 | -17.99% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8161 | -16.71% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8299 | -15.33% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8306 | -15.26% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8306 | -15.26% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8336 | -14.96% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8336 | -14.96% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8344 | -14.88% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8355 | -14.77% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8409 | -14.23% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8424 | -14.08% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8439 | -13.93% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8481 | -13.51% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8533 | -12.99% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8538 | -12.94% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8538 | -12.94% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8558 | -12.74% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8558 | -12.74% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8596 | -12.36% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8632 | -12% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8642 | -11.9% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8736 | -10.96% | 10% | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9832 | 0.8784 | -10.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232287 CHERITON_69 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.8875 | -11.69% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.8971 | -10.73% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9003 | -10.41% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0044 | 0.9006 | -10.38% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8082 | -18.8% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8088 | -18.74% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8317 | -16.45% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8417 | -15.45% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8637 | -13.25% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8711 | -12.51% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8787 | -11.75% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8853 | -11.09% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8909 | -10.53% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9962 | 0.8912 | -10.5% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.811 | -18.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8146 | -18.34% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8151 | -18.29% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8226 | -17.54% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8652 | -13.28% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8818 | -11.62% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.8959 | -10.21% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.998 | 0.896 | -10.2% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.5678 | -42.08% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.5691 | -41.95% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.7797 | -20.89% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.7996 | -18.9% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8029 | -18.57% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8153 | -17.33% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8252 | -16.34% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8288 | -15.98% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8307 | -15.79% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8333 | -15.53% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8427 | -14.59% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8521 | -13.65% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8526 | -13.6% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8526 | -13.6% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8545 | -13.41% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8545 | -13.41% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8569 | -13.17% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8569 | -13.17% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8597 | -12.89% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8597 | -12.89% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8613 | -12.73% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.866 | -12.26% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8678 | -12.08% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8728 | -11.58% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8839 | -10.47% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8842 | -10.44% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8843 | -10.43% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.887 | -10.16% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9886 | 0.8879 | -10.07% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.5279 | -45.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.5294 | -45.55% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.7577 | -22.72% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.7997 | -18.52% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8031 | -18.18% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8059 | -17.9% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8117 | -17.32% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8158 | -16.91% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8295 | -15.54% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8339 | -15.1% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8391 | -14.58% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8391 | -14.58% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.842 | -14.29% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.842 | -14.29% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8434 | -14.15% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8438 | -14.11% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8489 | -13.6% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8506 | -13.43% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8528 | -13.21% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8533 | -13.16% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8534 | -13.15% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8553 | -12.96% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8553 | -12.96% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8561 | -12.88% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8674 | -11.75% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8709 | -11.4% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8718 | -11.31% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9849 | 0.8828 | -10.21% | 10% | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8118 | -19.07% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.814 | -18.85% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8635 | -13.9% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8641 | -13.84% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8647 | -13.78% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8909 | -11.16% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8909 | -11.16% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8935 | -10.9% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8935 | -10.9% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8937 | -10.88% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8939 | -10.86% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.894 | -10.85% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8976 | -10.49% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.8991 | -10.34% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9001 | -10.24% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0025 | 0.9009 | -10.16% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.5279 | -45.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.5294 | -45.55% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.7577 | -22.72% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.7997 | -18.52% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8031 | -18.18% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8059 | -17.9% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8117 | -17.32% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8158 | -16.91% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8295 | -15.54% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8339 | -15.1% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8391 | -14.58% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8391 | -14.58% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.842 | -14.29% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.842 | -14.29% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8434 | -14.15% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8438 | -14.11% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8489 | -13.6% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8506 | -13.43% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8528 | -13.21% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8533 | -13.16% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8534 | -13.15% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8553 | -12.96% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8553 | -12.96% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8561 | -12.88% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8674 | -11.75% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8709 | -11.4% | 10% | N-1-1 | NF_232284 TASLEY 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8718 | -11.31% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_G_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9849 | 0.8828 | -10.21% | 10% | N-1-1 | S-P14_232287 CHERITON_69 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.7852 | -20.9% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.7857 | -20.85% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8595 | -13.47% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8622 | -13.2% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8694 | -12.48% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8737 | -12.05% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8762 | -11.8% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8805 | -11.37% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8896 | -10.46% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.8896 | -10.46% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.891 | -10.32% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232284 | TASLEY | 69 | 235 | 0.9942 | 0.891 | -10.32% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.6266 | -36.57% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.6275 | -36.48% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8258 | -16.65% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8376 | -15.47% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8421 | -15.02% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8511 | -14.12% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8609 | -13.14% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8609 | -13.14% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8614 | -13.09% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8628 | -12.95% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8628 | -12.95% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8643 | -12.8% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9923 | 0.8698 | -12.25% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.4865 | -49% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.4877 | -48.88% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.7921 | -18.44% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8183 | -15.82% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8307 | -14.58% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8351 | -14.14% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | -13.99% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | -13.99% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | -13.99% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8366 | -13.99% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8446 | -13.19% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8498 | -12.67% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8545 | -12.2% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8545 | -12.2% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8548 | -12.17% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8563 | -12.02% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8566 | -11.99% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8567 | -11.98% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8567 | -11.98% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8583 | -11.82% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8618 | -11.47% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8642 | -11.23% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9765 | 0.8642 | -11.23% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.5094 | -46.86% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.5106 | -46.74% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8028 | -17.52% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8177 | -16.03% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8301 | -14.79% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8344 | -14.36% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8439 | -13.41% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | -13.16% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | -13.16% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | -13.16% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8464 | -13.16% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8538 | -12.42% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8538 | -12.42% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.856 | -12.2% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.856 | -12.2% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8575 | -12.05% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8592 | -11.88% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8634 | -11.46% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8642 | -11.38% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8655 | -11.25% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8659 | -11.21% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8711 | -10.69% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.978 | 0.8733 | -10.47% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9003 | -10.16% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0019 | 0.9006 | -10.13% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8084 | -18.35% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8088 | -18.31% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8639 | -12.8% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8721 | -11.98% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8728 | -11.91% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8849 | -10.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8853 | -10.66% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9919 | 0.8912 | -10.07% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8147 | -17.91% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8151 | -17.87% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8585 | -13.53% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8725 | -12.13% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232846 | PERDUE | 69 | 235 | 0.9938 | 0.8819 | -11.19% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.5681 | -41.37% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.5691 | -41.27% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8168 | -16.5% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.829 | -15.28% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8304 | -15.14% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8334 | -14.84% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8426 | -13.92% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8526 | -12.92% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8526 | -12.92% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8546 | -12.72% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8546 | -12.72% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8561 | -12.57% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8618 | -12% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8715 | -11.03% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8715 | -11.03% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8716 | -11.02% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9818 | 0.8716 | -11.02% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.5283 | -45.1% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.5294 | -44.99% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8117 | -16.76% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8173 | -16.2% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8296 | -14.97% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.834 | -14.53% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8434 | -13.59% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8533 | -12.6% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8534 | -12.59% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8555 | -12.38% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8555 | -12.38% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.857 | -12.23% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8628 | -11.65% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8669 | -11.24% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8719 | -10.74% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8732 | -10.61% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8735 | -10.58% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9793 | 0.8787 | -10.06% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.867 | -12.71% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 0.9941 | 0.8713 | -12.28% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.5283 | -45.1% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.5294 | -44.99% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8117 | -16.76% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8173 | -16.2% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8296 | -14.97% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.834 | -14.53% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8434 | -13.59% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8533 | -12.6% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8534 | -12.59% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8545 | -12.48% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8555 | -12.38% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8555 | -12.38% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.857 | -12.23% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8628 | -11.65% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8669 | -11.24% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8719 | -10.74% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8732 | -10.61% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8735 | -10.58% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_G_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9793 | 0.8787 | -10.06% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.5413 | -46.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.5414 | -46.56% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.6095 | -39.75% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.627 | -38% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8149 | -19.21% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8196 | -18.74% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8764 | -13.06% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8764 | -13.06% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.8984 | -10.86% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9001 | -10.69% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9001 | -10.69% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.007 | 0.9037 | -10.33% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5024 | -50.68% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5024 | -50.68% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5033 | -50.59% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.5591 | -45.01% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.6688 | -34.04% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.6772 | -33.2% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8545 | -15.47% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8546 | -15.46% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8665 | -14.27% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8712 | -13.8% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8772 | -13.2% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8816 | -12.76% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8816 | -12.76% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8836 | -12.56% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8839 | -12.53% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8839 | -12.53% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8849 | -12.43% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8914 | -11.78% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.8948 | -11.44% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0092 | 0.9036 | -10.56% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4244 | -56.59% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4752 | -51.51% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.4752 | -51.51% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.476 | -51.43% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.5353 | -45.5% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.5461 | -44.42% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.7833 | -20.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.7833 | -20.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.7963 | -19.4% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8147 | -17.56% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8147 | -17.56% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.854 | -13.63% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8618 | -12.85% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8622 | -12.81% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8642 | -12.61% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8648 | -12.55% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8697 | -12.06% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8713 | -11.9% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8719 | -11.84% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8778 | -11.25% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8782 | -11.21% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8782 | -11.21% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8795 | -11.08% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8837 | -10.66% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8859 | -10.44% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232286 KELLAM 69.0
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.886 | -10.43% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9903 | 0.8897 | -10.06% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4463 | -54.62% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4768 | -51.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4768 | -51.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.4776 | -51.49% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.5569 | -43.56% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.5674 | -42.51% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.7943 | -19.82% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.7944 | -19.81% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8072 | -18.53% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8251 | -16.74% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8251 | -16.74% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8634 | -12.91% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8641 | -12.84% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8705 | -12.2% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.871 | -12.15% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8715 | -12.1% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8732 | -11.93% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8771 | -11.54% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8775 | -11.5% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8775 | -11.5% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8787 | -11.38% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8787 | -11.38% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8808 | -11.17% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8852 | -10.73% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8888 | -10.37% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232843 | EASTVILL | 69 | 235 | 0.9925 | 0.8924 | -10.01% | 10% | N-1-1 | S-P14_232286 KELLAM 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8547 | -15.6% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8632 | -14.75% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.8899 | -12.08% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9088 | -10.19% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0107 | 0.9088 | -10.19% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.5358 | -46.91% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.5358 | -46.91% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.6624 | -34.25% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.6782 | -32.67% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8365 | -16.84% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8406 | -16.43% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8855 | -11.94% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8856 | -11.93% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0049 | 0.8933 | -11.16% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.5959 | -40.98% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.5959 | -40.98% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.6047 | -40.1% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8413 | -16.44% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8453 | -16.04% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8883 | -11.74% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.8884 | -11.73% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0057 | 0.9045 | -10.12% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4828 | -51.5% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4828 | -51.5% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.4837 | -51.41% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.5025 | -49.53% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.6128 | -38.5% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.622 | -37.58% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8228 | -17.5% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8228 | -17.5% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8352 | -16.26% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8517 | -14.61% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8517 | -14.61% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8629 | -13.49% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8691 | -12.87% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8756 | -12.22% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.876 | -12.18% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.876 | -12.18% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8771 | -12.07% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8836 | -11.42% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8872 | -11.06% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8875 | -11.03% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8946 | -10.32% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8951 | -10.27% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8961 | -10.17% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9978 | 0.8963 | -10.15% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4644 | -52.98% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4785 | -51.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4785 | -51.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.4793 | -51.49% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.5749 | -41.93% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.5849 | -40.93% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8034 | -19.08% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8035 | -19.07% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8162 | -17.8% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8337 | -16.05% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8337 | -16.05% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8637 | -13.05% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.87 | -12.42% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8712 | -12.3% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8766 | -11.76% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8769 | -11.73% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8769 | -11.73% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8781 | -11.61% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8786 | -11.56% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8791 | -11.51% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8806 | -11.36% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8847 | -10.95% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8862 | -10.8% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8881 | -10.61% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 232890 | KENDGROV | 69 | 235 | 0.9942 | 0.8882 | -10.6% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5082 | -50.35% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5082 | -50.35% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.5686 | -44.31% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8594 | -15.23% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8594 | -15.23% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8862 | -12.55% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.8862 | -12.55% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0117 | 0.9102 | -10.15% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4644 | -52.98% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4785 | -51.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4785 | -51.57% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.4793 | -51.49% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.5749 | -41.93% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.5849 | -40.93% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8034 | -19.08% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8035 | -19.07% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8162 | -17.8% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8337 | -16.05% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8337 | -16.05% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8637 | -13.05% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.87 | -12.42% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8712 | -12.3% | 10% | N-1-1 | NF_232284 TASLEY 69 232286 KELLAM 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8766 | -11.76% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8769 | -11.73% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8769 | -11.73% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8781 | -11.61% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8786 | -11.56% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8791 | -11.51% | 10% | N-1-1 | NF_232284 TASLEY 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8806 | -11.36% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8847 | -10.95% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8862 | -10.8% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8881 | -10.61% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232284 TASLEY 69.0
| 2025_JAN_N_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9942 | 0.8882 | -10.6% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5447 | -45.61% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5454 | -45.54% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.546 | -45.48% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.546 | -45.48% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5484 | -45.24% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5484 | -45.24% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.6091 | -39.17% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8151 | -18.57% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8239 | -17.69% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8654 | -13.54% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.889 | -11.18% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.889 | -11.18% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8904 | -11.04% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8985 | -10.23% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.502 | -49.69% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5096 | -48.93% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5104 | -48.85% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5111 | -48.78% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5111 | -48.78% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5136 | -48.53% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.5136 | -48.53% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.6692 | -32.97% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.6847 | -31.42% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8464 | -15.25% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8713 | -12.76% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8755 | -12.34% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.877 | -12.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8828 | -11.61% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8831 | -11.58% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8846 | -11.43% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8847 | -11.42% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8866 | -11.23% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8866 | -11.23% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8873 | -11.16% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8873 | -11.16% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.892 | -10.69% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8936 | -10.53% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8936 | -10.53% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8937 | -10.52% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232286 | KELLAM | 69 | 235 | 0.9989 | 0.8977 | -10.12% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4755 | -50.48% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4811 | -49.92% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.482 | -49.83% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4829 | -49.74% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4829 | -49.74% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4852 | -49.51% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.4852 | -49.51% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.5357 | -44.46% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.5559 | -42.44% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.7734 | -20.69% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8099 | -17.04% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8211 | -15.92% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8211 | -15.92% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.822 | -15.83% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8221 | -15.82% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.834 | -14.63% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8357 | -14.46% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.865 | -11.53% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.871 | -10.93% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8771 | -10.32% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8776 | -10.27% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8792 | -10.11% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232287 | CHERITON_69 | 69 | 235 | 0.9803 | 0.8792 | -10.11% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.477 | -50.54% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.483 | -49.94% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4839 | -49.85% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4847 | -49.77% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4847 | -49.77% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4871 | -49.53% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.4871 | -49.53% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.5574 | -42.5% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.5767 | -40.57% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.7848 | -19.76% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.82 | -16.24% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8312 | -15.12% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8312 | -15.12% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8321 | -15.03% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8322 | -15.02% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8438 | -13.86% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8455 | -13.69% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8643 | -11.81% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8703 | -11.21% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8763 | -10.61% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8768 | -10.56% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8784 | -10.4% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232843 | EASTVILL | 69 | 235 | 0.9824 | 0.8785 | -10.39% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.809 | -19.85% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8094 | -19.81% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8097 | -19.78% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8097 | -19.78% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8116 | -19.59% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8116 | -19.59% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.8551 | -15.24% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0075 | 0.89 | -11.75% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5947 | -40.47% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5953 | -40.41% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5958 | -40.36% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5958 | -40.36% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5981 | -40.13% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.5981 | -40.13% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.6623 | -33.71% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8367 | -16.27% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8445 | -15.49% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8782 | -12.12% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.885 | -11.44% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.885 | -11.44% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9994 | 0.8934 | -10.6% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.6043 | -39.61% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8414 | -15.9% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8491 | -15.13% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8937 | -10.67% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232846 | PERDUE | 69 | 235 | 1.0004 | 0.8937 | -10.67% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4827 | -50.48% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4896 | -49.79% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4904 | -49.71% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4911 | -49.64% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4911 | -49.64% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4936 | -49.39% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.4936 | -49.39% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.6132 | -37.43% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.6304 | -35.71% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.814 | -17.35% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.846 | -14.15% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8572 | -13.03% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8573 | -13.02% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.858 | -12.95% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.858 | -12.95% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8631 | -12.44% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8689 | -11.86% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8691 | -11.84% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8707 | -11.68% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8749 | -11.26% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8752 | -11.23% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8769 | -11.06% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8769 | -11.06% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8843 | -10.32% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8856 | -10.19% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.8856 | -10.19% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232847 | WEIRWOOD | 69 | 235 | 0.9875 | 0.886 | -10.15% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4785 | -50.56% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4848 | -49.93% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4857 | -49.84% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4865 | -49.76% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4865 | -49.76% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4889 | -49.52% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.4889 | -49.52% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.5753 | -40.88% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.594 | -39.01% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.7941 | -19% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8284 | -15.57% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8396 | -14.45% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8396 | -14.45% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8404 | -14.37% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8405 | -14.36% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8519 | -13.22% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8536 | -13.05% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8639 | -12.02% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8698 | -11.43% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8758 | -10.83% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8762 | -10.79% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8779 | -10.62% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232890 | KENDGROV | 69 | 235 | 0.9841 | 0.8779 | -10.62% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5159 | -48.5% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5166 | -48.43% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5173 | -48.36% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5173 | -48.36% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5198 | -48.11% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.5198 | -48.11% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8518 | -14.91% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8805 | -12.04% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8916 | -10.93% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8916 | -10.93% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8922 | -10.87% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8922 | -10.87% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8963 | -10.46% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0009 | 0.8963 | -10.46% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4785 | -50.56% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4848 | -49.93% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4857 | -49.84% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4865 | -49.76% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4865 | -49.76% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4889 | -49.52% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.4889 | -49.52% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.5753 | -40.88% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.594 | -39.01% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.7941 | -19% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8284 | -15.57% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8396 | -14.45% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8396 | -14.45% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8404 | -14.37% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8405 | -14.36% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8519 | -13.22% | 10% | N-1-1 | NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8536 | -13.05% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8639 | -12.02% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8698 | -11.43% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8758 | -10.83% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8762 | -10.79% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8779 | -10.62% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2025_JAN_N_B1_S00 | 233901 | CHERRYDALE C | 69 | 235 | 0.9841 | 0.8779 | -10.62% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.838 | -16.92% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.838 | -16.92% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.9022 | -10.5% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0072 | 0.906 | -10.12% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.8583 | -15.95% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.8583 | -15.95% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9107 | -10.71% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9112 | -10.66% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9134 | -10.44% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0178 | 0.9134 | -10.44% | 10% | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8306 | -17.48% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8306 | -17.48% | 10% | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8629 | -14.25% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8629 | -14.25% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.8899 | -11.55% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0054 | 0.9018 | -10.36% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8306 | -17.7% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8306 | -17.7% | 10% | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8658 | -14.18% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8658 | -14.18% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.8899 | -11.77% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0076 | 0.903 | -10.46% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.8469 | -15.52% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 1.0021 | 0.8469 | -15.52% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8307 | -17.26% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8307 | -17.26% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8955 | -10.78% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232846 | PERDUE | 69 | 235 | 1.0033 | 0.8993 | -10.4% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_KELLAM_CHERITON_6750
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.8614 | -15.03% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.8614 | -15.03% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0117 | 0.9055 | -10.62% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.8676 | -14.14% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.8676 | -14.14% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.009 | 0.9037 | -10.53% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.8578 | -16.12% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.8578 | -16.12% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.019 | 0.9121 | -10.69% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.8676 | -14.14% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.8676 | -14.14% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_SUM_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.009 | 0.9037 | -10.53% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | G-233901 CHERRYDALE C 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5211 | -47.97% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5211 | -47.97% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5258 | -47.5% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5258 | -47.5% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5313 | -46.95% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.5313 | -46.95% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8045 | -19.63% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8364 | -16.44% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8466 | -15.42% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8585 | -14.23% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8701 | -13.07% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.88 | -12.08% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232284 | TASLEY | 69 | 235 | 1.0008 | 0.8856 | -11.52% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5038 | -50.86% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5038 | -50.86% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5075 | -50.49% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5075 | -50.49% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5139 | -49.85% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.5139 | -49.85% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.792 | -22.04% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.844 | -16.84% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8455 | -16.69% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8485 | -16.39% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8616 | -15.08% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8695 | -14.29% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8723 | -14.01% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8792 | -13.32% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.8829 | -12.95% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9064 | -10.6% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9069 | -10.55% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9069 | -10.55% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9078 | -10.46% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9078 | -10.46% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | -10.28% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | -10.28% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | -10.28% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232286 | KELLAM | 69 | 235 | 1.0124 | 0.9096 | -10.28% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4891 | -51.22% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4891 | -51.22% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4927 | -50.86% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4927 | -50.86% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4989 | -50.24% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.4989 | -50.24% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.7818 | -21.95% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8146 | -18.67% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8289 | -17.24% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8309 | -17.04% | 10% | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8353 | -16.6% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8368 | -16.45% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8375 | -16.38% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8406 | -16.07% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8424 | -15.89% | 10% | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8483 | -15.3% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8503 | -15.1% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8752 | -12.61% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | -12.08% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | -12.08% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | -12.08% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8805 | -12.08% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8902 | -11.11% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8909 | -11.04% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8952 | -10.61% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8966 | -10.47% | 10% | N-1-1 | NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8967 | -10.46% | 10% | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8969 | -10.44% | 10% | N-1-1 | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8975 | -10.38% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.899 | -10.23% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8997 | -10.16% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.8997 | -10.16% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9006 | -10.07% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232287 | CHERITON_69 | 69 | 235 | 1.0013 | 0.9006 | -10.07% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.491 | -51.21% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.491 | -51.21% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.4946 | -50.85% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.4946 | -50.85% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.5009 | -50.22% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.5009 | -50.22% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.7832 | -21.99% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8207 | -18.24% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8287 | -17.44% | 10% | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8348 | -16.83% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8364 | -16.67% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8379 | -16.52% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8424 | -16.07% | 10% | N-1-1 | P12_KELLAM_CHERITON_6750 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8432 | -15.99% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8463 | -15.68% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8503 | -15.28% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_KELLAM_CHERITON_6750
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8538 | -14.93% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8761 | -12.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | -11.74% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | -11.74% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | -11.74% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8857 | -11.74% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8953 | -10.78% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.896 | -10.71% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8967 | -10.64% | 10% | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.897 | -10.61% | 10% | N-1-1 | NF_232843 EASTVILL 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.8999 | -10.32% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9002 | -10.29% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9005 | -10.26% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9005 | -10.26% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9014 | -10.17% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9014 | -10.17% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232843 | EASTVILL | 69 | 235 | 1.0031 | 0.9026 | -10.05% | 10% | N-1-1 | S-P14_232284 TASLEY 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7839 | -21.67% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7839 | -21.67% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7912 | -20.94% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7912 | -20.94% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7926 | -20.8% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.7926 | -20.8% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232844 | HALLWOOD | 69 | 235 | 1.0006 | 0.8962 | -10.44% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5637 | -43.14% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5637 | -43.14% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5692 | -42.59% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5692 | -42.59% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5736 | -42.15% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.5736 | -42.15% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8204 | -17.47% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8475 | -14.76% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8565 | -13.86% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8668 | -12.83% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8771 | -11.8% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8855 | -10.96% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232845 | PARKSLEY | 69 | 235 | 0.9951 | 0.8906 | -10.45% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.7973 | -19.89% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8295 | -16.67% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8398 | -15.64% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8734 | -12.28% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8785 | -11.77% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232846 | PERDUE | 69 | 235 | 0.9962 | 0.8785 | -11.77% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.495 | -51.16% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.495 | -51.16% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.4987 | -50.79% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.4987 | -50.79% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.505 | -50.16% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.505 | -50.16% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.7858 | -22.08% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8238 | -18.28% | 10% | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8338 | -17.28% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8385 | -16.81% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8401 | -16.65% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8473 | -15.93% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8555 | -15.11% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8584 | -14.82% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8657 | -14.09% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8779 | -12.87% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | -10.98% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | -10.98% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | -10.98% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.8968 | -10.98% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9016 | -10.5% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9022 | -10.44% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9022 | -10.44% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9031 | -10.35% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9031 | -10.35% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232847 | WEIRWOOD | 69 | 235 | 1.0066 | 0.9062 | -10.04% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4921 | -51.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4921 | -51.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4957 | -50.83% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.4957 | -50.83% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.5019 | -50.21% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.5019 | -50.21% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.7839 | -22.01% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.824 | -18% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8272 | -17.68% | 10% | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.837 | -16.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.838 | -16.6% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8385 | -16.55% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8463 | -15.77% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8494 | -15.46% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8568 | -14.72% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8766 | -12.74% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8968 | -10.72% | 10% | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8981 | -10.59% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.8988 | -10.52% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9004 | -10.36% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.901 | -10.3% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.901 | -10.3% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9019 | -10.21% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9019 | -10.21% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 232890 | KENDGROV | 69 | 235 | 1.004 | 0.9029 | -10.11% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5063 | -50.7% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5063 | -50.7% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.51 | -50.33% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.51 | -50.33% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5164 | -49.69% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.5164 | -49.69% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8448 | -16.85% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8452 | -16.81% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8515 | -16.18% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8644 | -14.89% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8819 | -13.14% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.8845 | -12.88% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | -10.13% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | -10.13% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | -10.13% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 232903 | BELLHAVN | 69 | 235 | 1.0133 | 0.912 | -10.13% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4921 | -51.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4921 | -51.19% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4957 | -50.83% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.4957 | -50.83% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.5019 | -50.21% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.5019 | -50.21% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.7839 | -22.01% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.824 | -18% | 10% | N-1-1 | NF_232284 TASLEY 69 232846 PERDUE 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8272 | -17.68% | 10% | N-1-1 | NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.837 | -16.7% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232284 TASLEY 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.838 | -16.6% | 10% | N-1-1 | P12_OAKHILL_TASLEY_6778 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8385 | -16.55% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232903 BELLHAVN 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8463 | -15.77% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8494 | -15.46% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8568 | -14.72% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | P12_OAKHILL_TASLEY_6778
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8766 | -12.74% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | S-P14_232286 KELLAM 69.0
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8885 | -11.55% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8968 | -10.72% | 10% | N-1-1 | NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8981 | -10.59% | 10% | N-1-1 | NF_232286 KELLAM 69 232903 BELLHAVN 69 1 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.8988 | -10.52% | 10% | N-1-1 | S-P14_232903 BELLHAVN 69.0 | G-232905 CHERITON_25 24.9
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9004 | -10.36% | 10% | N-1-1 | NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.901 | -10.3% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | G-232921 TASLEY2G 13.2
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.901 | -10.3% | 10% | N-1-1 | P12_TASLEY_KELLAM_6703 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9019 | -10.21% | 10% | N-1-1 | G-232921 TASLEY2G 13.2 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9019 | -10.21% | 10% | N-1-1 | 232921 TASLEY2G 13.2 232284 TASLEY 69 1 | P12_TASLEY_KELLAM_6703
| 2030_WIN_B0_S00 | 233901 | CHERRYDALE C | 69 | 235 | 1.004 | 0.9029 | -10.11% | 10% | N-1-1 | G-232905 CHERITON_25 24.9 | S-P14_232903 BELLHAVN 69.0

## FERC Form 715 Short Circuit (hidden)
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | Bus KV | Area | Breaker | Rating Type | DUTY_P | DUTY_A | BKR_CAPA (A) | Pre-fault Voltage (KV) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment

## FERC Form 715 Stability (hidden)
Reserved(FG# assigned by PJM) | Analysis dynamics case info | Stability issue category | Bus # | Bus Name | Area | Stability Contingency description | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment

## FERC Form 715 Other
Reserved(FG# assigned by PJM) | Analysis Case | Areas | Facility Name | Violations details | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment

## Ratings_Ref (hidden)
Identifier | Line | Line Section | From Bus | To Bus | SUM - A | SUM - B | SUM - C | SUM - D | WIN - A | WIN - B | WIN - C | WIN - D | THM SUM - A | THM SUM - B | THM SUM - C | THM SUM - D | THM WIN - A | THM WIN - B | THM WIN - C | THM WIN - D | SUM2030 Rating | WIN2025 Rating | SUM2025 Conductor Rating | WIN2025 Conductor Rating | WIN2030 Rating
232284232903 | 6703 | 6703-1 | 232284 | 232903 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 114 | 150 | 150 | 163 | 139 | 177 | 177 | 193 | 97/97/97/97 | 97/97/97/97 | 114/150/150/163 | 139/177/177/193 | 97/97/97/97
232903232286 | 6703 | 6703-2 | 232903 | 232286 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 114 | 150 | 150 | 163 | 139 | 177 | 177 | 193 | 97/97/97/97 | 97/97/97/97 | 114/150/150/163 | 139/177/177/193 | 97/97/97/97
232284232286 | 6721 | 6721-1 | 232284 | 232286 | 76 | 104 | 104 | 104 | 99 | 104 | 104 | 104 | 114 | 150 | 150 | 163 | 139 | 177 | 177 | 193 | 76/104/104/104 | 99/104/104/104 | 114/150/150/163 | 139/177/177/193 | 99/104/104/104
232281232285 | 6745 | 6745-1 | 232281 | 232285 | 57 | 77 | 77 | 77 | 35 | 35 | 35 | 35 | 68 | 91 | 91 | 93 | 78 | 103 | 103 | 105 | 57/77/77/77 | 35/35/35/35 | 68/91/91/93 | 78/103/103/105 | 57/77/77/77
232285232282 | 6745 | 6745-2 | 232285 | 232282 | 57 | 77 | 77 | 77 | 35 | 35 | 35 | 35 | 68 | 91 | 91 | 93 | 78 | 103 | 103 | 105 | 57/77/77/77 | 35/35/35/35 | 68/91/91/93 | 78/103/103/105 | 57/77/77/78
232281232282 | 6746 | 6746-1 | 232281 | 232282 | 57 | 77 | 77 | 77 | 35 | 35 | 35 | 35 | 68 | 91 | 91 | 93 | 78 | 103 | 103 | 105 | 57/77/77/77 | 35/35/35/35 | 68/91/91/93 | 78/103/103/105 | 57/77/77/79
232283232285 | 6748 | 6748-1 | 232283 | 232285 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 68 | 91 | 91 | 93 | 78 | 103 | 103 | 105 | 35/35/35/35 | 35/35/35/35 | 68/91/91/93 | 78/103/103/105 | 35/35/35/35
232286232847 | 6750 | 6750-1 | 232286 | 232847 | 140 | 176 | 176 | 176 | 59 | 82 | 82 | 84 | 43 | 65 | 65 | 67 | 59 | 82 | 82 | 84 | 140/176/176/176 | 59/82/82/84 | 43/65/65/67 | 59/82/82/84 | 160/198/198/198
232847232890 | 6750 | 6750-2 | 232847 | 232890 | 140 | 176 | 176 | 176 | 59 | 82 | 82 | 84 | 43 | 65 | 65 | 67 | 59 | 82 | 82 | 84 | 140/176/176/176 | 59/82/82/84 | 43/65/65/67 | 59/82/82/84 | 160/198/198/199
232890232843 | 6750 | 6750-3 | 232890 | 232843 | 140 | 176 | 176 | 176 | 59 | 82 | 82 | 84 | 43 | 65 | 65 | 67 | 59 | 82 | 82 | 84 | 140/176/176/176 | 59/82/82/84 | 43/65/65/67 | 59/82/82/84 | 160/198/198/200
232843232287 | 6750 | 6750-4 | 232843 | 232287 | 140 | 176 | 176 | 176 | 59 | 82 | 82 | 84 | 43 | 65 | 65 | 67 | 59 | 82 | 82 | 84 | 140/176/176/176 | 59/82/82/84 | 43/65/65/67 | 59/82/82/84 | 160/198/198/201
232280232846 | 6778 | 6778-1 | 232280 | 232846 | 114 | 135 | 135 | 142 | 135 | 135 | 135 | 142 | 114 | 150 | 150 | 163 | 139 | 177 | 177 | 193 | 114/135/135/142 | 135/135/135/142 | 114/150/150/163 | 139/177/177/193 | 135/135/135/142
232284232846 | 6778 | 6778-2 | 232284 | 232846 | 99 | 135 | 135 | 142 | 129 | 135 | 135 | 142 | 114 | 150 | 150 | 163 | 139 | 177 | 177 | 193 | 99/135/135/142 | 129/135/135/142 | 114/150/150/163 | 139/177/177/193 | 129/135/135/142
232280232844 | 6790 | 6790-1 | 232280 | 232844 | 87 | 114 | 114 | 118 | 100 | 128 | 128 | 134 | 87 | 114 | 114 | 118 | 100 | 128 | 128 | 134 | 87/114/114/118 | 100/128/128/134 | 87/114/114/118 | 100/128/128/134 | 100/128/128/134
232844232845 | 6790 | 6790-2 | 232844 | 232845 | 87 | 114 | 114 | 118 | 100 | 128 | 128 | 134 | 87 | 114 | 114 | 118 | 100 | 128 | 128 | 134 | 87/114/114/118 | 100/128/128/134 | 87/114/114/118 | 100/128/128/134 | 100/128/128/134
232284232845 | 6790 | 6790-3 | 232284 | 232845 | 87 | 114 | 114 | 118 | 100 | 128 | 128 | 134 | 87 | 114 | 114 | 118 | 100 | 128 | 128 | 134 | 87/114/114/118 | 100/128/128/134 | 87/114/114/118 | 100/128/128/134 | 100/128/128/134

## Contingency_Ref (hidden)
Contingency Name | Contingency Type | Contingency Description
232280 OAKHL_69 69 232132 OAK HALL 138 1 | P1-3 | Loss of Oakhall Transformer #1
P12_TASLEY_KELLAM_6703 | P1-2 | Loss of 6703 line
P12_OAKHILL_TASLEY_6778 | P1-2 | Loss of 6778 line
NF_232280 OAKHL_69 69 232846 PERDUE 69 1 | P1-2 | Loss of 6778 - line section Oakhall to Perdue
NF_232844 HALLWOOD 69 232845 PARKSLEY 69 1 | P1-2 | Loss of 6790 - line section Hallwood to Parksley
NF_232284 TASLEY 69 232846 PERDUE 69 1 | P1-2 | Loss of 6778 - line section Perdue to Tasley
232280 OAKHL_69 69 232132 OAK HALL 138 2 | P1-3 | Loss of Oakhall Transformer #2
G-232905 CHERITON_25 24.9 | P1-1 | Loss of Cheriton Generator
G-232921 TASLEY2G 13.2 | P1-1 | Loss of Tasley Generator
P12_KELLAM_CHERITON_6750 |  | Loss of 6750 line
NF_232286 KELLAM 69 232847 WEIRWOOD 69 1 |  | Loss of 6750 - line section Kellam to Weirwood
NF_232287 CHERITON_69 69 232843 EASTVILL 69 1 |  | Loss of 6750 - line section Cheriton to Eastville
NF_232843 EASTVILL 69 232890 KENDGROV 69 1 |  | Loss of 6750 - line section Eastville to Kendgrov
G-233901 CHERRYDALE C 69.0 |  | Loss of Cherrydale Generator
NF_232890 KENDGROV 69 233901 CHERRYDALE C 69 1 |  | Loss of 6750 - line section Kendgrove to Cherrydale
S-P14_232284 TASLEY 69.0 |  | Loss of Tasley Shunt
S-P14_232903 BELLHAVN 69.0 |  | Loss of Bell Haven Shunt
NF_232284 TASLEY 69 232286 KELLAM 69 1 |  | Loss of 6721 line
NF_232286 KELLAM 69 232903 BELLHAVN 69 1 |  | Loss of 6703 - line section Kellam to Bell Haven
NF_232284 TASLEY 69 232903 BELLHAVN 69 1 |  | Loss of 6703 - line section Tasley to Bell Haven
S-P14_232286 KELLAM 69.0 |  | Loss of Kellam Shunt
232921 TASLEY2G 13.2 232284 TASLEY 69 1 |  | Loss of Tasley Generator Transformer
NF_232284 TASLEY 69 232845 PARKSLEY 69 1 |  | Loss of 6790 - line section Tasley to Parksley
NF_232280 OAKHL_69 69 232844 HALLWOOD 69 1 |  | Loss of 6790 - line section Oakhall to Hallwood
S-P14_232287 CHERITON_69 69.0 |  | Loss of Cheriton Shunt
S-P14_232281 WATTSVIL 69.0 |  | Loss of Wattsville Shunt
NF_232847 WEIRWOOD 69 232890 KENDGROV 69 1 |  | Loss of 6750 - line section Kendgrov to Weirwood
232132 OAK HALL 138 232133 WATTSVILLE 138 1 |  | Loss of line from Oak Hall to Wattsville 138kV
232133 WATTSVILLE 138 232281 WATTSVIL 69 1 |  | Loss of Wattsville Transformer
NF_232280 OAKHL_69 69 232281 WATTSVIL 69 1 |  | Loss of line from Oak Hall to Wattsville 69 kV
NF_232281 WATTSVIL 69 232282 CHINCOTG 69 1 |  | Loss of line from Wattsville to Chincotg
NF_232281 WATTSVIL 69 232285 WALLOPST 69 1 |  | Loss of line from Wattsville to Wallopst
NF_232281 WATTSVIL 69 232290 SIGNPOST 69 1 |  | Loss of line from Wattsville to Signpost
NF_232282 CHINCOTG 69 232285 WALLOPST 69 1 |  | Loss of line from Chincotg to Wallopst
NF_232283 WALLOPS 69 232285 WALLOPST 69 1 |  | Loss of line from Wallops to Wallopst
232642 CHNCOTG1 12.5 232282 CHINCOTG 69 1 |  | Loss of line from Chincotg 1 to Chincotg
232643 CHNCOTG2 12.5 232282 CHINCOTG 69 1 |  | Loss of line from Chincotg 2 to Chincotg
232647 WALLOPS1 12.5 232283 WALLOPS 69 1 |  | Loss of Wallops 1 Load Transformer
232648 WATTSVL1 12.5 232281 WATTSVIL 69 1 |  | Loss of Wattsville 1 Load Transformer
232649 WATTSVL2 12.5 232281 WATTSVIL 69 1 |  | Loss of Wattsville 2 Load Transformer
ODEC_P1-4_BELLHAVENSTATCOM_SRT-A |  | Loss of Bell Haven Statcom
P12_OAKHILL_TASLEY_6790 |  | Loss of 6790 line
S-P14_232280 OAKHL_69 69.0 |  | Loss of Oak Hall Shunt
S-P14_232648 WATTSVL1 12.5 |  | Loss of Wattsville 1 Load
S-P14_232649 WATTSVL2 12.5 |  | Loss of Wattsville 2 Load
232544 KELLAM 2 24.9 232286 KELLAM 69 1 |  | Loss of Kellam 2 Load Transformer
232553 OAKHALL1 24.9 232132 OAK HALL 138 1 |  | Loss of Oakhall Transformer
232556 TASLEY 1 24.9 232284 TASLEY 69 1 |  | Loss of Tasley 1 Load Transformer
232557 TASLEY 4 24.9 232284 TASLEY 69 1 |  | Loss of Tasley 2 Load Transformer
P12_DPL_CKT 6750_RTEP |  | Loss of 6750 line
NF_232286 KELLAM 69 232287 CHERITON_69 69 1 |  | Loss of Express Line
232905 CHERITON_25 24.9 232287 CHERITON_69 69 1 |  | Loss of Tasley Generator Transformer
232543 KELLAM 1 24.9 232286 KELLAM 69 1 |  | Loss of Kellam 1 Load Transformer
S-P14:232280 OAKHL_69 69.0 |  | Loss of Oak Hall Shunt
S-P14:232281 WATTSVIL 69.0 |  | Loss of Wattsville Shunt
S-P14:232284 TASLEY 69.0 |  | Loss of Tasley Shunt
S-P14:232286 KELLAM 69.0 |  | Loss of Kellam Shunt
S-P14:232287 CHERITON_69 69.0 |  | Loss of Cheriton Shunt
S-P14:232648 WATTSVL1 12.5 |  | Loss of Wattsville 1 Shunt
S-P14:232649 WATTSVL2 12.5 |  | Loss of Wattsville 2 Shunt
S-P14:232903 BELLHAVN 69.0 |  | Loss of Bell Haven Shunt
NF_232274 PINEY_69 69 232839 M OLIVE1 69 1 |  | Loss of DPL Line - Piney to M Olive
NF_232277 KENNEY 69 232839 M OLIVE1 69 1 |  | Loss of DPL Line - Kenny to M Olive
232646 POCMOKE2 12.5 232130 POCOMOKE 138 1 |  | Loss of DPL Transformer - Pocmoke2
NF_230912 PINEYCAP 69 232274 PINEY_69 69 1 |  | Loss of DPL Transformer - Piney Cap
NF_232272 M HERMON 69 232274 PINEY_69 69 1 |  | Loss of DPL Line - M Hermon to Piney
232274 PINEY_69 69 232128 PINEY138 138 1 |  | Loss of DPL Transformer - Piney
NF_232277 KENNEY 69 232278 STOCKTON 69 1 |  | Loss of DPL Line - Kenney to Stockton
P12_DPL_CKT 6712_SRT-A |  | Loss of 6712 line
P11_DPL_OH 1-3 NUG_SRT-A |  | Loss of N Church Generation - Oh Nug 1-3
BLANK |  | No contingency run