## Notes
Thermal analysis column headings
Column Heading | Title | Description
Reserved(FG# assinged by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Fr Bus | From Bus Number | PSSE model bus number corresponding to the FROM bus of a facility identified as a potential violation
Fr Name | From Bus Name | PSSE model bus name corresponding to the FROM bus of a facility identified as a potential violation
To Bus | To Bus Number | PSSE model bus number corresponding to the TO bus of a facility identified as a potential violation
To Name | To Bus Name | PSSE model bus name corresponding to the TO bus of a facility identified as a potential violation
Tert Bus | Tertiary Bus Number | PSSE model bus number corresponding to the tertiary bus of a facility identified as a potential violation
Tert Name | Tertiary Bus Name | PSSE model bus name corresponding to the tertiary bus of a facility identified as a potential violation
CKT | Circuit | Circuit number of identified potential violation
KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Rating | Facility Rating | Applicable thermal rating (MVA) of facility
DC Ld(%) | Direct Current Loading percentage | Percentage above Line Rating determined from DC testing
AC Ld(%) | Alternating Current Loading percentage | Percentage above Line Rating determined from AC testing
Cont Type | Contingency Type | N-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Conductor Rating (MVA) | Conductor Rating | Normal/Long Term Emergency/Short Term Emergency/Load Dump ratings of conductor
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Magnitude analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Upper/Lower Limit | High/Low Voltage Limit (P.U.) | Threshold of Per Unit High/Low voltage, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Type | Contingency 2 Type | N-1-1 Contingency categorization (e.g., Single, Bus, Line_FB, Tower)
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Voltage Drop analysis column headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation
Bus Name | Bus Name | PSSE model bus name corresponding to the bus of a facility identified as a potential violation
KV | Kilovolt level | Kilovolt level of bus identified as potential violation
Area | Area Number | Area number of bus identified as potential violation
BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied
ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied
Vdrop (%) | Voltage Drop | The percentage that the voltage has dropped as a result of the contingency
Delta Voltage Limit | Voltage Drop Limit | Threshold of percentage drop, if ContVolt is over this limit, a potential violation is identified
Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower, N-1-1)
Cont 1 Name | Contingency 1 Name | N-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 1 Description | Contingency 1 Description | N-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
Cont 2 Name | Contingency 2 Name | N-1-1 Contingency name as identified in associated contingency file or embedded in the spreadsheet
Contingency 2 Description | Contingency 2 Description | N-1-1 Contingency description as identified in associated contingency file or embedded in the spreadsheet
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Short Circuit analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Bus # | Bus Number | Short Circuit model bus number where breaker is located
Bus Name | Bus Name | Aspen bus name and voltage where breaker is located
Bus KV | BUS Voltage | Nominal BUS voltage
Area | Area Number | Area number of bus identified as potential violation
Breaker | Breaker Name | Breaker name as given by Transmission Owner
Rating Type | Type of Breaker | Symmetrical (S) or Total (T) rated type of breaker
DUTY_P | Duty Percentage | The percentage of the asymmetrical fault current divided by breaker capacity
DUTY_A | Asymmetrical Fault Current | The combination of the symmetrical component and the direct current component of the current.
BKR_CAPA (A) | Breaker Capacity | Breaker’s derated interrupting capability, (A)
Pre-fault Voltage (KV) | Pre-fault KV | Voltage on the bus prior to fault event
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Stability analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis dynamics case info. | Analysis dynamics case info. | Dynamics case year, loading condition, MMWG Series. For example, MMWG 2018 Series 2023 SLL case.
Stability issue category | Stability issue category | Stability issue category: transient stability or damping or dynamic voltage recovery or voltage ride through
Bus # | Bus number | Bus number of the identified plant or station in the analysis power flow model.
Bus Name | Bus name | Bus name of the identified plant or station in the analysis power flow model.
Area | Area | Area number of the identified plant or station.
Stability Contingency description | Contingency description | Detailed contingency description that causes the identified potential stability issue including sequence and fault clearing times.
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Other analysis headings
Column Heading | Title | Description
Reserved(FG# assigned by PJM) | FG# | PJM use only
Analysis Case | Analysis Case | Case title to use in replicating analysis
Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line
Facility Name | Facility Name | Facilities such as line, substation, generator, etc.
Violations details | Violations details | TO to describe the details of the violation
PJM Accepting Proposals | PJM Accepting Proposals | PJM use only
715 Criteria Description | FERC Form 715 Criteria Description | Reference to applicable section of FERC Form 715 criteria
Justification for applicable exclusion from receiving competitive proposals | Justification for applicable exclusion from receiving competitive proposals | PJM use only
Comment | TO Comments if needed | Additional information needed
Purpose of FERC FORM 715 VIOLATION SUBMISSIONS:
PJM seeks Transmission Owner (TO) criteria violation submissions on facilities in accordance with Local TO criteria. This would also include violations which are not power flow violations of criteria.
Criteria applied by Transmission Owner:
FERC Form 715 Analysis (Thermal/Voltage Magnitude/Voltage Drop/Short Circuit/Stability/Other)
TERMINOLOGY USED IN TEMPLATE:
Descriptions of the column headings used in each Excel tab are provided below.
ANALYSIS PROCEDURE:
Transmission Owners are expected to identify FERC Form 715 violations. All violations are to be captured and recorded in the applicable Excel tab. Please use the corresponding tabs based on the type of violation below:
  * FERC Form 715 Thermal tab should be used to enter thermal violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Magnitude tab should be used to enter voltage magnitude violations associated with FERC Form 715 criteria
  * FERC Form 715 Voltage Drop tab should be used to enter voltage drop/rise violations associated with FERC Form 715 criteria
  * FERC Form 715 Short Circuit tab should be used to enter short circuit violations associated with FERC Form 715 criteria
  * FERC Form 715 Stability tab should be used to enter stability violations associated with FERC Form 715 criteria
  * FERC Form 715 Other tab should be used to enter violations associated with FERC Form 715 criteria which can not be included in the other tabs
TRANSMISSION OWNER CRITERIA:
In addition to the NERC and PJM criteria included in RTEP studies, PJM also considers Transmission Owner specific criteria. Individual TO criteria can be found at the following link:
http://pjm.com/planning/planning-criteria/to-planning-criteria.aspx

## FERC Form 715 Thermal
Reserved(FG# assigned by PJM) | Analysis Case | Fr Bus | Fr Name | To Bus | To Name | Tert Bus | Tert Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Cont 1 Name | Cont 2 Name | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025W1-AEP-T1 | 2030 LL RTEP | 245864 | 05AUGLAIZE | 245904 | 05SHERWOOD |  |  | 1 | 69 | 205 | 47 | 105.04 | 103.71 | Breaker | AEP_P4_#17337_05PLATTERCRK69.0_CB1_SRT-A | N/A | Summer Normal 47 MVA, Summer Emergency 47 MVA | Yes | FERC 715 Part 4 Thermal N-1
2025W1-AEP-T2 | 2030 LL RTEP | 290390 | 05PLATTERCRK | 245904 | 05SHERWOOD |  |  | 1 | 69 | 205 | 47 | 116.06 | 114.13 | Breaker | AEP_P4_#17337_05PLATTERCRK69.0_CB1_SRT-A | N/A | Summer Normal 47 MVA, Summer Emergency 47 MVA | Yes | 715 Part 4 Gen Deliv
2025W1-AEP-T3 | 2030 SUMMER RTEP | 290390 | 05PLATTERCRK | 245904 | 05SHERWOOD |  |  | 1 | 69 | 205 | 47 | 163.93 | 161.73 | Breaker | AEP_P4_#17337_05PLATTERCRK69.0_CB1_SRT-A | N/A | Summer Normal 47 MVA, Summer Emergency 47 MVA | Yes | FERC 715 Part 4 Thermal GD
2025W1-AEP-T4 | 2030 LL RTEP | 245904 | 05SHERWOOD | 290390 | 05PLATTERCRK |  |  | 1 | 69 | 205 | 47 | 115.58 | 113.65 | Breaker | AEP_P4_#17337_05PLATTERCRK69.0_CB1_SRT-A | N/A | Summer Normal 47 MVA, Summer Emergency 47 MVA | Yes | FERC 715 Part 4 Thermal N-1
2025W1-AEP-T5 | 2030 LL RTEP | 245904 | 05SHERWOOD | 245864 | 05AUGLAIZE |  |  | 1 | 69 | 205 | 47 | 105.49 | 104.15 | Breaker | AEP_P4_#17337_05PLATTERCRK69.0_CB1_SRT-A | N/A | Summer Normal 47 MVA, Summer Emergency 47 MVA | Yes | 715 Part 4 Gen Deliv
2025W1-AEP-T6 | 2030 SUMMER RTEP | 245904 | 05SHERWOOD | 245864 | 05AUGLAIZE |  |  | 1 | 69 | 205 | 47 | 159.46 | 158.51 | Breaker | AEP_P4_#17337_05PLATTERCRK69.0_CB1_SRT-A | N/A | Summer Normal 47 MVA, Summer Emergency 47 MVA | Yes | FERC 715 Part 4 Thermal GD
2025-W1-AEP-T7 | 2030 WINTER RTEP | 243063 | 05N.NEWARK1 | 245513 | 05N.NEWARK1 |  |  | 1 | 138/69 | 205 | 53 | 102.76 | 101.99 | N-1-1 | AEP_P1-2_#11508_957_SRT-A | AEP_P1-3_#11510_05N.NEWARK2 138_2_SRT-A | Winter Normal 49 MVA, Winter Emergency 53 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T8 | 2030 WINTER RTEP | 243063 | 05N.NEWARK1 | 245513 | 05N.NEWARK1 |  |  | 1 | 138/69 | 205 | 53 | 107.22 | 107.55 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#11510_05N.NEWARK2 138_2_SRT-A | Winter Normal 49 MVA, Winter Emergency 53 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T9 | 2030 WINTER RTEP | 243063 | 05N.NEWARK1 | 245513 | 05N.NEWARK1 |  |  | 1 | 138/69 | 205 | 53 | 108.62 | 108.62 | N-1-1 | AEP_P1-2_#5734_2322_SRT-A | AEP_P1-3_#11510_05N.NEWARK2 138_2_SRT-A | Winter Normal 49 MVA, Winter Emergency 53 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T10 | 2030 WINTER RTEP | 243063 | 05N.NEWARK1 | 245513 | 05N.NEWARK1 |  |  | 1 | 138/69 | 205 | 53 | 102.54 | 102.74 | N-1-1 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-3_#11510_05N.NEWARK2 138_2_SRT-A | Winter Normal 49 MVA, Winter Emergency 53 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T11 | 2030 WINTER RTEP | 243063 | 05N.NEWARK1 | 245513 | 05N.NEWARK1 |  |  | 1 | 138/69 | 205 | 53 | 102.57 | 102.43 | N-1-1 | AEP_P1-2_#9854_SRT-A | AEP_P1-3_#11510_05N.NEWARK2 138_2_SRT-A | Winter Normal 49 MVA, Winter Emergency 53 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025W1-AEP-T12 | 2030 SUMMER RTEP | 246687 | 05TRABUE | 290174 | 05HILLIARD2 |  |  | 1 | 69 | 205 | 73 | 127.23 | 127.45 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T13 | 2030 SUMMER RTEP | 246687 | 05TRABUE | 290174 | 05HILLIARD2 |  |  | 1 | 69 | 205 | 73 | 127.23 | 127.62 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T14 | 2030 SUMMER RTEP | 246588 | 05HILLIARD1 | 288638 | 05DAVIDS |  |  | 1 | 69 | 205 | 90 | 117.19 | 117.67 | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | Summer Normal 73 MVA, Summer Emergency 90 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T15 | 2030 SUMMER RTEP | 246588 | 05HILLIARD1 | 288638 | 05DAVIDS |  |  | 1 | 69 | 205 | 90 | 137.45 | 137.66 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | Summer Normal 73 MVA, Summer Emergency 90 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T16 | 2030 SUMMER RTEP | 246588 | 05HILLIARD1 | 288638 | 05DAVIDS |  |  | 1 | 69 | 205 | 90 | 117.19 | 117.32 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | Summer Normal 73 MVA, Summer Emergency 90 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T17 | 2030 WINTER RTEP | 246588 | 05HILLIARD1 | 288638 | 05DAVIDS |  |  | 1 | 69 | 205 | 106 | 100.41 | 100.25 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | Winter Normal 91 MVA, Winter Emergency 106 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T18 | 2030 SUMMER RTEP | 246588 | 05HILLIARD1 | 288638 | 05DAVIDS |  |  | 1 | 69 | 205 | 90 | 137.45 | 137.96 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | Summer Normal 73 MVA, Summer Emergency 90 MVA | Yes | 715 Part 4 Thermal N-1-1
2025W1-AEP-T19 | 2030 WINTER RTEP | 246588 | 05HILLIARD1 | 288638 | 05DAVIDS |  |  | 1 | 69 | 205 | 106 | 100.42 | 100.25 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | Winter Normal 91 MVA, Winter Emergency 106 MVA | Yes | 715 Part 4 Thermal N-1-1
2025-W1-AEP-T20 | 2030 WINTER RTEP | 244033 | 05CATAWBA | 244034 | 05CATAWBEQ |  |  | 1 | 69/1.0 | 205 | 117 | 113.4 | 112.9 | N-1-1 | AEP_P1-2_#11307_334_SRT-A | AEP_P1-3_#13885_05HANCK1 138_1_SRT-A | Winter Normal 117 MVA, Winter Emergency 117 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T21 | 2030 WINTER RTEP | 244033 | 05CATAWBA | 244034 | 05CATAWBEQ |  |  | 1 | 69/1.0 | 205 | 117 | 121.22 | 120.45 | N-1-1 | AEP_P1-3_#12037_05HUNTCT 138_1_SRT-A | AEP_P1-3_#13885_05HANCK1 138_1_SRT-A | Winter Normal 117 MVA, Winter Emergency 117 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T22 | 2030 WINTER RTEP | 244033 | 05CATAWBA | 244034 | 05CATAWBEQ |  |  | 1 | 69/1.0 | 205 | 117 | 121.22 | 120.42 | N-1-1 | AEP_P1-3_#13885_05HANCK1 138_1_SRT-A | AEP_P1-3_#12037_05HUNTCT 138_1_SRT-A | Winter Normal 117 MVA, Winter Emergency 117 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T23 | 2030 WINTER RTEP | 244033 | 05CATAWBA | 244034 | 05CATAWBEQ |  |  | 1 | 69/1.0 | 205 | 117 | 121.17 | 120.34 | N-1-1 | AEP_P1-3_#13885_05HANCK1 138_1_SRT-A | AEP_P1-3_#16602_05ROANO2 138_5_SRT-A | Winter Normal 117 MVA, Winter Emergency 117 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T24 | 2030 WINTER RTEP | 244033 | 05CATAWBA | 244034 | 05CATAWBEQ |  |  | 1 | 69/1.0 | 205 | 117 | 121.17 | 120.41 | N-1-1 | AEP_P1-3_#16602_05ROANO2 138_5_SRT-A | AEP_P1-3_#13885_05HANCK1 138_1_SRT-A | Winter Normal 117 MVA, Winter Emergency 117 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T25 | 2030 SUMMER RTEP | 244772 | 05COLE | 246657 | 05GALLOWAY1 |  |  | 1 | 69 | 205 | 82 | 109.23 | 109.21 | N-1-1 | AEP_P1-3_#11597_05HARRISON 138_1_SRT-A | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | Summer Normal 65 MVA, Summer Emergency 82 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T26 | 2030 SUMMER RTEP | 244772 | 05COLE | 246657 | 05GALLOWAY1 |  |  | 1 | 69 | 205 | 82 | 109.21 | 109.21 | N-1-1 | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | AEP_P1-3_#11597_05HARRISON 138_1_SRT-A | Summer Normal 65 MVA, Summer Emergency 82 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T27 | 2030 SUMMER RTEP | 243829 | 05ELLIOTT | 243833 | 05OHIO UNIV |  |  | 1 | 69 | 205 | 73 | 146.2 | 143.49 | N-1-1 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#707_8315_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T28 | 2030 SUMMER RTEP | 243829 | 05ELLIOTT | 243833 | 05OHIO UNIV |  |  | 1 | 69 | 205 | 73 | 143.56 | 140.83 | N-1-1 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#6764_21618_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T29 | 2030 SUMMER RTEP | 243829 | 05ELLIOTT | 243833 | 05OHIO UNIV |  |  | 1 | 69 | 205 | 73 | 142.09 | 139.28 | N-1-1 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#734_8011_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T30 | 2030 SUMMER RTEP | 243829 | 05ELLIOTT | 243833 | 05OHIO UNIV |  |  | 1 | 69 | 205 | 73 | 141.61 | 138.79 | N-1-1 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5939_1202255_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T31 | 2030 SUMMER RTEP | 243829 | 05ELLIOTT | 243833 | 05OHIO UNIV |  |  | 1 | 69 | 205 | 73 | 141.31 | 138.45 | N-1-1 | AEP_P1-2_#16351_SRT-A | AEP_P1-2_#5933_902255_SRT-A | Summer Normal 73 MVA, Summer Emergency 73 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T32 | 2030 SUMMER RTEP | 245747 | 05FINDLAY C | 245749 | 05FNDCTREQ |  |  | 1 | 35/1.0 | 205 | 45 | 100.79 | 101.06 | N-1-1 | AEP_P1-2_#7759_11700706_SRT-A | AEP_P1-3_#15308_05NWOODC 138_1_SRT-A | Summer Normal 45 MVA, Summer Emergency 45 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T33 | 2030 SUMMER RTEP | 245747 | 05FINDLAY C | 245749 | 05FNDCTREQ |  |  | 1 | 35/1.0 | 205 | 45 | 100.79 | 101.05 | N-1-1 | AEP_P1-3_#15308_05NWOODC 138_1_SRT-A | AEP_P1-2_#7759_11700706_SRT-A | Summer Normal 45 MVA, Summer Emergency 45 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T34 | 2030 WINTER RTEP | 246352 | 05HAVILAND2 | 243169 | 05HAVILND2 | N/A | N/A | 4 | 138/69 | 205 | 113 | 115.43 | 116.2 | Bus | AEP_P2-2_#10084_05HAVILAND1 138_1_SRT-A | N/A | Winter Normal 119 MVA, Winter Emergency 119 MVA | No | FERC 715 Part 4 Thermal GD | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T35 | 2030 WINTER RTEP | 246352 | 05HAVILAND2 | 243169 | 05HAVILND2 | N/A | N/A | 4 | 138/69 | 205 | 113 | 115.43 | 116.2 | Breaker | AEP_P4_#10084_05HAVILAND1 138_I_SRT-A | N/A | Winter Normal 119 MVA, Winter Emergency 119 MVA | No | FERC 715 Part 4 Thermal GD | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T36 | 2030 WINTER RTEP | 243610 | 05LICK | 244549 | 05IRONMAN SW |  |  | 1 | 69 | 205 | 121 | 123.01 | 117.28 | N-1-1 | AEP_P1-2_#18202_SRT-A | AEP_P1-2_#6764_21618_SRT-A | Winter Normal 94 MVA, Winter Emergency 121 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T37 | 2030 WINTER RTEP | 243610 | 05LICK | 244549 | 05IRONMAN SW |  |  | 1 | 69 | 205 | 121 | 123.02 | 120.84 | N-1-1 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#18202_SRT-A | Winter Normal 94 MVA, Winter Emergency 121 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T38 | 2030 WINTER RTEP | 243610 | 05LICK | 244549 | 05IRONMAN SW |  |  | 1 | 69 | 205 | 121 | 112.85 | 110.29 | N-1-1 | AEP_P1-3_#6781_05BIERSR 345_1_SRT-A | AEP_P1-2_#18202_SRT-A | Winter Normal 94 MVA, Winter Emergency 121 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T39 | 2030 SUMMER RTEP | 243610 | 05LICK | 244549 | 05IRONMAN SW |  |  | 1 | 69 | 205 | 110 | 108.81 | 108.66 | Breaker | AEP_P4_#9723_05LICK 138_103_SRT-A | N/A | Summer Normal 75 MVA, Summer Emergency 110 MVA | No | FERC 715 Part 4 Thermal GD | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T40 | 2030 SUMMER RTEP | 243610 | 05LICK | 244549 | 05IRONMAN SW |  |  | 1 | 69 | 205 | 110 | 108.81 | 108.66 | Breaker | AEP_P4_#9724_05LICK 138_104_SRT-A | N/A | Summer Normal 75 MVA, Summer Emergency 110 MVA | No | FERC 715 Part 4 Thermal GD | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T41 | 2030 LL RTEP | 247383 | 05N.VANWRTSS | 245907 | 05VAN WERT |  |  | 1 | 69 | 205 | 53 | 140.43 | 140.78 | Breaker | AEP_P4_#18285_05POTTAWATOM69.0_CB1_SRT-A | N/A | Summer Normal 148 MVA, Summer Emergency 206 MVA | No | 715 Part 4 Gen Deliv | Substation Equipment Exclusion
2025-W1-AEP-T42 | 2030 LL RTEP | 247383 | 05N.VANWRTSS | 245907 | 05VAN WERT |  |  | 1 | 69 | 205 | 53 | 140.34 | 140.72 | Breaker | AEP_P4_#18287_05POTTAWATOM69.0_CB3_SRT-A | N/A | Summer Normal 148 MVA, Summer Emergency 206 MVA | No | 715 Part 4 Gen Deliv | Substation Equipment Exclusion
2025-W1-AEP-T43 | 2030 LL RTEP | 247383 | 05N.VANWRTSS | 245907 | 05VAN WERT |  |  | 1 | 69 | 205 | 53 | 139.66 | 139.91 | Tower | AEP_P7-1_#11068___SRT-A | N/A | Summer Normal 148 MVA, Summer Emergency 206 MVA | No | 715 Part 4 Gen Deliv | Substation Equipment Exclusion
2025-W1-AEP-T44 | 2030 WINTER RTEP | 245840 | 05S SIDE | 290064 | 05LIMA PMPSS |  |  | 1 | 35 | 205 | 32 | 116.875 | 117.25 | Breaker | AEP_P4_#10091_05ROCKHILL1 138_E_SRT-A | N/A | Winter Normal 30 MVA, Winter Emergency 32 MVA | No | 715 Part 4 Thermal N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T45 | 2030 SUMMER RTEP | 242886 | 05SKIMMR | 314861 | 3SKIMMER |  |  | 2 | 69/115 | 205/345 | 68 | 106.67 | 105.53 | N-1-1 | AEP_P1-2_#3174_6_SRT-A | AEP_P1-3_#11296_3SKIMMER 115_1_SRT-A | Summer Normal 60 MVA, Summer Emergency 68 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T46 | 2030 SUMMER RTEP | 242886 | 05SKIMMR | 314861 | 3SKIMMER |  |  | 1 | 69/115 | 205/345 | 68 | 105.87 | 104.73 | N-1-1 | AEP_P1-2_#3174_6_SRT-A | AEP_P1-3_#13259_3SKIMMER 115_2_SRT-A | Summer Normal 60 MVA, Summer Emergency 68 MVA | No | 715 Part 4 Thermal N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-T47 | 2030 LL RTEP | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 53 | 104.24 | 104.58 | Breaker | AEP_P4_#18285_05POTTAWATOM69.0_CB1_SRT-A | N/A | Summer Normal 148 MVA, Summer Emergency 206 MVA | No | FERC 715 Part 4 Thermal N-1 | Substation Equipment Exclusion
2025-W1-AEP-T48 | 2030 LL RTEP | 245907 | 05VAN WERT | 247383 | 05N.VANWRTSS |  |  | 1 | 69 | 205 | 53 | 104.15 | 104.53 | Breaker | AEP_P4_#18287_05POTTAWATOM69.0_CB3_SRT-A | N/A | Summer Normal 148 MVA, Summer Emergency 206 MVA | No | FERC 715 Part 4 Thermal N-1 | Substation Equipment Exclusion
2025-W1-AEP-T49 | 2030 SUMMER RTEP | 246879 | 05S KENTN1 | 246874 | 05KENTON |  |  | 1 | 69 | 205 | 35 | 123.37 | 122.28 | Breaker | AEP_P4_#17792_05SKENTO 138_CB2_SRT-A | N/A | Summer Normal 35 MVA, Summer Emergency 35 MVA | No | FERC 715 Part 4 Thermal GD | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Voltage Magnitude
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Upper/Lower Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025-W1-AEP-VM1 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 1.0115 | 0.7692 | 1.05/0.92 PU | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM2 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 1.0115 | 0.7692 | 1.05/0.92 PU | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM3 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 1.0115 | 0.7884 | 1.05/0.92 PU | BUS | EKPC_P2-2_FALCON 69_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM4 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 1.0035 | 0.8192 | 1.05/0.92 PU | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM5 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 1.0035 | 0.8192 | 1.05/0.92 PU | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM6 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 1.0035 | 0.8395 | 1.05/0.92 PU | BUS | EKPC_P2-2_FALCON 69_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM7 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0987 | 1.05/0.92 PU | BRANCH | 244333 05AMONTLTS 34.5 247161 05FARADAY 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM8 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0987 | 1.05/0.92 PU | BRANCH | 247150 05FARADAY 138 247161 05FARADAY 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM9 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0989 | 1.05/0.92 PU | BRANCH | 244333 05AMONTLTS 34.5 244350 05HICKORGP 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM10 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0992 | 1.05/0.92 PU | BRANCH | 244350 05HICKORGP 34.5 244356 05MCDOWELL 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM11 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0993 | 1.05/0.92 PU | LINEFB | AEP_P4_#15807_05FARADAY 34.5_F_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM12 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0995 | 1.05/0.92 PU | BRANCH | 244310 05TAZEWELL 34.5 244356 05MCDOWELL 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM13 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0996 | 1.05/0.92 PU | BUS | AEP_P2-2_#15795_05MCDOWELL 34.5_1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM14 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0996 | 1.05/0.92 PU | LINEFB | AEP_P4_#15795_05MCDOWELL 34.5_A_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM15 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.0997 | 1.05/0.92 PU | LINEFB | AEP_P4_#15796_05MCDOWELL 34.5_B_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM16 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.1032 | 1.05/0.92 PU | BUS | AEP_P2-2_#8428_05FARADAY 138_1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM17 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.1032 | 1.05/0.92 PU | LINEFB | AEP_P4_#10358_05FARADAY 138_C_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM18 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.1032 | 1.05/0.92 PU | LINEFB | AEP_P4_#15808_05FARADAY 34.5_D_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM19 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | 1.1033 | 1.05/0.92 PU | LINEFB | AEP_P4_#14194_05FARADAY 138_B_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM20 | Winter 2030 | 244310 | 05TAZEWELL | 34.5 | 205 | 1.0859 | - | 1.05/0.92 PU | BASE | Base Case | N/A | No | FERC 715 Part 4 Voltage N-0 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM21 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.0969 | 1.05/0.92 PU | BRANCH | 244333 05AMONTLTS 34.5 247161 05FARADAY 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM22 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.0969 | 1.05/0.92 PU | BRANCH | 247150 05FARADAY 138 247161 05FARADAY 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM23 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.0974 | 1.05/0.92 PU | BRANCH | 244333 05AMONTLTS 34.5 244350 05HICKORGP 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM24 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.0985 | 1.05/0.92 PU | BRANCH | 244350 05HICKORGP 34.5 244356 05MCDOWELL 34.5 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM25 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.0986 | 1.05/0.92 PU | LINEFB | AEP_P4_#15807_05FARADAY 34.5_F_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM26 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.1014 | 1.05/0.92 PU | BUS | AEP_P2-2_#8428_05FARADAY 138_1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM27 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.1014 | 1.05/0.92 PU | LINEFB | AEP_P4_#10358_05FARADAY 138_C_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM28 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.1014 | 1.05/0.92 PU | LINEFB | AEP_P4_#15808_05FARADAY 34.5_D_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM29 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | 1.1015 | 1.05/0.92 PU | LINEFB | AEP_P4_#14194_05FARADAY 138_B_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM30 | Winter 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0641 | - | 1.05/0.92 PU | BASE | Base Case | N/A | No | FERC 715 Part 4 Voltage N-0 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM31 | Winter 2030 | 244692 | 05BALLAH SS | 69 | 205 | 1.0006 | 0.879 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15075_SRT-A | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM32 | Winter 2030 | 246624 | 05GENOA 1 | 69 | 205 | 0.953 | 0.9165 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM33 | Winter 2030 | 246624 | 05GENOA 1 | 69 | 205 | 0.9499 | 0.9165 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM34 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9559 | 0.9188 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM35 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9236 | 0.9131 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM36 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9236 | 0.9022 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#5800_676_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM37 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9527 | 0.9188 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM38 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9236 | 0.9186 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#762_8072_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM39 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9527 | 0.9131 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM40 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9571 | 0.9022 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM41 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9559 | 0.9144 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM42 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9646 | 0.9186 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM43 | Winter 2030 | 246626 | 05WESTRVL4 | 69 | 205 | 0.9606 | 0.9131 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#9655_14218_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM44 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9182 | 0.9077 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM45 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9182 | 0.8967 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#5800_676_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM46 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9182 | 0.9132 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#762_8072_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM47 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9591 | 0.9077 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM48 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9736 | 0.9154 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#18090_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM49 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9638 | 0.8967 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM50 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9742 | 0.9154 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM51 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9737 | 0.915 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM52 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9622 | 0.9089 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM53 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9747 | 0.9159 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#730_590_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM54 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9709 | 0.9132 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM55 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9671 | 0.9076 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#9655_14218_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM56 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9742 | 0.9152 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM57 | Winter 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.9748 | 0.916 | 1.05/0.92 PU | N-1-1 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM58 | Winter 2030 | 246628 | 05WESTRVL1 | 69 | 205 | 0.9518 | 0.915 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM59 | Winter 2030 | 246628 | 05WESTRVL1 | 69 | 205 | 0.9349 | 0.9138 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#5800_676_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM60 | Winter 2030 | 246628 | 05WESTRVL1 | 69 | 205 | 0.9487 | 0.915 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM61 | Winter 2030 | 246628 | 05WESTRVL1 | 69 | 205 | 0.9526 | 0.9138 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM62 | Winter 2030 | 246642 | 05WESTRV2A | 69 | 205 | 0.953 | 0.9164 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM63 | Winter 2030 | 246642 | 05WESTRV2A | 69 | 205 | 0.9499 | 0.9164 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM64 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9158 | 0.9052 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM65 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9158 | 0.8943 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#5800_676_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM66 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9158 | 0.9108 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | AEP_P1-2_#762_8072_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM67 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9841 | 0.9138 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM68 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9683 | 0.9052 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM69 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9828 | 0.913 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#18090_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM70 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9733 | 0.8942 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM71 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9833 | 0.913 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM72 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9828 | 0.9125 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM73 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9714 | 0.9065 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM74 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9838 | 0.9135 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#730_590_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM75 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9801 | 0.9108 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM76 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9765 | 0.9052 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#9655_14218_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM77 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9834 | 0.9128 | 1.05/0.92 PU | N-1-1 | AEP_P1-3_#7218_05VASSEL 765_1_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM78 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.984 | 0.9136 | 1.05/0.92 PU | N-1-1 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM79 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9861 | 0.9137 | 1.05/0.92 PU | BRANCH | 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM80 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9861 | 0.9158 | 1.05/0.92 PU | LINEFB | AEP_P4_#11531_05GENOA 69.0_64_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM81 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9861 | 0.9158 | 1.05/0.92 PU | SINGLE | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM82 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9158 | - | 1.05/0.92 PU | SINGLE | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM83 | Winter 2030 | 246648 | 05BEATTY | 69 | 205 | 0.997 | 0.8582 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15075_SRT-A | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM84 | Winter 2030 | 246657 | 05GALLOWAY1 | 69 | 205 | 0.9758 | 0.8331 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15075_SRT-A | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM85 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 0.998 | 0.7833 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM86 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 1.0023 | 0.7834 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM87 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 1.0009 | 0.7484 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM88 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 0.998 | 0.7487 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM89 | Winter 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9864 | 0.8206 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM90 | Winter 2030 | 247093 | 05BLAIR | 69 | 205 | 0.985 | 0.8209 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM91 | Winter 2030 | 247841 | 05NAUTILUS1 | 69 | 205 | 0.9859 | 0.836 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM92 | Winter 2030 | 247841 | 05NAUTILUS1 | 69 | 205 | 0.9884 | 0.836 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM93 | Winter 2030 | 247841 | 05NAUTILUS1 | 69 | 205 | 0.9875 | 0.8132 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM94 | Winter 2030 | 247841 | 05NAUTILUS1 | 69 | 205 | 0.9859 | 0.8135 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM95 | Winter 2030 | 290190 | 05GALLOWAY2 | 69 | 205 | 0.9758 | 0.8331 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15075_SRT-A | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM96 | Winter 2030 | 290191 | 05GALLOWAY3 | 69 | 205 | 0.9758 | 0.8331 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15075_SRT-A | AEP_P1-3_#15083_05BEATTY 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM97 | Winter 2030 | 290344 | 05NAUTILUS2 | 69 | 205 | 0.9859 | 0.8359 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM98 | Winter 2030 | 290344 | 05NAUTILUS2 | 69 | 205 | 0.9884 | 0.836 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM99 | Winter 2030 | 290344 | 05NAUTILUS2 | 69 | 205 | 0.9875 | 0.8132 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM100 | Winter 2030 | 290344 | 05NAUTILUS2 | 69 | 205 | 0.9859 | 0.8134 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM101 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.8659 | - | 1.05/0.92 PU | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM102 | Summer 2030 | 243755 | 05FALCON | 46 | 205 | 0.8949 | - | 1.05/0.92 PU | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM103 | Summer 2030 | 244356 | 05MCDOWELL | 34.5 | 205 | 1.0666 | - | 1.05/0.92 PU | BASE | Base Case | N/A | No | FERC 715 Part 4 Voltage N-0 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM104 | Summer 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.97859 | 0.91469 | 1.05/0.92 PU | SINGLE | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM105 | Summer 2030 | 246627 | 05WESTRVL5 | 69 | 205 | 0.97859 | 0.9135 | 1.05/0.92 PU | BRANCH | 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM106 | Summer 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.98815 | 0.91203 | 1.05/0.92 PU | SINGLE | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM107 | Summer 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.98815 | 0.91083 | 1.05/0.92 PU | BRANCH | 246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM108 | Summer 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9806 | 0.7882 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM109 | Summer 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9844 | 0.7885 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM110 | Summer 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9855 | 0.8107 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM111 | Summer 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9806 | 0.8124 | 1.05/0.92 PU | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM112 | LL 2030 | 244506 | 05LIMBERLOST | 69 | 205 | 1.0017 | 1.0541 | 1.05/0.92 PU | N-1-1 | 244506 05LIMBERLOST 69.0 246260 05S BERNE 69.0 1_SRT-A | AEP_P1-2_#18289_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM113 | LL 2030 | 245911 | 05W VAN WR | 34.5 | 205 | 1.0441 | 1.0508 | 1.05/0.92 PU | N-1-1 | DAY_P1_6663_CELINA-STMARYS_69KV_SRT-A | DAY_P1_69##_COLDWATER-CHICKA_69KV_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM114 | LL 2030 | 245911 | 05W VAN WR | 34.5 | 205 | 1.0441 | 1.0601 | 1.05/0.92 PU | N-1-1 | DAY_P1_6663_CELINA-STMARYS_69KV_SRT-A | DAY_P1_6688_COLDWATER-GRAND_LAKE_69KV_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM115 | LL 2030 | 246639 | 05MARA_BOCK | 69 | 205 | 1.0096 | 1.0524 | 1.05/0.92 PU | N-1-1 | 246020 05N PORTLN 69.0 246638 05BOCKOVENSS 69.0 1_SRT-A | AEP_P1-2_#11915_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VM116 | LL 2030 | 246639 | 05MARA_BOCK | 69 | 205 | 1.0096 | 1.0524 | 1.05/0.92 PU | N-1-1 | 246020 05N PORTLN 69.0 246638 05BOCKOVENSS 69.0 1_SRT-A | AEP_P1-2_#18290_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Voltage Drop
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | KV | Area | BaseVolt | ContVolt | Vdrop(%) | Delta Voltage Limit | Cont Type | Cont 1 Name | Cont 2 Name | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025-W1-AEP-VD1 | Winter 2030 | 242886 | 05SKIMMR | 69 | 205 | 0.9878 | 0.899 | 8.874 | 0.08 | N-1-1 | DVP_P1-2: LN 30_SRT-A | AEP_P1-2_#11295_251_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD2 | Winter 2030 | 242886 | 05SKIMMR | 69 | 205 | 0.9878 | 0.8991 | 8.874 | 0.08 | N-1-1 | DVP_P1-3: 3SKIMMER-3SKIMMER_SRT-A | AEP_P1-2_#11295_251_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD3 | Winter 2030 | 243213 | 05MARA_LUNAT | 34.5 | 205 | 1.0118 | 0.9302 | 8.156 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD4 | Winter 2030 | 243213 | 05MARA_LUNAT | 34.5 | 205 | 1.012 | 0.9302 | 8.179 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD5 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 0.9981 | 0.8755 | 12.266 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | AEP_P1-2_#7389_17037_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD6 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 0.9981 | 0.8813 | 11.687 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | AEP_P1-3_#11485_05THELMA 138_3_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD7 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 0.9981 | 0.8815 | 11.667 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | AEP_P1-2_#12138_206_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD8 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 0.9981 | 0.9164 | 8.172 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | EKPC_P1-2_THEL-AEPTHEL69_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD9 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 1.0115 | 0.7501 | 26.139 | 0.08 | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD10 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 1.0115 | 0.7501 | 26.139 | 0.08 | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD11 | Winter 2030 | 243721 | 05FALCON | 69 | 205 | 1.0115 | 0.7507 | 26.076 | 0.08 | BUS | EKPC_P2-2_FALCON 69_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD12 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 0.9989 | 0.7951 | 20.38 | 0.08 | N-1-1 | AEP_P1-2_#12131_440_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD13 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 0.991 | 0.8942 | 9.685 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | AEP_P1-2_#12138_206_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD14 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 0.991 | 0.8942 | 9.68 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | AEP_P1-3_#11485_05THELMA 138_3_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD15 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 0.991 | 0.8966 | 9.441 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | AEP_P1-2_#7389_17037_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD16 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 1.0035 | 0.8005 | 20.301 | 0.08 | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD17 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 1.0035 | 0.8005 | 20.301 | 0.08 | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD18 | Winter 2030 | 243755 | 05FALCON | 46 | 205 | 1.0035 | 0.8011 | 20.238 | 0.08 | BUS | EKPC_P2-2_FALCON 69_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD19 | Winter 2030 | 243758 | 05MIDDLECR | 46 | 205 | 0.9902 | 0.8773 | 11.288 | 0.08 | N-1-1 | AEP_P1-2_#12131_440_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD20 | Winter 2030 | 243758 | 05MIDDLECR | 46 | 205 | 1.0005 | 0.899 | 10.156 | 0.08 | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD21 | Winter 2030 | 243758 | 05MIDDLECR | 46 | 205 | 1.0005 | 0.899 | 10.156 | 0.08 | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD22 | Winter 2030 | 243758 | 05MIDDLECR | 46 | 205 | 1.0005 | 0.8995 | 10.103 | 0.08 | BUS | EKPC_P2-2_FALCON 69_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD23 | Winter 2030 | 243978 | 05STERLING2 | 34.5 | 205 | 1.0164 | 0.9352 | 8.12 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD24 | Winter 2030 | 243978 | 05STERLING2 | 34.5 | 205 | 1.0166 | 0.9352 | 8.141 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD25 | Winter 2030 | 244059 | 05LONE STA | 69 | 205 | 1.0075 | 0.9042 | 10.329 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD26 | Winter 2030 | 244063 | 05MEADOW C | 34.5 | 205 | 0.9727 | 0.8568 | 11.593 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD27 | Winter 2030 | 244069 | 05NEW CAST | 34.5 | 205 | 0.9747 | 0.859 | 11.569 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD28 | Winter 2030 | 244077 | 05STONECGA | 34.5 | 205 | 0.9834 | 0.8723 | 11.109 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD29 | Winter 2030 | 244078 | 05TRINITY | 69 | 205 | 1.0075 | 0.922 | 8.549 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD30 | Winter 2030 | 244088 | 05WHEATLAN | 69 | 205 | 1.0028 | 0.9169 | 8.592 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD31 | Winter 2030 | 244092 | 05MT.UNION | 69 | 205 | 1.0114 | 0.9086 | 10.284 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD32 | Winter 2030 | 244093 | 05MT.UNION | 34.5 | 205 | 0.995 | 0.8871 | 10.789 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD33 | Winter 2030 | 244315 | 05TOWNOF R | 69 | 205 | 1.027 | 0.9395 | 8.745 | 0.08 | BRANCH | 244305 05RICHLNDS 69.0 247486 05RICHLANDSS 69.0 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD34 | Winter 2030 | 244315 | 05TOWNOF R | 69 | 205 | 1.027 | 0.9398 | 8.723 | 0.08 | LINEFB | AEP_P4_#13247_05RICHLNDS 69.0_A_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD35 | Winter 2030 | 244315 | 05TOWNOF R | 69 | 205 | 1.027 | 0.9398 | 8.719 | 0.08 | BUS | AEP_P2-2_#13245_05RICHLNDS 69.0_1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD36 | Winter 2030 | 244315 | 05TOWNOF R | 69 | 205 | 1.027 | 0.9398 | 8.719 | 0.08 | LINEFB | AEP_P4_#13245_05RICHLNDS 69.0_C_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD37 | Winter 2030 | 244426 | 05MARSHFRK | 46 | 205 | 0.9945 | 0.8961 | 9.84 | 0.08 | N-1-1 | AEP_P1-3_#16301_05BAILS1 138_1_SRT-A | AEP_P1-2_#14354_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD38 | Winter 2030 | 244606 | 05JOHNSCR | 69 | 205 | 1.0205 | 0.9164 | 10.412 | 0.08 | N-1-1 | AEP_P1-2_#17389_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD39 | Winter 2030 | 244606 | 05JOHNSCR | 69 | 205 | 1.0215 | 0.9194 | 10.208 | 0.08 | N-1-1 | AEP_P1-3_#11469_05HATFLD 138_1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD40 | Winter 2030 | 244627 | 05SCOTTBR | 69 | 205 | 1.0068 | 0.9011 | 10.573 | 0.08 | N-1-1 | AEP_P1-2_#17389_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD41 | Winter 2030 | 244627 | 05SCOTTBR | 69 | 205 | 1.0078 | 0.9042 | 10.366 | 0.08 | N-1-1 | AEP_P1-3_#11469_05HATFLD 138_1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD42 | Winter 2030 | 245594 | 05SHAWNEE | 69 | 205 | 1.0103 | 0.8614 | 14.888 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD43 | Winter 2030 | 245594 | 05SHAWNEE | 69 | 205 | 1.0116 | 0.8614 | 15.021 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD44 | Winter 2030 | 245816 | 05FT.SHAW SS | 34.5 | 205 | 1.0114 | 0.9298 | 8.159 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD45 | Winter 2030 | 245816 | 05FT.SHAW SS | 34.5 | 205 | 1.0116 | 0.9298 | 8.182 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD46 | Winter 2030 | 245840 | 05S SIDE | 34.5 | 205 | 1.0102 | 0.9296 | 8.059 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD47 | Winter 2030 | 245840 | 05S SIDE | 34.5 | 205 | 1.0104 | 0.9296 | 8.079 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD48 | Winter 2030 | 245842 | 05SHAWNE R | 34.5 | 205 | 1.0102 | 0.9286 | 8.158 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD49 | Winter 2030 | 245842 | 05SHAWNE R | 34.5 | 205 | 1.0104 | 0.9286 | 8.183 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD50 | Winter 2030 | 245843 | 05SHAWNE R | 69 | 205 | 1.0215 | 0.9384 | 8.304 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD51 | Winter 2030 | 245843 | 05SHAWNE R | 69 | 205 | 1.0216 | 0.9384 | 8.324 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD52 | Winter 2030 | 245844 | 05SHAWNER2EQ | 1 | 205 | 1.0214 | 0.9386 | 8.278 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD53 | Winter 2030 | 245844 | 05SHAWNER2EQ | 1 | 205 | 1.0215 | 0.9386 | 8.293 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD54 | Winter 2030 | 245849 | 05STERLING1 | 34.5 | 205 | 1.0164 | 0.9352 | 8.12 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD55 | Winter 2030 | 245849 | 05STERLING1 | 34.5 | 205 | 1.0166 | 0.9352 | 8.141 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD56 | Winter 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9815 | 0.9005 | 8.096 | 0.08 | N-1-1 | AEP_P1-4_05GENOA 1 69.0_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD57 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 1.0009 | 0.7442 | 25.675 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD58 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 1.0023 | 0.7824 | 21.985 | 0.08 | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD59 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 0.998 | 0.7434 | 25.465 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD60 | Winter 2030 | 246687 | 05TRABUE | 69 | 205 | 0.998 | 0.7826 | 21.538 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD61 | Winter 2030 | 247037 | 05META SS | 69 | 205 | 1.0161 | 0.9115 | 10.464 | 0.08 | N-1-1 | AEP_P1-2_#17389_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD62 | Winter 2030 | 247037 | 05META SS | 69 | 205 | 1.0171 | 0.9145 | 10.259 | 0.08 | N-1-1 | AEP_P1-3_#11469_05HATFLD 138_1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD63 | Winter 2030 | 247486 | 05RICHLANDSS | 69 | 205 | 1.027 | 0.9396 | 8.745 | 0.08 | BRANCH | 244305 05RICHLNDS 69.0 247486 05RICHLANDSS 69.0 1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD64 | Winter 2030 | 247486 | 05RICHLANDSS | 69 | 205 | 1.027 | 0.9398 | 8.723 | 0.08 | LINEFB | AEP_P4_#13247_05RICHLNDS 69.0_A_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD65 | Winter 2030 | 247486 | 05RICHLANDSS | 69 | 205 | 1.027 | 0.9398 | 8.719 | 0.08 | BUS | AEP_P2-2_#13245_05RICHLNDS 69.0_1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD66 | Winter 2030 | 247486 | 05RICHLANDSS | 69 | 205 | 1.027 | 0.9398 | 8.719 | 0.08 | LINEFB | AEP_P4_#13245_05RICHLNDS 69.0_C_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD67 | Winter 2030 | 247769 | 05SHAWNE RSS | 34.5 | 205 | 1.0102 | 0.9286 | 8.158 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD68 | Winter 2030 | 247769 | 05SHAWNE RSS | 34.5 | 205 | 1.0104 | 0.9286 | 8.183 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD69 | Winter 2030 | 290034 | 05MARA_LIMA | 34.5 | 205 | 1.0134 | 0.932 | 8.144 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD70 | Winter 2030 | 290034 | 05MARA_LIMA | 34.5 | 205 | 1.0136 | 0.932 | 8.166 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD71 | Winter 2030 | 290064 | 05LIMA PMPSS | 34.5 | 205 | 1.0132 | 0.9322 | 8.1 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD72 | Winter 2030 | 290064 | 05LIMA PMPSS | 34.5 | 205 | 1.0134 | 0.9322 | 8.12 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD73 | Winter 2030 | 290065 | 05AIRFOIL SS | 34.5 | 205 | 1.0128 | 0.9317 | 8.104 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD74 | Winter 2030 | 290065 | 05AIRFOIL SS | 34.5 | 205 | 1.0129 | 0.9317 | 8.125 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD75 | Winter 2030 | 290066 | 05MAR_LIMA P | 34.5 | 205 | 1.0127 | 0.9316 | 8.105 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD76 | Winter 2030 | 290066 | 05MAR_LIMA P | 34.5 | 205 | 1.0129 | 0.9316 | 8.125 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD77 | Winter 2030 | 290297 | 05AIRFOIL | 34.5 | 205 | 1.0127 | 0.9316 | 8.104 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD78 | Winter 2030 | 290297 | 05AIRFOIL | 34.5 | 205 | 1.0129 | 0.9316 | 8.125 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD79 | Winter 2030 | 290894 | 05W.LIMA | 34.5 | 205 | 0.9811 | 0.8986 | 8.25 | 0.08 | N-1-1 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD80 | Winter 2030 | 290894 | 05W.LIMA | 34.5 | 205 | 0.9813 | 0.8985 | 8.28 | 0.08 | N-1-1 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD81 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9945 | 0.8391 | 15.534 | 0.08 | N-1-1 | AEP_P1-4_05ALLEN 46.0_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD82 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 1.0023 | 0.8569 | 14.537 | 0.08 | N-1-1 | AEP_P1-2_#7389_17037_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD83 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 1.0003 | 0.8623 | 13.799 | 0.08 | N-1-1 | AEP_P1-2_#12131_440_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD84 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9947 | 0.8584 | 13.634 | 0.08 | N-1-1 | AEP_P1-4_05MORGFK 138_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD85 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9982 | 0.8619 | 13.63 | 0.08 | N-1-1 | AEP_P1-4_05INEZ 138_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD86 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9947 | 0.8589 | 13.582 | 0.08 | N-1-1 | AEP_P1-2_#11119_26119_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD87 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9988 | 0.8652 | 13.365 | 0.08 | N-1-1 | AEP_P1-2_#12052_360_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD88 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9969 | 0.8644 | 13.254 | 0.08 | N-1-1 | AEP_P1-2_#7813_2900151_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD89 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9987 | 0.8668 | 13.198 | 0.08 | N-1-1 | AEP_P1-2_#15566_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD90 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9958 | 0.8644 | 13.132 | 0.08 | N-1-1 | AEP_P1-3_#11500_05INEZ 138_1_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD91 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9974 | 0.8664 | 13.096 | 0.08 | N-1-1 | AEP_P1-2_#5976_4643_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD92 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9967 | 0.866 | 13.063 | 0.08 | N-1-1 | AEP_P1-2_#11444_339_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD93 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9966 | 0.866 | 13.063 | 0.08 | N-1-1 | AEP_P1-3_#16538_05DEWEY 138_1_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD94 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9983 | 0.8682 | 13.013 | 0.08 | N-1-1 | AEP_P1-2_#6173_98_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD95 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9984 | 0.8686 | 12.975 | 0.08 | N-1-1 | AEP_P1-3_#17628_05CEDARC 138_1_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD96 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.998 | 0.8685 | 12.954 | 0.08 | N-1-1 | 957241 AF2-018 C 138_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD97 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9984 | 0.8689 | 12.95 | 0.08 | N-1-1 | AEP_P1-2_#14774_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD98 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9978 | 0.8689 | 12.895 | 0.08 | N-1-1 | AEP_P1-2_#16633_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD99 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9978 | 0.8689 | 12.895 | 0.08 | N-1-1 | AEP_P1-3_#327_05BAKER 345_2_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD100 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.9918 | 0.869 | 12.283 | 0.08 | N-1-1 | EKPC_P1-2_GODD - ROW138_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD101 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.987 | 0.868 | 11.9 | 0.08 | N-1-1 | EKPC_P1-2_ROW-SKAG138_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD102 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.99928 | 0.87103 | 12.825 | 0.08 | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD103 | Summer 2030 | 243721 | 05FALCON | 69 | 205 | 0.99928 | 0.87103 | 12.825 | 0.08 | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD104 | Summer 2030 | 243755 | 05FALCON | 46 | 205 | 0.99648 | 0.89566 | 10.082 | 0.08 | SINGLE | EKPC_P1-2_FALCON 69 TIE_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD105 | Summer 2030 | 243755 | 05FALCON | 46 | 205 | 0.99648 | 0.89566 | 10.082 | 0.08 | BRANCH | 243721 05FALCON 69.0 341461 2FALCON EK 69.0 Z1_SRT-A | N/A | No | FERC 715 Part 4 Voltage N-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD106 | Summer 2030 | 244063 | 05MEADOW C | 34.5 | 205 | 0.9731 | 0.89 | 8.312 | 0.08 | N-1-1 | AEP_P1-3_#14672_05CLOVRD 138_18_SRT-A | AEP_P1-2_#14669_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD107 | Summer 2030 | 246588 | 05HILLIARD1 | 69 | 205 | 1.011 | 0.6989 | 31.202 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD108 | Summer 2030 | 246588 | 05HILLIARD1 | 69 | 205 | 1.0034 | 0.6993 | 30.411 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD109 | Summer 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9754 | 0.8893 | 8.609 | 0.08 | N-1-1 | AEP_P1-2_#5800_676_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD110 | Summer 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.978 | 0.8944 | 8.365 | 0.08 | N-1-1 | AEP_P1-2_#9655_14218_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD111 | Summer 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9798 | 0.8996 | 8.026 | 0.08 | N-1-1 | AEP_P1-4_05GENOA 138_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD112 | Summer 2030 | 246643 | 05WESTRV2B | 69 | 205 | 0.9835 | 0.8966 | 8.691 | 0.08 | N-1-1 | AEP_P1-4_05GENOA 1 69.0_SRT-A | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD113 | Summer 2030 | 246687 | 05TRABUE | 69 | 205 | 0.9993 | 0.6957 | 30.355 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD114 | Summer 2030 | 246687 | 05TRABUE | 69 | 205 | 1.0009 | 0.7347 | 26.624 | 0.08 | N-1-1 | AEP_P1-2_#10138_26757_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD115 | Summer 2030 | 246687 | 05TRABUE | 69 | 205 | 0.992 | 0.696 | 29.592 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD116 | Summer 2030 | 246687 | 05TRABUE | 69 | 205 | 0.992 | 0.7347 | 25.724 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#10138_26757_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD117 | Summer 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9844 | 0.7847 | 19.971 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD118 | Summer 2030 | 247093 | 05BLAIR | 69 | 205 | 0.9806 | 0.7848 | 19.574 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD119 | Summer 2030 | 247841 | 05NAUTILUS1 | 69 | 205 | 0.9855 | 0.7756 | 20.984 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD120 | Summer 2030 | 247841 | 05NAUTILUS1 | 69 | 205 | 0.9814 | 0.7758 | 20.557 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD121 | Summer 2030 | 247854 | 05JEFFRS IND | 69 | 205 | 0.9771 | 0.7807 | 19.644 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD122 | Summer 2030 | 247854 | 05JEFFRS IND | 69 | 205 | 0.9809 | 0.7805 | 20.042 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD123 | Summer 2030 | 290174 | 05HILLIARD2 | 69 | 205 | 1.0109 | 0.6989 | 31.201 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD124 | Summer 2030 | 290174 | 05HILLIARD2 | 69 | 205 | 1.0033 | 0.6992 | 30.41 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD125 | Summer 2030 | 290344 | 05NAUTILUS2 | 69 | 205 | 0.9855 | 0.7755 | 20.995 | 0.08 | N-1-1 | AEP_P1-2_#5838_11337_SRT-A | AEP_P1-2_#15081_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD126 | Summer 2030 | 290344 | 05NAUTILUS2 | 69 | 205 | 0.9814 | 0.7757 | 20.568 | 0.08 | N-1-1 | AEP_P1-2_#15081_SRT-A | AEP_P1-2_#5838_11337_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD127 | LL 2030 | 243721 | 05FALCON | 69 | 205 | 1.015 | 0.9315 | 8.351 | 0.08 | N-1-1 | 243759 05PRESTNSB 46.0 244608 05KENWOOD 46.0 1_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD128 | LL 2030 | 243721 | 05FALCON | 69 | 205 | 1.0154 | 0.9318 | 8.363 | 0.08 | N-1-1 | AEP_P1-2_#12131_440_SRT-A | EKPC_P1-2_FALCON 69 TIE_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD129 | LL 2030 | 244131 | 05N.CLAYTOR | 69 | 205 | 1.002 | 0.8878 | 11.426 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD130 | LL 2030 | 244133 | 05INGLES | 69 | 205 | 1.0015 | 0.8786 | 12.287 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD131 | LL 2030 | 244134 | 05KLOPMAN | 34.5 | 205 | 1.0074 | 0.9239 | 8.348 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD132 | LL 2030 | 244138 | 05N.CLAYTO | 34.5 | 205 | 1.0105 | 0.9273 | 8.328 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD133 | LL 2030 | 244140 | 05HICKMAN | 69 | 205 | 1.0038 | 0.8693 | 13.455 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD134 | LL 2030 | 244141 | 05PULASFUR | 34.5 | 205 | 1.0073 | 0.9238 | 8.349 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD135 | LL 2030 | 244144 | 05PULASK3T | 34.5 | 205 | 1.0073 | 0.9238 | 8.349 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD136 | LL 2030 | 244146 | 05RADFRD A | 69 | 205 | 0.9999 | 0.8648 | 13.508 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD137 | LL 2030 | 244148 | 05RIVERBEN | 69 | 205 | 1.002 | 0.8758 | 12.621 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD138 | LL 2030 | 244150 | 05SMITH LA | 34.5 | 205 | 1.0085 | 0.9251 | 8.341 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD139 | LL 2030 | 244156 | 05INGLSTSS | 34.5 | 205 | 1.0433 | 0.9126 | 13.064 | 0.08 | N-1-1 | 247868 05N.CLAYTOR 138 247870 05CLAYTR HY2 138 1_SRT-A | AEP_P1-2_#11342_14740_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD140 | LL 2030 | 244480 | 05CHAUNCEY | 46 | 205 | 1.041 | 0.9311 | 10.99 | 0.08 | N-1-1 | 242761 05RAGLDZ 138 288897 05SPRIGG 138 1_SRT-A | AEP_P1-2_#17185_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD141 | LL 2030 | 244522 | 05WVA COAL | 46 | 205 | 1.041 | 0.9311 | 10.99 | 0.08 | N-1-1 | 242761 05RAGLDZ 138 288897 05SPRIGG 138 1_SRT-A | AEP_P1-2_#17185_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD142 | LL 2030 | 244604 | 05GUNDMINE Z | 69 | 205 | 0.9773 | 0.7709 | 20.643 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD143 | LL 2030 | 244606 | 05JOHNSCR | 69 | 205 | 1.0239 | 0.8265 | 19.743 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD144 | LL 2030 | 244606 | 05JOHNSCR | 69 | 205 | 1.0278 | 0.9024 | 12.547 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD145 | LL 2030 | 244610 | 05KIMPER | 69 | 205 | 1.025 | 0.8618 | 16.316 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD146 | LL 2030 | 244610 | 05KIMPER | 69 | 205 | 1.0282 | 0.925 | 10.318 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD147 | LL 2030 | 244613 | 05MCCOYELK | 69 | 205 | 1.026 | 0.9136 | 11.235 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD148 | LL 2030 | 244617 | 05MCOYELTP | 69 | 205 | 1.026 | 0.9136 | 11.234 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD149 | LL 2030 | 244627 | 05SCOTTBR | 69 | 205 | 1.0137 | 0.8137 | 20.002 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD150 | LL 2030 | 244627 | 05SCOTTBR | 69 | 205 | 1.0177 | 0.8908 | 12.687 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD151 | LL 2030 | 244628 | 05SECONDFK | 69 | 205 | 1.0267 | 0.9405 | 8.62 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD152 | LL 2030 | 244634 | 05SIDNEY | 69 | 205 | 0.9911 | 0.787 | 20.409 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD153 | LL 2030 | 244634 | 05SIDNEY | 69 | 205 | 1.0093 | 0.8813 | 12.796 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD154 | LL 2030 | 244636 | 05BIGCREEKSS | 69 | 205 | 0.9935 | 0.7899 | 20.364 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD155 | LL 2030 | 244636 | 05BIGCREEKSS | 69 | 205 | 1.0106 | 0.8828 | 12.779 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD156 | LL 2030 | 244638 | 05FISHTP L | 69 | 205 | 1.0262 | 0.9274 | 9.883 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD157 | LL 2030 | 244642 | 05BEVINS SS | 69 | 205 | 0.9783 | 0.7721 | 20.626 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD158 | LL 2030 | 244642 | 05BEVINS SS | 69 | 205 | 1.0026 | 0.8738 | 12.878 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD159 | LL 2030 | 244827 | 05KELLYCRKSS | 46 | 205 | 1.0159 | 0.9143 | 10.161 | 0.08 | N-1-1 | 244827 05KELLYCRKSS 46.0 244848 05CABNCRK1 46.0 1_SRT-A | AEP_P1-3_#14961_05JARRETT 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD160 | LL 2030 | 244835 | 05MAMMOTHSS | 46 | 205 | 1.0194 | 0.9178 | 10.161 | 0.08 | N-1-1 | 244827 05KELLYCRKSS 46.0 244848 05CABNCRK1 46.0 1_SRT-A | AEP_P1-3_#14961_05JARRETT 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD161 | LL 2030 | 247037 | 05META SS | 69 | 205 | 1.0206 | 0.8224 | 19.826 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD162 | LL 2030 | 247037 | 05META SS | 69 | 205 | 1.0246 | 0.8986 | 12.592 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD163 | LL 2030 | 247427 | 05FISHTRAPSS | 69 | 205 | 1.0263 | 0.9275 | 9.882 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD164 | LL 2030 | 288673 | 05KELLYCREEK | 46 | 205 | 1.0159 | 0.9143 | 10.161 | 0.08 | N-1-1 | 244827 05KELLYCRKSS 46.0 244848 05CABNCRK1 46.0 1_SRT-A | AEP_P1-3_#14961_05JARRETT 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD165 | LL 2030 | 288748 | 05MAMMOTH | 46 | 205 | 1.0194 | 0.9178 | 10.161 | 0.08 | N-1-1 | 244827 05KELLYCRKSS 46.0 244848 05CABNCRK1 46.0 1_SRT-A | AEP_P1-3_#14961_05JARRETT 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD166 | LL 2030 | 289213 | 05LESLIE1TAP | 69 | 205 | 0.9936 | 0.79 | 20.362 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD167 | LL 2030 | 289213 | 05LESLIE1TAP | 69 | 205 | 1.0106 | 0.8829 | 12.778 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD168 | LL 2030 | 289214 | 05LESLIE NO1 | 69 | 205 | 0.9936 | 0.79 | 20.362 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD169 | LL 2030 | 289214 | 05LESLIE NO1 | 69 | 205 | 1.0106 | 0.8829 | 12.778 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD170 | LL 2030 | 290991 | 05SIDNEYCOAL | 69 | 205 | 0.9775 | 0.7711 | 20.64 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD171 | LL 2030 | 290991 | 05SIDNEYCOAL | 69 | 205 | 1.0018 | 0.8729 | 12.887 | 0.08 | N-1-1 | 244604 05GUNDMINE Z 69.0 244642 05BEVINS SS 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-VD172 | LL 2030 | 290992 | 05GUNDMINE | 69 | 205 | 0.9773 | 0.7709 | 20.643 | 0.08 | N-1-1 | 244582 05HATFLD 69.0 244604 05GUNDMINE Z 69.0 1_SRT-A | AEP_P1-3_#13697_05JOHNSC 138_1_SRT-A | No | FERC 715 Part 4 Voltage N-1-1 | Reliability Violations on Transmission Facilities Below 200 kV exclusion

## FERC Form 715 Short Circuit
Reserved(FG# assigned by PJM) | Analysis case | Bus # | Bus Name | Bus KV | Area | Breaker | Rating Type | DUTY_P | DUTY_A | BKR_CAPA (A) | Pre-fault Voltage (KV) | PJM Accepting Proposals | 715 criteria description | Justification for applicable exclusion from receiving competitive proposals | Comment
2025-W1-AEP-SC1 | 2027 & 2030 case | 243730 | 05HAZARD 2 | 69 | 205 | R | S | 114.1 | 12893.8 | 11300 | 1.05 pu | No | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-SC2 | 2027 & 2030 case | 246902 | 05THOMASRD | 69 | 205 | CS-TX1 | S | 119.4 | 29841 | 25000 | 1.05 pu | No | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-AEP-SC3 | 2030 case | 245444 | 05CAMBRIDG | 34.5 | 205 | F | S | 100.2 | 8420.4 | 8400 | 1.05 pu | No | 715 Part 4 Short Circuit | Reliability Violations on Transmission Facilities Below 200 kV exclusion