## Light Load GenDeliv
2032 RTEP PJM Generator Deliverability Result (Light Load)
FG # Status | PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals
Active | Require solution | 2025W1-32GD-LL1 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 4192.7 | 4192.7 | 151.97 | 151.97 | DVP_P1-2: LN 563_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL2 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4734.3 | 5263.2 | 128.68 | 143.05 | DVP_P1-2: LN 557_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL3 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4759.3 | 5262.6 | 129.36 | 143.04 | DVP_P1-2: LN 567_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL4 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3933.2 | 3933.2 | 142.56 | 142.56 | DVP_P1-2: LN 576_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL5 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4600.1 | 5175 | 125.03 | 140.66 | DVP_P1-2: LN 557_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution | 2025W1-32GD-LL6 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4726.2 | 5127.3 | 128.46 | 139.36 | DVP_P1-2: LN 574_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-LL7 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1119.8 | 1164.8 | 132.84 | 138.18 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-LL8 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1112.7 | 1151.6 | 132 | 136.61 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Require solution | 2025W1-32GD-LL9 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4462.5 | 4970.5 | 121.29 | 135.1 | DVP_P1-2: LN 567_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1200.4 | 1584.5 | 1610.2 | 132 | 134.14 | DVP_P1-2: LN 576_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL10 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3493 | 3672.3 | 126.61 | 133.11 | DVP_P1-2: LN 582_2_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL11 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4506.1 | 4825.8 | 122.48 | 131.17 | DVP_P1-2: LN 574_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1100.7 | 1433.1 | 1412 | 130.2 | 128.28 | DVP_P1-2: LN 567_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL12 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3341.7 | 3530 | 121.12 | 127.95 | DVP_P1-2: LN 2154_2_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL13 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3337.5 | 3526.7 | 120.97 | 127.83 | DVP_P1-2: LN 2113_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL14 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 4278.8 | 4278.8 | 124.89 | 124.89 | DVP_P4-2: H6T563_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL15 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 4267.7 | 4267.7 | 124.57 | 124.57 | DVP_P4-2: 56372_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL16 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 5126.2 | 5659.4 | 110.76 | 122.29 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 1100.7 | 1341.4 | 1346 | 121.87 | 122.28 | DVP_P1-2: LN 557_SRT-A | Single |  | No
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-LL17 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1005 | 1027.1 | 119.21 | 121.84 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-LL18 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 999.2 | 1015.5 | 118.53 | 120.46 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Require solution | 2025W1-32GD-LL19 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4200.2 | 4424.8 | 114.16 | 120.27 | DVP_P1-2: LN 298_2_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL20 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2771 | 3149.2 | 3319.6 | 113.65 | 119.8 | DVP_P2-2: SURRY B1_SRT-WL | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL21 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4188.1 | 4404.3 | 113.83 | 119.71 | DVP_P1-2: LN 298_3_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL22 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4037.7 | 4312.6 | 109.75 | 117.22 | DVP_P1-2: LN 2028_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution | 2025W1-32GD-LL23 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4009.6 | 4292.5 | 108.98 | 116.67 | AEP_P1-3_#1377_05J.FERR 765_1_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution | 2025W1-32GD-LL24 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4599.4 | 5343.4 | 5343.4 | 116.18 | 116.18 | DVP_P1-2: LN 576_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1200.4 | 1382.2 | 1382.2 | 115.15 | 115.15 | DVP_P1-2: LN 563_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL25 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3933.4 | 3933.4 | 114.81 | 114.81 | DVP_P4-2: 57602_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL26 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3933.4 | 3933.4 | 114.81 | 114.81 | DVP_P4-2: WT576_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL27 | 314923 | 8SEPTA | 314924 | 8SURRY | 1 | 500 | 345 | 2758.9 | 3126.7 | 3160.4 | 113.33 | 114.55 | DVP_P1-2: LN 531_SRT-L | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL28 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2909 | 3149.2 | 3319.6 | 108.26 | 114.11 | Base Case | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 2 | 230/500 | 345 | 1031.2 | 1130.4 | 1174.9 | 109.62 | 113.94 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 1 | 230/500 | 345 | 1038.7 | 1136 | 1180.7 | 109.37 | 113.68 | DVP_P1-2: LN 557_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL29 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3656.8 | 3880.5 | 106.74 | 113.27 | DVP_P4-2: 2113T2154_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL30 | 314923 | 8SEPTA | 314924 | 8SURRY | 1 | 500 | 345 | 2758.9 | 3034.8 | 3102.4 | 110 | 112.45 | DVP_P1-2: LN 563_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL31 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4742.2 | 5149.6 | 102.47 | 111.27 | DVP_P4-2: H2T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314902 | 8CARSON | 314282 | 6CARSON | 2 | 500/230 | 345 | 1204 | 1326.4 | 1339.1 | 110.16 | 111.22 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
Active | Require solution | 2025W1-32GD-LL32 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4730.3 | 5141.4 | 102.21 | 111.09 | DVP_P4-2: H1T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
N/A | Not soliciting proposals - transformer | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1344 | 1484.8 | 1492.9 | 110.47 | 111.08 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1344 | 1484.8 | 1492.9 | 110.47 | 111.08 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
Active | Require solution | 2025W1-32GD-LL33 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4599.4 | 4764.6 | 5061.5 | 103.59 | 110.05 | DVP_P1-2: LN 534_SRT-L | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL34 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1053.7 | 1137.6 | 101.9 | 110.02 | PL_48_P42_100926_SRT-A | Breaker | Same as base case | Yes
Active | Require solution | 2025W1-32GD-LL35 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 5080.3 | 5080.3 | 109.77 | 109.77 | DVP_P4-2: 557T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL36 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1044.6 | 1127.5 | 101.02 | 109.05 | PL_48_P42_000438_SRT-A | Breaker | Same as base case | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL37 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1044.6 | 1127.5 | 101.02 | 109.05 | PL_48_P71_102649_SRT-A | Tower | Same as base case | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL38 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1043.9 | 1125.1 | 100.96 | 108.81 | PL_48_P12_000189_SRT-A | Single | Same as base case | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL39 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1043.9 | 1125.1 | 100.96 | 108.81 | PL_48_P11_000840_SRT-A | Single | Same as base case | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL40 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1052.3 | 1124 | 101.77 | 108.7 | 208918 SUSQ 1 24.0_SRT-A | Single | Same as base case | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL41 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1052.3 | 1124 | 101.77 | 108.7 | 208918 SUSQ 1 24.0_SRT-A | Single | Same as base case | Yes
Active | Require solution | 2025W1-32GD-LL42 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4759.3 | 5262.6 | 98.03 | 108.4 | DVP_P4-2: 56702_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL43 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1038.3 | 1116.6 | 100.42 | 107.99 | PL_40_P11_001448_SRT-A | Single | Same as base case | Yes
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 2017.7 | 2158.7 | 100.89 | 107.94 | DVP_P4-2: H6T563_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1989.5 | 2155.5 | 99.48 | 107.78 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1287 | 1405.8 | 1386.3 | 109.23 | 107.71 | DVP_P4-2: 56702_SRT-A | Breaker |  | No
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL44 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1033.1 | 1112.5 | 99.91 | 107.59 | PL_48_P41_102622_SRT-A | Breaker | Same as base case | Yes
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 2018.5 | 2148.5 | 100.92 | 107.43 | DVP_P4-2: H6T563_SRT-A | Breaker |  | No
Active | Require solution | 2025W1-32GD-LL45 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4462.5 | 4970.5 | 96.42 | 107.4 | DVP_P4-2: 56702_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1990.3 | 2145 | 99.51 | 107.25 | DVP_P1-2: LN 557_SRT-A | Single |  | No
Active | Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-LL46 | 208013 | SUMT2_B4 | 208090 | SUMT | 2 | 230 | 229 | 801 | 866.9 | 857.7 | 108.23 | 107.08 | PL_02_P42_001053_SRT-A | Breaker |  | Yes
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1976.1 | 2134.3 | 98.8 | 106.72 | DVP_P1-2: LN 567_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1976.8 | 2123.8 | 98.84 | 106.19 | DVP_P1-2: LN 567_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 2116.6 | 2116.6 | 105.83 | 105.83 | DVP_P1-2: LN 563_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 2115.9 | 2115.9 | 105.79 | 105.79 | DVP_P1-2: LN 563_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL47 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3879 | 3913.6 | 4095.9 | 100.89 | 105.59 | Base Case | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1991.2 | 2109.4 | 99.56 | 105.47 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1991.9 | 2100.7 | 99.6 | 105.04 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
Active | Require solution | 2025W1-32GD-LL48 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4696.7 | 5090.4 | 96.74 | 104.85 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL49 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3359.7 | 3577.6 | 98.06 | 104.42 | DVP_P7-1: LN 211-228_SRT-L | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL50 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4599.4 | 4802.4 | 4802.4 | 104.41 | 104.41 | DVP_P1-2: LN 563_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 2079 | 2079 | 103.95 | 103.95 | DVP_P1-2: LN 576_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 2078.3 | 2078.3 | 103.91 | 103.91 | DVP_P1-2: LN 576_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL51 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3354.2 | 3552.3 | 97.9 | 103.69 | DVP_P7-1: LN 2024-2102_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL52 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3347.2 | 3549.9 | 97.7 | 103.62 | DVP_P7-1: LN 2197-2215_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL53 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3879 | 3799.9 | 4015.4 | 97.96 | 103.52 | Base Case | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution | 2025W1-32GD-LL54 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3302.6 | 3528.3 | 96.4 | 102.99 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL55 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3332.3 | 3527.7 | 97.27 | 102.97 | DVP_P7-1: LN 2197-240_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL56 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3337.3 | 3527.2 | 97.41 | 102.95 | DVP_P7-1: LN 177-2113_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL57 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3292.5 | 3522 | 96.1 | 102.8 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL58 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4976.3 | 4976.3 | 102.5 | 102.5 | DVP_P4-2: 557T574_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL59 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4967.1 | 4967.1 | 102.31 | 102.31 | DVP_P4-2: 56722_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL60 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4721.3 | 4721.3 | 102.02 | 102.02 | DVP_P4-2: 56722_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
N/A | Not soliciting proposals - transformer | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1406.3 | 1405.9 | 101.98 | 101.95 | 765-L11216__-S_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1287 | 1319.9 | 1308.8 | 102.56 | 101.69 | DVP_P4-2: G2T567_SRT-A | Breaker |  | No
Active | Require solution | 2025W1-32GD-LL61 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4573.2 | 4936.7 | 94.2 | 101.68 | DVP_P4-2: G2T567_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1933.2 | 2030.6 | 96.66 | 101.53 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1933.2 | 2030.6 | 96.66 | 101.53 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1934 | 2023.7 | 96.7 | 101.19 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1934 | 2023.7 | 96.7 | 101.19 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1991.4 | 2023.4 | 99.57 | 101.17 | AEP_P1-2_#1375_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1394.3 | 1393.6 | 101.11 | 101.06 | COMED_P4_023-65-BT3-4___SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1393.8 | 1393.4 | 101.07 | 101.05 | COMED_P4_023-65-BT4-5___SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1254.9 | 1263.8 | 1268.1 | 100.71 | 101.05 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | Not soliciting proposals - terminal equipment limited | N/A | 243206 | 05DUMONT | 290606 | 05DUMONT_RS | Z1 | 765 | 205 | 5001 | 4898.4 | 5048.7 | 97.95 | 100.95 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1992.1 | 2015 | 99.61 | 100.75 | AEP_P1-2_#1375_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1246.4 | 1248.4 | 1252.7 | 100.15 | 100.5 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1386.4 | 1385.5 | 100.54 | 100.47 | 765-L11216__-S_SRT-A | Single |  | No
Active | Require solution | 2025W1-32GD-LL62 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4536.6 | 4865 | 93.44 | 100.21 | DVP_P4-2: H1T574_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
N/A | Not soliciting proposals - transformer | N/A | 255205 | 17REYNOLDS | 255204 | 17REYNOLDS | 3 | 345/765 | 217 | 2239 | 2225.6 | 2241.9 | 99.4 | 100.13 | AEP_P7-1_#11043___SRT-A | Tower |  | No
N/A | Not soliciting proposals - transformer | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 1 | 230/500 | 345 | 1212 | 1647.3 | 1735.9 | 135.91 | 143.23 | DVP_P4-2: H2T557_SRT-L | Breaker |  | No
Active | Require solution | 2025W1-32GD-LL63 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 3299 | 3829.3 | 4078.5 | 116.07 | 123.63 | DVP_P4-2: H1T553_SRT-L | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Active | Require solution | 2025W1-32GD-LL64 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3994.8 | 3994.8 | 116.6 | 116.6 | DVP_P4-2: 562T563_SRT-L | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL65 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2771 | 3009.8 | 3182.8 | 108.62 | 114.86 | DVP_P4-2: 53102_SRT-L | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL66 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3559 | 3866.1 | 4031.7 | 108.63 | 113.28 | DVP_P4-2: 56272_SRT-L | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL67 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4797.8 | 5410.9 | 98.82 | 111.45 | DVP_P4-2: H2T557_SRT-L | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL68 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4730.3 | 5141.3 | 102.21 | 111.09 | DVP_P4-2: H1T574_SRT-L | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution | 2025W1-32GD-LL69 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3559 | 3804.1 | 3941.1 | 106.89 | 110.74 | DVP_P4-2: 562T578_SRT-L | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL70 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3559 | 3786.4 | 3915.6 | 106.39 | 110.02 | DVP_P4-2: 562T579_SRT-L | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Active | Require solution | 2025W1-32GD-LL71 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2771 | 2848.1 | 3008.5 | 102.78 | 108.57 | DVP_P4-2: 57802_SRT-L | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL72 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3358.8 | 3546.7 | 98.04 | 103.52 | DVP_P4-2: 214672_SRT-L | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL73 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3359.2 | 3541.8 | 98.05 | 103.38 | DVP_P4-2: 215472_SRT-L | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Active | Require solution | 2025W1-32GD-LL74 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4739.5 | 4739.5 | 102.41 | 102.41 | DVP_P4-2: H2T557_SRT-L | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Active | Require solution | 2025W1-32GD-LL75 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 3559 | 3430.2 | 3594.2 | 96.38 | 100.99 | DVP_P4-2: H2T9517_SRT-L | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Active | Require solution | 2025W1-32GD-LL76 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4536.6 | 4865 | 93.44 | 100.21 | DVP_P4-2: H1T574_SRT-L | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes