## Summer GenDeliv
Caused by deactivation generators
2030 RTEP PJM Generator Deliverability Result (Summer)
FG # Status | FG Index | FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
Active | 123 | 2025W1-GD-S123 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 347.5 | 400 | 143.6 | 165.29 | ATSI_P2-4_OES-138-047_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 1 | 2025W1-GD-S1 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 662.7 | 961.7 | 965.8 | 145.12 | 145.74 | DVP_P1-2: LN 563_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 124 | 2025W1-GD-S124 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 375.3 | 406.5 | 133.1 | 144.16 | ATSI_P2-3_OES-138-060H_SRT-A | Breaker | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 125 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 829 | 1196.7 | 1193.5 | 144.35 | 143.97 | DVP_P4-2: H2T588_SRT-A | Breaker | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 126 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 829 | 1196.7 | 1193.4 | 144.35 | 143.96 | DVP_P4-2: H5T588_SRT-A | Breaker | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2 | 2025W1-GD-S2 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 662.7 | 927.9 | 937.1 | 140.02 | 141.41 | DVP_P1-2: LN 217_SRT-S | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 127 | 2025W1-GD-S127 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 811 | 1131.5 | 1134.2 | 139.52 | 139.86 | DVP_P4-2: 562T563_SRT-S | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 446 | 2025W1-GD-S446 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 227.4 | 267.1 | 118.44 | 139.1 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 160/192/180/228 | Yes
Active | 128 | 2025W1-GD-S128 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 228.2 | 262.6 | 118.84 | 136.77 | ATSI_P2-3_OES-138-0208BT_SRT-A | Breaker | 160/192/180/228 | Yes
Active | 384 | 2025W1-GD-S384 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 228.1 | 262.1 | 118.79 | 136.49 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 160/192/180/228 | Yes
Active | 129 | 2025W1-GD-S129 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 285.6 | 311.7 | 124.71 | 136.13 | ATSI_P2-3_OES-138-065_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 130 | 2025W1-GD-S130 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 285.6 | 311.7 | 124.71 | 136.13 | ATSI_P2-3_OES-138-065B_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 131 | 2025W1-GD-S131 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 283.4 | 325.6 | 117.1 | 134.56 | ATSI_P2-3_OES-138-060H_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 132 | 2025W1-GD-S132 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 811 | 1060.6 | 1064.9 | 130.77 | 131.3 | DVP_P4-2: 56372_SRT-A | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 133 | 2025W1-GD-S133 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 292.5 | 317.7 | 120.86 | 131.28 | ATSI_P2-3_OES-138-065G_SRT-A | Breaker | 200/242/226/286 | Yes
Active | 135 | 2025W1-GD-S135 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 811 | 1048.6 | 1057.7 | 129.3 | 130.42 | DVP_P4-2: H8T217_SRT-S | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 136 | 2025W1-GD-S136 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 811 | 1048.2 | 1057.3 | 129.25 | 130.37 | DVP_P4-2: 21712_SRT-S | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 137 | 2025W1-GD-S137 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 289.9 | 310.4 | 119.81 | 128.25 | ATSI_P2-3_OES-138-0607A_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 138 | 2025W1-GD-S138 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 289.9 | 310.3 | 119.79 | 128.23 | ATSI_P2-3_OES-138-0607C_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 139 | 2025W1-GD-S139 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 289.8 | 310.3 | 119.75 | 128.22 | ATSI_P2-3_OES-138-0607E_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 385 | 2025W1-GD-S385 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 290.1 | 310.2 | 119.88 | 128.2 | ATSI_P2-2_OES-138-054_SRT-A | Bus | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 3 | 2025W1-GD-S3 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 662.7 | 841.2 | 849.2 | 126.94 | 128.15 | DVP_P1-2: LN 228_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 4 | 2025W1-GD-S4 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 271.9 | 291.9 | 118.73 | 127.48 | ATSI_P1-2_OES-138-002D_SRT-A | Single | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 448 | 2025W1-GD-S448 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 265.4 | 287.9 | 115.91 | 125.7 | ATSI_P7-1_OES-138-066_SRT-A | Tower | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 141 | 2025W1-GD-S141 | 243469 | 05BEATTY | 241952 | 02DEERCREEK | 1 | 138 | 202/205 | 242 | 257.1 | 303.3 | 106.24 | 125.34 | ATSI_P2-4_OES-138-047_SRT-A | Breaker | ATSI: 200/242/226/286 AEP: conductor owned by FirstEnergy | Yes |  | Overlap FE EOL candidate
Active | 449 | 2025W1-GD-S449 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 249.9 | 249.5 | 124.93 | 124.77 | 34506 34542_SRT-A | Tower | 163/200/201/220 | Yes
Active | 142 | 2025W1-GD-S142 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 811 | 996.9 | 1008 | 122.92 | 124.29 | DVP_P4-2: 205T217_SRT-A | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 450 | 2025W1-GD-S450 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 319 | 347.4 | 113.13 | 123.2 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 145 | 2025W1-GD-S145 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 259 | 282 | 113.1 | 123.13 | ATSI_P2-3_OES-138-050_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 5 | 2025W1-GD-S5 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 278.4 | 297.6 | 115.06 | 122.96 | ATSI_P1-2_OES-138-002C_SRT-A | Single | 200/242/226/286 | Yes
Active | 146 | 2025W1-GD-S146 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 256.8 | 279.9 | 112.12 | 122.22 | ATSI_P2-3_OES-138-051_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 387 | 2025W1-GD-S387 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 256.8 | 279.9 | 112.12 | 122.22 | ATSI_P2-2_OES-138-003_SRT-A | Bus | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 147 | 2025W1-GD-S147 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 223.2 | 234.6 | 116.27 | 122.19 | ATSI_P2-3_OES-138-050_SRT-A | Breaker | 160/192/180/228 | Yes
Active | 148 | 2025W1-GD-S148 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 226.2 | 234.4 | 117.81 | 122.08 | ATSI_P2-3_OES-138-025_SRT-A | Breaker | 160/192/180/228 | Yes
Active | 451 | 2025W1-GD-S451 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 340.2 | 344.2 | 120.64 | 122.05 | 34506 34542_SRT-A | Tower | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 388 | 2025W1-GD-S388 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 319.4 | 343.8 | 113.25 | 121.93 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 149 | 2025W1-GD-S149 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 318.9 | 343.7 | 113.1 | 121.87 | ATSI_P2-3_OES-138-0208BT_SRT-A | Breaker | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 151 | 2025W1-GD-S151 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 222 | 233.6 | 115.61 | 121.65 | ATSI_P2-3_OES-138-051_SRT-A | Breaker | 160/192/180/228 | Yes
Active | 389 | 2025W1-GD-S389 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 222 | 233.6 | 115.61 | 121.65 | ATSI_P2-2_OES-138-003_SRT-A | Bus | 160/192/180/228 | Yes
Active | 152 | 2025W1-GD-S152 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 226 | 233.5 | 117.72 | 121.63 | ATSI_P2-3_OES-138-026_SRT-A | Breaker | 160/192/180/228 | Yes
Active | 452 | 2025W1-GD-S452 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1001.6 | 1011.1 | 118.81 | 119.94 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 | Yes
Active | 453 | 2025W1-GD-S453 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 284.1 | 325.4 | 104.46 | 119.65 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 153 | 2025W1-GD-S153 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 313.8 | 324.6 | 115.37 | 119.34 | ATSI_P2-3_OES-138-023T_SRT-SL | Breaker | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 154 | 2025W1-GD-S154 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 314.1 | 324.5 | 115.46 | 119.3 | ATSI_P2-3_OES-138-024AT_SRT-A | Breaker | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 156 | 2025W1-GD-S156 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 237.7 | 238.4 | 118.86 | 119.19 | ATSI_P2-3_OES-138-024AT_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 8 | 2025W1-GD-S8 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 237.7 | 238.4 | 118.86 | 119.19 | ATSI_P1-2_OES-138-935TB_SRT-A | Single | 163/200/201/220 | Yes
Active | 157 | 2025W1-GD-S157 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 237.6 | 238.3 | 118.8 | 119.16 | ATSI_P2-3_OES-138-023T_SRT-SL | Breaker | 163/200/201/220 | Yes
Active | 158 | 2025W1-GD-S158 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 326.5 | 334.9 | 115.79 | 118.77 | DAY_URBANA_FB_DB_D_SRT-A | Breaker | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 454 | 2025W1-GD-S454 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 994.4 | 999.6 | 117.96 | 118.57 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 | Yes
Active | 390 | 2025W1-GD-S390 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 284.7 | 321.3 | 104.65 | 118.14 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 161 | 2025W1-GD-S161 | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 954.4 | 945.5 | 119.15 | 118.04 | PL_48_P42_101954_SRT-A | Breaker | 647/801/746/903 | Yes
Active | 162 | 2025W1-GD-S162 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 953.7 | 944.8 | 119.06 | 117.95 | PL_08_P42_102683_SRT-A | Breaker | 647/801/746/903 | Yes
Active | 163 | 2025W1-GD-S163 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 953.7 | 944.8 | 119.06 | 117.95 | PL_08_P42_101955_SRT-A | Breaker | 647/801/746/903 | Yes
Active | 164 | 2025W1-GD-S164 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 953.7 | 944.6 | 119.06 | 117.92 | PL_08_P42_102684_SRT-A | Breaker | 647/801/746/903 | Yes
Active | 165 | 2025W1-GD-S165 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 323.3 | 332.1 | 114.66 | 117.77 | DAY_URBANA_FB_DB_C_SRT-A | Breaker | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 166 | 2025W1-GD-S166 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 284.1 | 320 | 104.45 | 117.64 | ATSI_P2-3_OES-138-0208BT_SRT-A | Breaker | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 391 | 2025W1-GD-S391 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 322.6 | 331.2 | 114.4 | 117.46 | URBANA_138KV_W_SRT-A | Bus | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 455 | 2025W1-GD-S455 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 233.1 | 233.8 | 116.54 | 116.9 | ATSI_P7-1_OES-138-065T_SRT-A | Tower | 163/200/201/220 | Yes
Active | 167 | 2025W1-GD-S167 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 179.6 | 202 | 103.82 | 116.75 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 131/173/136/178 | Yes
Active | 9 | 2025W1-GD-S9 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 306.2 | 316.6 | 112.56 | 116.4 | ATSI_P1-2_OES-138-935TB_SRT-A | Single | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 456 | 2025W1-GD-S456 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 304.3 | 313.6 | 111.89 | 115.3 | ATSI_P7-1_OES-138-065T_SRT-A | Tower | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 168 | 2025W1-GD-S168 | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 926.4 | 917.5 | 115.66 | 114.55 | PL_48_P42_103291_SRT-A | Breaker | 647/801/746/903 | Yes
Active | 169 | 2025W1-GD-S169 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 227.5 | 228.4 | 113.73 | 114.2 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 170 | 2025W1-GD-S170 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 252.4 | 276.1 | 104.31 | 114.09 | ATSI_P2-3_OES-138-048_SRT-A | Breaker | 200/242/226/286 | Yes
Active | 394 | 2025W1-GD-S394 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 252.4 | 276.1 | 104.31 | 114.09 | ATSI_P2-2_OES-138-002_SRT-A | Bus | 200/242/226/286 | Yes
Active | 457 | 2025W1-GD-S457 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 259.7 | 275.9 | 107.3 | 114.01 | ATSI_P7-1_OES-138-065T_SRT-A | Tower | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 458 | 2025W1-GD-S458 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 262.3 | 274.8 | 108.4 | 113.55 | ATSI_P7-1_OES-345-68T_SRT-A | Tower | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 11 | 2025W1-GD-S11 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 662.7 | 744 | 751.2 | 112.27 | 113.35 | DVP_P1-2: LN 567_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 13 | 2025W1-GD-S13 | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 908.4 | 899.2 | 113.41 | 112.26 | PL_48_P12_101741_SRT-A | Single | 647/801/746/903 | Yes
Active | 14 | 2025W1-GD-S14 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 907.7 | 898.6 | 113.32 | 112.18 | PL_08_P12_101740_SRT-A | Single | 647/801/746/903 | Yes
Active | 172 | 2025W1-GD-S172 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 310.6 | 316 | 110.13 | 112.05 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 15 | 2025W1-GD-S15 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 208 | 215.1 | 108.33 | 112.01 | ATSI_P1-2_OES-138-018_SRT-A | Single | 160/192/180/228 | Yes
Active | 173 | 2025W1-GD-S173 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 177.8 | 192.8 | 102.8 | 111.45 | AEP_P4_#9653_05GAY 138_102_SRT-A | Breaker | 131/173/136/178 | Yes
Removed | 460 | 2025W1-GD-S460 | 243522 | 05HARRISON | 243593 | 05ZUBER | 1 | 138 | 205 | 180 | 200.7 | 199.1 | 111.49 | 110.62 | AEP_P7-1_#10921___SRT-A | Tower | 150/212/189/234 | Yes
Active | 461 | 2025W1-GD-S461 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 204.2 | 212.1 | 106.35 | 110.47 | ATSI_P7-1_OES-138-066_SRT-A | Tower | 160/192/180/228 | Yes
Active | 462 | 2025W1-GD-S462 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 210.6 | 219.8 | 105.3 | 109.92 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 163/200/201/220 | Yes
Active | 18 | 2025W1-GD-S18 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 300.9 | 309.5 | 106.69 | 109.75 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Single | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 175 | 2025-W1-GD-S175 | 242687 | 05JOHNMT | 242734 | 05NEWLDN | 1 | 138 | 205 | 285 | 303.4 | 312.7 | 106.47 | 109.72 | AEP_P4_#3174_05CLOVRD 765_AA2_SRT-A | Breaker | 205/285/258/320 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | The ratings in the cases reflect B4000.211
Removed | 176 | 2025W1-GD-S176 | 243522 | 05HARRISON | 243593 | 05ZUBER | 1 | 138 | 205 | 180 | 199 | 197.3 | 110.54 | 109.63 | AEP_P4_#18274_05MARION RD 138_CB6_SRT-A | Breaker | 150/212/189/234 | Yes
Active | 178 | 2025W1-GD-S178 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 173.7 | 189.4 | 100.42 | 109.48 | AEP_P4_#10715_05COLE 345_C_SRT-A | Breaker | 131/173/136/178 | Yes
Removed | 179 | 2025W1-GD-S179 | 243522 | 05HARRISON | 243593 | 05ZUBER | 1 | 138 | 205 | 180 | 198.4 | 196.7 | 110.24 | 109.3 | AEP_P4_#18275_05MARION RD 138_CB7_SRT-A | Breaker | 150/212/189/234 | Yes
Active | 180 | 2025W1-GD-S180 | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1079 | 1175.8 | 1179.2 | 108.97 | 109.29 | PL_48_P42_000438_SRT-A | Breaker | 647/801/746/903 | Yes
Active | 464 | 2025W1-GD-S464 | 208120 | SU10 | 208113 | SUSQ | 1 | 230 | 229 | 1079 | 1175.8 | 1179.2 | 108.97 | 109.29 | PL_48_P71_102649_SRT-A | Tower | 647/801/746/903 | Yes
Active | 398 | 2025W1-GD-S398 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 210.8 | 218.4 | 105.38 | 109.21 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 163/200/201/220 | Yes
Active | 19 | 2025W1-GD-S19 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 662.7 | 715.2 | 723 | 107.92 | 109.1 | DVP_P1-2: LN 557_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 181 | 2025W1-GD-S181 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 210.4 | 218.1 | 105.19 | 109.06 | ATSI_P2-3_OES-138-0208BT_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 399 | 2025W1-GD-S399 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 245.8 | 263.8 | 101.58 | 109 | URBANA_138KV_W_SRT-A | Bus | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 465 | 2025W1-GD-S465 | 241980 | AD2-163_POI | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 184 | 209.1 | 95.81 | 108.91 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
Active | 183 | 2025W1-GD-S183 | 243522 | 05HARRISON | 243550 | 05OBETZ | 1 | 138 | 205 | 223 | 242.4 | 242.4 | 108.68 | 108.7 | AEP_P4_#9672_05HARRISON 138_2W_SRT-A | Breaker | 223/223/281/281 | Yes
Active | 184 | 2025W1-GD-S184 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 178 | 191 | 193.5 | 107.3 | 108.68 | DEOK_P4_1403_MIAMI FORT_SRT-A | Breaker | DEOK: 178/178/224/224, AEP: 167/245/210/280 | Yes
Active | 187 | 2025W1-GD-S187 | 241980 | AD2-163_POI | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 185.6 | 208.1 | 96.67 | 108.37 | ATSI_P2-3_OES-138-0208BT_SRT-A | Breaker | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
Active | 467 | 2025W1-GD-S467 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 171.2 | 187 | 98.96 | 108.11 | AEP_P7-1_#17439___SRT-A | Tower | 131/173/136/178 | Yes
Active | 400 | 2025W1-GD-S400 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 298.3 | 304.2 | 105.79 | 107.88 | ATSI_P2-2_OES-138-054_SRT-A | Bus | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 401 | 2025W1-GD-S401 | 241980 | AD2-163_POI | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 184.7 | 206.9 | 96.17 | 107.76 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
Active | 189 | 2025-W1-GD-S189 | 249567 | 08M.FORT | 250057 | 08M.FORT | 10 | 345/138 | 212 | 498 | 514.2 | 534.2 | 103.26 | 107.26 | DEOK_P4_1418_MIAMI FORT_SRT-A | Breaker | 478/498/498/600/600/600 MVA | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 22 | 2025W1-GD-S22 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 194.1 | 205.5 | 101.08 | 107.04 | AEP_P1-2_#5809_1984_SRT-A | Single | 160/192/180/228 | Yes
Active | 468 | 2025W1-GD-S468 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 168.9 | 184.6 | 97.61 | 106.73 | AEP_P7-1_#16019___SRT-A | Tower | 131/173/136/178 | Yes
Active | 190 | 2025W1-GD-S190 | 243522 | 05HARRISON | 243550 | 05OBETZ | 1 | 138 | 205 | 223 | 236.5 | 237.6 | 106.05 | 106.52 | AEP_P4_#8094_05BIXBY 345_C_SRT-A | Breaker | 223/223/281/281 | Yes
Active | 469 | 2025W1-GD-S469 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345 | 205 | 1385 | 1449.5 | 1471.8 | 104.66 | 106.27 | 34506 34542_SRT-A | Tower | 1385/1385/1750/1750 | Yes
Active | 23 | 2025W1-GD-S23 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 213.9 | 212.4 | 106.95 | 106.21 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | Single | 163/200/201/220 | Yes
Active | 191 | 2025W1-GD-S191 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 212.8 | 212.3 | 106.41 | 106.17 | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 24 | 2025W1-GD-S24 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 163 | 175.4 | 173 | 107.6 | 106.12 | Base Case | Single | 163/200/201/220 | Yes
Active | 470 | 2025W1-GD-S470 | 243232 | 05SORENS | 243211 | 05ALLEN | 1 | 345 | 205 | 897 | 952.5 | 950.4 | 106.19 | 105.95 | AEP_P7-1_#10901___SRT-A | Tower | 897/897/1138/1138 | Yes
Removed | 471 | 2025W1-GD-S471 | 243522 | 05HARRISON | 243593 | 05ZUBER | 1 | 138 | 205 | 180 | 192 | 190.6 | 106.65 | 105.89 | 34506 34542_SRT-A | Tower | 150/212/189/234 | Yes
Active | 193 | 2025-W1-GD-S193 | 232239 | SHARPTWN | 232249 | LAUREL | 1 | 69 | 235 | 43 | 45.5 | 45.3 | 105.81 | 105.41 | DPL_P4_2_DP6_SRT-A | Breaker | 43/43/54/54/52/52 (SN/SE/WN/WE/LLN/LLE) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 194 | 2025W1-GD-S194 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 165.2 | 182.3 | 95.46 | 105.4 | AEP_P4_#9668_05GROVES1 138_5_SRT-A | Breaker | 131/173/136/178 | Yes
Active | 28 | 2025W1-GD-S28 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 212.2 | 210.5 | 106.09 | 105.26 | AEP_P1-2_#18134_SRT-A | Single | 163/200/201/220 | Yes
Active | 196 | 2025W1-GD-S196 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 164 | 181.7 | 94.79 | 105.02 | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | Breaker | 131/173/136/178 | Yes
Active | 472 | 2025W1-GD-S472 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 178 | 183.6 | 186.8 | 103.16 | 104.96 | DEOK_P7.1_4561TODWOOD14562TODWOOD2_SRT-A | Tower | DEOK: 178/178/224/224, AEP: 167/245/210/280 | Yes
Active | 474 | 2025W1-GD-S474 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 190 | 201.1 | 98.94 | 104.72 | ATSI_P7-1_OES-138-065T_SRT-A | Tower | 160/192/180/228 | Yes
Active | 199 | 2025W1-GD-S199 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 280.1 | 283.8 | 102.99 | 104.33 | DAY_GREENE_FB_GJ_H_SRT-A | Breaker | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 200 | 2025W1-GD-S200 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 279.7 | 283.4 | 102.85 | 104.18 | DAY_GREENE_FB_GJ_I_SRT-A | Breaker | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 476 | 2025W1-GD-S476 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 290.6 | 293.7 | 103.04 | 104.16 | ATSI_P7-1_OES-345-68T_SRT-A | Tower | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 201 | 2025W1-GD-S201 | 253026 | 09GREENE | 241968 | AD1-140 TAP | 1 | 138 | 202/209 | 282 | 272.6 | 293.1 | 96.68 | 103.94 | ATSI_P2-3_OES-138-060H_SRT-A | Breaker | 233/282/263/330 (Dayton) 233/282/263/333 (ATSI) | Yes |  | Overlap FE EOL candidate
Active | 202 | 2025-W1-GD-S202 | 242688 | 05JOSHUA | 247670 | 05JOSHUA_XFL | 1 | 138 | 205 | 747 | 778.1 | 774.9 | 104.16 | 103.74 | AEP_P4_#3174_05CLOVRD 765_AA2_SRT-A | Breaker | 775/1114/982/1241 (transformer lead) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 477 | 2025-W1-GD-S477 | 239030 | 02OTTAWA | 238874 | 02LAKVEW | 1 | 138 | 202 | 516 | 527.9 | 535.3 | 102.3 | 103.74 | ATSI_P7-1_TE-345-027B_SRT-A | Tower | 448/516/448/543 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 32 | 2025W1-GD-S32 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 233 | 240.2 | 241.3 | 103.07 | 103.56 | Base Case | Single | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 478 | 2025W1-GD-S478 | 207973 | FRAC | 208072 | SIEG | 1 | 230 | 229 | 628 | 644.7 | 649.7 | 102.65 | 103.46 | PL_60_P71_000890_SRT-A | Tower | 513/628/564/682 | Yes
Active | 34 | 2025W1-GD-S34 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 208.3 | 206.6 | 104.15 | 103.29 | AEP_P1-2_#18232_SRT-A | Single | 163/200/201/220 | Yes
Active | 480 | 2025W1-GD-S480 | 242802 | 05SMITHMTN | 242775 | 05ROCKCAS SS | 1 | 138 | 205 | 409 | 415.9 | 421.9 | 101.69 | 103.16 | AEP_P7-1_#10817___SRT-A | Tower | 358/409/453/501 | Yes
Active | 203 | 2025-W1-GD-S203 | 249576 | 08WODSDL | 249574 | 08TDHNTR | 2 | 345 | 212 | 1245 | 1294.3 | 1281.3 | 103.96 | 102.91 | DEOK_P4_1517_WOODSDALE_SRT-SL | Breaker | 1509/1509/1894/1894 MVA | No | Substation Equipment Exclusion
Active | 204 | 2025-W1-GD-S204 | 249576 | 08WODSDL | 249574 | 08TDHNTR | 1 | 345 | 212 | 1245 | 1294.3 | 1281.3 | 103.96 | 102.91 | DEOK_P4_1513_WOODSDALE_SRT-SL | Breaker | 1509/1509/1894/1894 MVA | No | Substation Equipment Exclusion
Active | 36 | 2025-W1-GD-S36 | 242687 | 05JOHNMT | 242734 | 05NEWLDN | 1 | 138 | 205 | 285 | 283.9 | 293.2 | 99.62 | 102.87 | AEP_P1-2_#3174_6_SRT-A | Single | 205/285/258/320 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | The ratings in the cases reflect B4000.211
Active | 405 | 2025W1-GD-S405 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 159.7 | 178 | 92.29 | 102.87 | AEP_P2-2_#9665_05GROVES2 138_W_SRT-A | Bus | 131/173/136/178 | Yes
Active | 481 | 2025W1-GD-S481 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 861.1 | 865.1 | 102.14 | 102.62 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 | Yes
Active | 205 | 2025W1-GD-S205 | 243522 | 05HARRISON | 243550 | 05OBETZ | 1 | 138 | 205 | 223 | 227 | 228.3 | 101.8 | 102.38 | AEP_P4_#6763_05BIXBY 345_C1_SRT-A | Breaker | 223/223/281/281 | Yes
Active | 406 | 2025W1-GD-S406 | 243522 | 05HARRISON | 243550 | 05OBETZ | 1 | 138 | 205 | 223 | 227 | 228.3 | 101.8 | 102.38 | AEP_P2-2_#6763_05BIERSR 345_2_SRT-A | Bus | 223/223/281/281 | Yes
Active | 206 | 2025W1-GD-S206 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 178 | 179.4 | 182.1 | 100.77 | 102.33 | AEP_P4_#2812_05TANNER 345_T2_SRT-A | Breaker | DEOK: 178/178/224/224, AEP: 167/245/210/280 | Yes
Active | 207 | 2025W1-GD-S207 | 243550 | 05OBETZ | 243539 | 05MARION RD | 1 | 138 | 205 | 223 | 226.8 | 228 | 101.7 | 102.23 | AEP_P4_#9672_05HARRISON 138_2W_SRT-A | Breaker | 223/223/281/281 | Yes
Active | 208 | 2025W1-GD-S208 | 243262 | 05COLLEGE C | 250001 | 08COLINV | 1 | 138 | 205/212 | 178 | 179.1 | 181.9 | 100.62 | 102.22 | DEOK_P4_1401_MIAMI FORT_SRT-A | Breaker | DEOK: 178/178/224/224, AEP: 167/245/210/280 | Yes
Active | 209 | 2025W1-GD-S209 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 239.4 | 247.3 | 98.91 | 102.18 | ATSI_P2-3_OES-138-065H_SRT-A | Breaker | 200/242/226/286 | Yes
Active | 482 | 2025W1-GD-S482 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 191.8 | 196 | 99.87 | 102.06 | 34506 34542_SRT-A | Tower | 160/192/180/228 | Yes
Active | 407 | 2025W1-GD-S407 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 230.2 | 246.6 | 95.11 | 101.92 | ATSI_P2-2_OES-138-002_SRT-A | Bus | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Removed | 210 | 2025W1-GD-S210 | 242865 | 05JEFRSO | 248000 | 06CLIFTY | 1 | 345 | 205/206 | 2354 | 2401.1 | 2389 | 102 | 101.49 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker | 2354/2354/2991/2991 | Yes No
Active | 483 | 2025W1-GD-S483 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 855.5 | 855.3 | 101.48 | 101.46 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 | Yes
Active | 484 | 2025W1-GD-S484 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 156.9 | 175.3 | 90.69 | 101.33 | AEP_P7-1_#17440___SRT-A | Tower | 131/173/136/178 | Yes
Active | 38 | 2025W1-GD-S38 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 282.4 | 284.4 | 100.15 | 100.87 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | Single | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 410 | 2025W1-GD-S410 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138 | 202/209 | 272 | 264.4 | 274.3 | 97.2 | 100.86 | ATSI_P2-2_OES-138-054_SRT-A | Bus | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 219 | 2025W1-GD-S219 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 1203 | 1211.9 | 1211.1 | 100.74 | 100.67 | DVP_P4-2: 562T563_SRT-S | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | Yes |  | DOM-2024-2023-DNH reconductors portions of Lines 211 and 228, May TEAC 2025.
Active | 220 | 2025-W1-GD-S220 | 213490 | CHICHST2 | 213496 | CHIREACT_53 | 1 | 230 | 230 | 772 | 786.8 | 776.9 | 101.92 | 100.63 | PECO_P4_CHICH045_SRT-A | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 221 | 2025-W1-GD-S221 | 213496 | CHIREACT_53 | 213972 | TRAINER | 1 | 230 | 230 | 772 | 786.8 | 776.9 | 101.92 | 100.63 | PECO_P4_CHICH045_SRT-A | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 222 | 2025-W1-GD-S222 | 213496 | CHIREACT_53 | 213972 | TRAINER | 1 | 230 | 230 | 772 | 786.9 | 776.9 | 101.92 | 100.63 | PECO_P4_CHICH195_SRT-A | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 223 | 2025-W1-GD-S223 | 213490 | CHICHST2 | 213496 | CHIREACT_53 | 1 | 230 | 230 | 772 | 786.9 | 776.9 | 101.92 | 100.63 | PECO_P4_CHICH195_SRT-A | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 411 | 2025-W1-GD-S411 | 213496 | CHIREACT_53 | 213972 | TRAINER | 1 | 230 | 230 | 772 | 785.6 | 776.9 | 101.77 | 100.63 | PECO_P2-2_CHI230B1_SRT-A | Bus | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 412 | 2025-W1-GD-S412 | 213490 | CHICHST2 | 213496 | CHIREACT_53 | 1 | 230 | 230 | 772 | 785.6 | 776.9 | 101.77 | 100.63 | PECO_P2-2_CHI230B1_SRT-A | Bus | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 224 | 2025-W1-GD-S224 | 213496 | CHIREACT_53 | 213972 | TRAINER | 1 | 230 | 230 | 772 | 786 | 776.6 | 101.81 | 100.6 | PECO_P4_CHICH435_SRT-A | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 225 | 2025-W1-GD-S225 | 213490 | CHICHST2 | 213496 | CHIREACT_53 | 1 | 230 | 230 | 772 | 786 | 776.6 | 101.81 | 100.6 | PECO_P4_CHICH435_SRT-A | Breaker | 721/840/756/876/749/870 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 39 | 2025-W1-GD-S39 | 231000 | CLAY_230 | 214235 | LINWOOD84 | 1 | 230 | 230/235 | 800 | 816.5 | 803.2 | 102.07 | 100.4 | PECO_P1-2_220-85_SRT-A | Single | PECO: 731/885/821/978/804/960 (SN/SE/WN/WE/LN/LE) DPL: 653/808/752/910/733/891 (SN/SE/WN/WE/LN/LE) | No | Substation Equipment Exclusion
Active | 227 | 2025-W1-GD-S227 | 232239 | SHARPTWN | 232249 | LAUREL | 1 | 69 | 235 | 43 | 43.1 | 43.1 | 100.21 | 100.28 | DPL_P4_2_DP36_SRT-A | Breaker | 43/43/54/54/52/52 (SN/SE/WN/WE/LLN/LLE) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 40 | 2025W1-GD-S40 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 983.2 | 985.8 | 985.6 | 100.26 | 100.24 | DVP_P1-2: LN 563_SRT-A | Single | 1046/1046/1203:1160/1160/1333:1140/1140/1311 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes |  | DOM-2024-2023-DNH reconductors portions of Lines 211 and 228, May TEAC 2025.
Active | 229 | 2025W1-GD-S229 | 243550 | 05OBETZ | 243539 | 05MARION RD | 1 | 138 | 205 | 223 | 220.9 | 223.2 | 99.07 | 100.09 | AEP_P4_#8094_05BIXBY 345_C_SRT-A | Breaker | 223/223/281/281 | Yes
Active | 488 | 2025W1-GD-S488 | 242775 | 05ROCKCAS SS | 242720 | 05MONETA | 1 | 138 | 205 | 409 | 400.8 | 409.2 | 97.99 | 100.05 | AEP_P7-1_#10817___SRT-A | Tower | 409/409/516/516 | Yes

## Summer IPD
2030 RTEP PJM Individual Plant Deliverability Result (Summer)
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
Active | 2025W1-IPD-S1 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 242 | 404.5 | 145.98 | 167.15 | AD1-081 | ATSI_P2-4_OES-138-047_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S2 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 406.4 | 133.63 | 144.13 | AD1-140 | ATSI_P2-3_OES-138-060H_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S3 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 396.3 | 129.41 | 140.52 | 08ZIMRHP | ATSI_P2-3_OES-138-060H_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S4 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 394.9 | 128.94 | 140.02 | 08ZIMRLP | ATSI_P2-3_OES-138-060H_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S5 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 261.8 | 116.13 | 136.35 | AD1-140 | ATSI_P7-1_OES-138-066A_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S6 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 257.8 | 116.44 | 134.28 | AD1-140 | ATSI_P2-2_OES-138-055T_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S7 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 378.3 | 121.93 | 134.14 | AD1-081 | ATSI_P2-3_OES-138-060H_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S8 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 257.2 | 116.49 | 133.97 | AD1-140 | ATSI_P2-3_OES-138-0208BT_SRT-A | 160 / 192 / 180 / 228 | Yes
N/A | N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 886.9 | 133.02 | 133.83 | AF1-125 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 886.6 | 132.98 | 133.79 | AF1-123 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 886.6 | 132.98 | 133.78 | AF1-124 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 870.7 | 129.88 | 131.39 | AF1-125 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 870.6 | 129.85 | 131.36 | AF1-123 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 870.5 | 129.84 | 131.36 | AF1-124 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2025W1-IPD-S9 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 867.1 | 130.27 | 130.85 | AE1-173 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S10 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 855.5 | 128.6 | 129.09 | W1-029 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S11 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 855.5 | 128.59 | 129.09 | Z1-036 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S12 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 854.3 | 128.43 | 128.92 | AB2-190 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S13 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 854.3 | 128.4 | 128.92 | LTFIMP_O-066 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S14 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 854.3 | 128.43 | 128.91 | AD1-074 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S15 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 854.3 | 128.43 | 128.91 | AD1-151 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S16 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 853.9 | 128.37 | 128.85 | AD1-025 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S17 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 295 | 117.4 | 128.82 | AD2-163 | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S18 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 295 | 117.4 | 128.82 | AD2-163 | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S19 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 853.6 | 128.32 | 128.8 | AB2-134 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S20 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 853 | 127.31 | 128.72 | AE1-173 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S21 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 852.9 | 128.24 | 128.69 | AE2-033 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S22 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 852 | 128.09 | 128.56 | AC1-161 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S23 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 851.9 | 128.08 | 128.56 | AC2-141 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S24 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 851.7 | 128.06 | 128.51 | AE1-149 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S25 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 851.1 | 127.97 | 128.43 | AC1-086 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S26 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 851 | 127.95 | 128.41 | AC1-216 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S27 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 850.3 | 127.9 | 128.31 | 1STONECA | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S28 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 850.3 | 127.86 | 128.31 | AF1-017 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S29 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 293.8 | 116.88 | 128.29 | AD1-140 | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S30 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 293.8 | 116.88 | 128.29 | AD1-140 | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S31 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 847.1 | 126.47 | 127.83 | AD1-151 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S32 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 847.1 | 126.47 | 127.82 | AB2-190 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S33 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 846.5 | 126.38 | 127.74 | AD1-025 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S34 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 846.2 | 126.33 | 127.69 | AB2-134 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S35 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 845.6 | 126.23 | 127.59 | W1-029 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S36 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 662.7 | 845.5 | 126.23 | 127.59 | Z1-036 | DVP_P1-2: LN 217_SRT-S | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 2025W1-IPD-S37 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290.3 | 115.12 | 126.77 | 08ZIMRHP | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S38 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290.3 | 115.12 | 126.77 | 08ZIMRHP | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S39 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 289.2 | 117.4 | 126.31 | AD2-163 | ATSI_P1-2_OES-138-002D_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S40 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 288 | 116.88 | 125.77 | AD1-140 | ATSI_P1-2_OES-138-002D_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S41 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 247 | 123.83 | 123.5 | AE2-148 | 34506 34542_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S42 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 244.5 | 122.31 | 122.23 | AC1-085 | 34506 34542_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S43 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 244.1 | 121.97 | 122.04 | GM 55199 IA | 34506 34542_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S44 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 341.4 | 111.51 | 121.05 | AD1-140 | ATSI_P7-1_OES-138-066A_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S45 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 338.5 | 111.6 | 120.05 | AD1-140 | ATSI_P2-2_OES-138-055T_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S46 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 338.5 | 118.41 | 120.04 | AD1-140 | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S47 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 337.6 | 111.45 | 119.73 | AD1-140 | ATSI_P2-3_OES-138-0208BT_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S48 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 226 | 113.04 | 117.69 | AD2-163 | ATSI_P2-3_OES-138-025_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S49 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 225.1 | 112.95 | 117.23 | AD2-163 | ATSI_P2-3_OES-138-026_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S50 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 225 | 111.02 | 117.17 | AD2-163 | ATSI_P2-3_OES-138-050_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S51 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 233.5 | 116.35 | 116.74 | AC1-085 | ATSI_P1-2_OES-138-935TB_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S52 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 233.5 | 116.35 | 116.74 | AC1-085 | ATSI_P2-3_OES-138-024AT_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S53 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 233.4 | 116.29 | 116.72 | AC1-085 | ATSI_P2-3_OES-138-023T_SRT-SL | 163/200/201/220 | Yes
Active | 2025W1-IPD-S54 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 223.9 | 110.35 | 116.62 | AD2-163 | ATSI_P2-3_OES-138-051_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S55 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 223.9 | 110.35 | 116.62 | AD2-163 | ATSI_P2-2_OES-138-003_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S56 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 223.3 | 100.85 | 116.3 | AD2-163 | ATSI_P7-1_OES-138-066A_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S57 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 326.7 | 105.8 | 115.85 | 08ZIMRHP | ATSI_P7-1_OES-138-066A_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S58 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 326.5 | 112.83 | 115.77 | AD1-140 | DAY_URBANA_FB_DB_D_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S59 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 222 | 101.69 | 115.62 | AD2-163 | ATSI_P2-3_OES-138-0208BT_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S60 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 199.3 | 102.08 | 115.22 | AD2-016 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S61 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 324.7 | 113.5 | 115.14 | 08ZIMRHP | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S62 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 220.9 | 101.19 | 115.05 | AD2-163 | ATSI_P2-2_OES-138-055T_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S63 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 220.8 | 108.86 | 115 | AD1-140 | ATSI_P2-3_OES-138-050_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S64 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 323.6 | 111.7 | 114.77 | AD1-140 | DAY_URBANA_FB_DB_C_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S65 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 323.6 | 105.92 | 114.76 | 08ZIMRHP | ATSI_P2-2_OES-138-055T_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S66 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 323 | 105.77 | 114.54 | 08ZIMRHP | ATSI_P2-3_OES-138-0208BT_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S67 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 322.9 | 111.52 | 114.52 | AD1-140 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S68 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 322.9 | 111.52 | 114.52 | AD1-140 | URBANA_138KV_W_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S69 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 229 | 114.05 | 114.49 | AC1-085 | ATSI_P7-1_OES-138-065T_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S70 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 219.7 | 108.19 | 114.44 | AD1-140 | ATSI_P2-2_OES-138-003_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S71 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 219.7 | 108.19 | 114.44 | AD1-140 | ATSI_P2-3_OES-138-051_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S72 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 322.3 | 112.7 | 114.28 | 08ZIMRLP | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S73 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 197.1 | 100.81 | 113.92 | 08ZIMRHP | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S74 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 320.5 | 112.32 | 113.67 | AE2-148 | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S75 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 318 | 111.24 | 112.77 | AC1-085 | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S76 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 215 | 107.97 | 112 | AD2-163 | ATSI_P1-2_OES-138-018_SRT-A | 160 / 192 / 180 / 228 | Yes
N/A | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 677.7 | 757.9 | 113.38 | 111.83 | AF1-125 | DVP_P1-2: LN 588_SRT-A | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2025W1-IPD-S77 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | - | 110.94 | 111.55 | AD1-140 | Base Case | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
N/A | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 677.7 | 755.8 | 113.06 | 111.51 | AF1-123 | DVP_P1-2: LN 588_SRT-A | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2025W1-IPD-S78 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 223 | 110.98 | 111.51 | GM 55199 IA | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 163/200/201/220 | Yes
N/A | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 677.7 | 755.3 | 112.98 | 111.44 | AF1-124 | DVP_P1-2: LN 588_SRT-A | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2025W1-IPD-S79 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 313.9 | 102.03 | 111.3 | AE2-305 | ATSI_P7-1_OES-138-066A_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S80 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 313.7 | 108.16 | 111.25 | 08ZIMRHP | DAY_URBANA_FB_DB_D_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S81 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 312 | 107.58 | 110.64 | 08ZIMRLP | DAY_URBANA_FB_DB_D_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S82 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 310.9 | 107.01 | 110.23 | 08ZIMRHP | DAY_URBANA_FB_DB_C_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S83 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 310.7 | 102.13 | 110.18 | AE2-305 | ATSI_P2-2_OES-138-055T_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S84 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 310.5 | 107.87 | 110.12 | AD1-140 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S85 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 310 | 106.77 | 109.94 | 08ZIMRHP | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S86 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 310 | 106.77 | 109.94 | 08ZIMRHP | URBANA_138KV_W_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S87 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 309.8 | 101.98 | 109.85 | AE2-305 | ATSI_P2-3_OES-138-0208BT_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S88 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 272 | 298.5 | 93.9 | 109.75 | AE2-305 | ATSI_P7-1_OES-138-066A_SRT-A | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 2025W1-IPD-S89 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 309.1 | 106.43 | 109.62 | 08ZIMRLP | DAY_URBANA_FB_DB_C_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S90 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 308.4 | 106.21 | 109.34 | 08ZIMRLP | URBANA_138KV_W_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S91 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 308.4 | 106.21 | 109.34 | 08ZIMRLP | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S92 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 307.7 | 98.97 | 109.1 | AD2-163 | ATSI_P7-1_OES-138-066A_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S93 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 188.6 | 100.24 | 109.03 | AD2-016 | AEP_P4_#9653_05GAY 138_102_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S94 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 272 | 294.6 | 104.27 | 108.3 | AE2-305 | ATSI_P2-3_OES-138-023T_SRT-SL | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 2025W1-IPD-S95 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 272 | 294.5 | 104.36 | 108.27 | AE2-305 | ATSI_P1-2_OES-138-935TB_SRT-A | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 2025W1-IPD-S96 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 272 | 294.5 | 104.36 | 108.27 | AE2-305 | ATSI_P2-3_OES-138-024AT_SRT-A | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 2025W1-IPD-S97 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 187.2 | 98.9 | 108.2 | AD2-016 | AEP_P7-1_#17439___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S98 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 207.4 | 101.55 | 108.04 | AD2-163 | AEP_P4_#9530_05BEATTY 138_5C_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S99 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 207.3 | 101.51 | 107.96 | AD2-163 | AEP_P4_#5809_05BEATTY 138_5W_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S100 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 207.3 | 101.51 | 107.96 | AD2-163 | AEP_P1-2_#5809_1984_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S101 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 272 | 293.6 | 94.07 | 107.94 | AE2-305 | ATSI_P2-2_OES-138-055T_SRT-A | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 2025W1-IPD-S102 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 303.7 | 99.06 | 107.7 | AD2-163 | ATSI_P2-2_OES-138-055T_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S103 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 303.5 | 98.91 | 107.62 | AD2-163 | ATSI_P2-3_OES-138-0208BT_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S104 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 303.3 | 106.39 | 107.56 | AD1-081 | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S105 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 206.3 | 103.07 | 107.47 | AD2-163 | ATSI_P7-1_OES-138-066_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S106 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 272 | 292.3 | 93.87 | 107.47 | AE2-305 | ATSI_P2-3_OES-138-0208BT_SRT-A | 221/272/301/330 (Dayton) 278/339/315/401 (ATSI) | Yes
Active | 2025W1-IPD-S107 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 185.4 | 97.83 | 107.16 | 08ZIMRHP | AEP_P7-1_#17439___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S108 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 302.1 | 105.83 | 107.12 | AD2-163 | 34506 34542_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S109 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 205.6 | 99.4 | 107.11 | AD2-163 | DAY_URBANA_FB_DB_C_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S110 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 205.6 | 99.52 | 107.09 | AD2-163 | URBANA_138KV_W_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S111 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 205.6 | 99.52 | 107.09 | AD2-163 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S112 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 205.6 | 102.36 | 107.08 | AD1-081 | ATSI_P2-3_OES-138-025_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S113 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 185 | 98.14 | 106.96 | 08ZIMRHP | AEP_P4_#9653_05GAY 138_102_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S114 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 184.6 | 97.44 | 106.73 | AE2-148 | AEP_P7-1_#17439___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S115 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 184.5 | 97.39 | 106.67 | 08ZIMRHP | AEP_P4_#10715_05COLE 345_C_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S116 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 204.7 | 102.27 | 106.64 | AD1-081 | ATSI_P2-3_OES-138-026_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S117 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 184.4 | 97.4 | 106.6 | AD2-016 | AEP_P4_#10715_05COLE 345_C_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S118 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 184.2 | 97.26 | 106.49 | AE2-148 | AEP_P4_#10715_05COLE 345_C_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S119 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 204.4 | 99.69 | 106.48 | AD1-081 | ATSI_P2-3_OES-138-050_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S120 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 204.4 | 98.76 | 106.45 | AD2-163 | DAY_URBANA_FB_DB_D_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S121 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 184.1 | 97.75 | 106.4 | AC2-029 | AEP_P4_#9653_05GAY 138_102_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S122 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 204 | 99.33 | 106.25 | AD2-163 | ATSI_P2-3_OES-138-023T_SRT-SL | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S123 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 203.8 | 99.4 | 106.16 | AD2-163 | ATSI_P1-2_OES-138-935TB_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S124 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | 203.8 | 99.4 | 106.16 | AD2-163 | ATSI_P2-3_OES-138-024AT_SRT-A | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S125 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 203.4 | 99.02 | 105.94 | AD1-081 | ATSI_P2-2_OES-138-003_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S126 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 203.4 | 99.02 | 105.94 | AD1-081 | ATSI_P2-3_OES-138-051_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S127 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 183.1 | 96.59 | 105.82 | 08ZIMRLP | AEP_P4_#10715_05COLE 345_C_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S128 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 210 | 106 | 104.99 | AE2-148 | AEP_P4_#8122_05BEATTY 345_302W_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S129 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 209.9 | 105.86 | 104.95 | AE2-148 | AEP_P4_#8121_05BEATTY 345_302C_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S130 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 208.5 | 105.26 | 104.25 | AE2-148 | AEP_P1-2_#18134_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S131 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | - | 103.44 | 104.11 | 08ZIMRHP | Base Case | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S132 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 293.6 | 101.01 | 104.1 | AD1-081 | DAY_URBANA_FB_DB_D_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025-W1-IPD-S133 | 217270 | PROSPECT69 | 218180 | NORTHPAT69 | 1 | 69 | 231 | 95 | 131.5 | 106.11 | 103.94 | LTFIMP_O-066 | PS_P7-1_B2228+K2263_LT_SRT-A | 95/132/129/155 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025W1-IPD-S134 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 179.7 | 94.54 | 103.88 | 08ZIMRHP | AEP_P7-1_#16019___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S135 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 292.9 | 101.7 | 103.85 | 08ZIMRHP | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S136 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 179.6 | 94.57 | 103.83 | AD2-016 | AEP_P7-1_#16019___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S137 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 179.4 | 94.4 | 103.69 | AE2-148 | AEP_P7-1_#16019___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S138 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | - | 105.04 | 103.67 | AC1-085 | Base Case | 163/200/201/220 | Yes
Active | 2025W1-IPD-S139 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 207.2 | 104.24 | 103.58 | AC1-085 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S140 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345 | 205 | 1385 | 1434.2 | 101.79 | 103.55 | GM 55199 IA | 34506 34542_SRT-A | 1385/1385/1750/1750 | Yes
Active | 2025W1-IPD-S141 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 207.1 | 104.27 | 103.55 | AC1-085 | AEP_P4_#8122_05BEATTY 345_302W_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S142 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 207.1 | 103.78 | 103.55 | GM 55199 IA | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S143 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 282 | 292 | 96.45 | 103.54 | 08ZIMRHP | ATSI_P2-3_OES-138-060H_SRT-A | 233/282/263/330 (Dayton) 233/282/263/333 (ATSI) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S144 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 207 | 104.13 | 103.52 | AC1-085 | AEP_P4_#8121_05BEATTY 345_302C_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S145 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 206.9 | 104.12 | 103.46 | GM 55199 IA | AEP_P4_#8122_05BEATTY 345_302W_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S146 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345 | 205 | 1385 | 1432.7 | 101.81 | 103.45 | U2-072 | 34506 34542_SRT-A | 1385/1385/1750/1750 | Yes
Active | 2025W1-IPD-S147 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | - | 102.84 | 103.45 | 08ZIMRLP | Base Case | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S148 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 206.8 | 103.96 | 103.42 | GM 55199 IA | AEP_P4_#8121_05BEATTY 345_302C_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S149 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 291.4 | 101.2 | 103.32 | 08ZIMRLP | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S150 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 178.7 | 92.9 | 103.32 | AD2-016 | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S151 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345 | 205 | 1385 | 1430.8 | 101.7 | 103.3 | AF1-227 | 34506 34542_SRT-A | 1385/1385/1750/1750 | Yes
Active | 2025W1-IPD-S152 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 290.8 | 99.89 | 103.1 | AD1-081 | DAY_URBANA_FB_DB_C_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S153 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 178.3 | 93.01 | 103.08 | AD2-016 | AEP_P4_#9668_05GROVES1 138_5_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S154 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 282 | 290.6 | 95.94 | 103.05 | 08ZIMRLP | ATSI_P2-3_OES-138-060H_SRT-A | 233/282/263/330 (Dayton) 233/282/263/333 (ATSI) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S155 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 178.2 | 93.74 | 103.03 | 08ZIMRLP | AEP_P7-1_#16019___SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S156 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 290.4 | 100.92 | 102.98 | GM 55199 IA | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S157 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 205.6 | 103.53 | 102.81 | AC1-085 | AEP_P1-2_#18134_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S158 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 289.8 | 99.72 | 102.78 | AD1-081 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S159 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 289.8 | 99.72 | 102.78 | AD1-081 | URBANA_138KV_W_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S160 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 205.4 | 103.38 | 102.72 | GM 55199 IA | AEP_P1-2_#18134_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S161 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 205.4 | 103.74 | 102.71 | AE2-148 | AEP_P4_#18234_05BIG PLAIN 345_CB1_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S162 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 205.4 | 103.65 | 102.71 | AE2-148 | AEP_P4_#18235_05BIG PLAIN 345_CB2_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S163 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 205.4 | 103.76 | 102.69 | AE2-148 | AEP_P4_#18236_05BIG PLAIN 345_CB3_SRT-A | 163/200/201/220 | Yes
Active | 2025-W1-IPD-S164 | 217270 | PROSPECT69 | 218180 | NORTHPAT69 | 1 | 69 | 231 | 95 | 131.5 | 104.82 | 102.6 | LTFIMP_O-066 | PS_P7-1_B2228+K2263_SRT-A | 95/132/129/155 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025W1-IPD-S165 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 204.4 | 103.33 | 102.22 | AE2-148 | AEP_P1-2_#18232_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S166 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 176.6 | 91.66 | 102.08 | 08ZIMRHP | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S167 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 203.7 | 102.49 | 101.85 | AC1-085 | DAY_GREENE_FB_GJ_I_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S168 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 176.2 | 91.73 | 101.84 | 08ZIMRHP | AEP_P4_#9668_05GROVES1 138_5_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S169 | 243522 | 05HARRISON | 243550 | 05OBETZ | 1 | 138 | 205 | 223 | 227.1 | 101.34 | 101.83 | AD2-016 | AEP_P4_#8094_05BIXBY 345_C_SRT-A | 223/223/281/281 | Yes
Active | 2025W1-IPD-S170 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 287 | 99.17 | 101.79 | AD2-163 | DAY_URBANA_FB_DB_D_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S171 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 176.1 | 92.86 | 101.79 | AD2-016 | AEP_P1-2_#5775_643_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S172 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 176.1 | 92.86 | 101.79 | AD2-016 | AEP_P4_#5775_05GAY 138_105_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S173 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 176 | 92.86 | 101.75 | AD2-016 | AEP_P4_#9815_05VINE 138_103_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S174 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 192 | 195.1 | 97.44 | 101.63 | AD1-081 | ATSI_P1-2_OES-138-018_SRT-A | 160 / 192 / 180 / 228 | Yes
Active | 2025W1-IPD-S175 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 192 | - | 96.37 | 101.31 | AD2-163 | Base Case | 160 / 192 / 180 / 228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-S176 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 175.2 | 91.21 | 101.27 | 08ZIMRLP | AEP_P4_#9668_05GROVES1 138_5_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S177 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 175.1 | 91.2 | 101.24 | AE2-148 | AEP_P4_#9668_05GROVES1 138_5_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S178 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 175.1 | 91.52 | 101.23 | 08ZIMRHP | AEP_P1-2_#10137_570_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S179 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 175.1 | 91.52 | 101.23 | 08ZIMRHP | AEP_P4_#10137_05COLE 345_B2_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S180 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 202.3 | 101.77 | 101.17 | GM 55199 IA | AEP_P4_#18235_05BIG PLAIN 345_CB2_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S181 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 202.3 | 101.84 | 101.17 | GM 55199 IA | AEP_P4_#18234_05BIG PLAIN 345_CB1_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S182 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 202.3 | 101.86 | 101.15 | GM 55199 IA | AEP_P4_#18236_05BIG PLAIN 345_CB3_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S183 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 174.8 | 91.37 | 101.03 | AE2-148 | AEP_P1-2_#10137_570_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S184 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 174.8 | 91.37 | 101.03 | AE2-148 | AEP_P4_#10137_05COLE 345_B2_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S185 | 216950 | ROSELAND | 217997 | LIVINGSTON | 1 | 230 | 231 | 885 | 891.9 | 100.37 | 100.79 | LTFIMP_O-066 | PS_P2-3_ROSE_1920_SRT-A | 731/885/821/978 | Yes
Active | 2025W1-IPD-S186 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 200 | 201.3 | 101.42 | 100.67 | GM 55199 IA | AEP_P1-2_#18232_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-S187 | 243522 | 05HARRISON | 243550 | 05OBETZ | 1 | 138 | 205 | 223 | 224.2 | 100.29 | 100.54 | AD2-016 | AEP_P4_#9672_05HARRISON 138_2W_SRT-A | 223/223/281/281 | Yes
Active | 2025W1-IPD-S188 | 216950 | ROSELAND | 217997 | LIVINGSTON | 1 | 230 | 231 | 885 | 889.4 | 100.04 | 100.49 | LTFIMP_O-066 | PS_P2-3_ROSE_1920_LT_SRT-A | 731/885/821/978 | Yes
N/A | N/A | 313818 | 6BENCHRCH | 314522 | 6CHCKTUK | 1 | 230 | 345 | 548 | 550.6 | 100.41 | 100.48 | AF1-125 | DVP_P1-2: LN 582_SRT-A | 583/583/670:740/740/852:715/715/823 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 313818 | 6BENCHRCH | 314522 | 6CHCKTUK | 1 | 230 | 345 | 548 | 550.5 | 100.38 | 100.45 | AF1-123 | DVP_P1-2: LN 582_SRT-A | 583/583/670:740/740/852:715/715/823 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 313818 | 6BENCHRCH | 314522 | 6CHCKTUK | 1 | 230 | 345 | 548 | 550.4 | 100.37 | 100.44 | AF1-124 | DVP_P1-2: LN 582_SRT-A | 583/583/670:740/740/852:715/715/823 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2025W1-IPD-S189 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 173.7 | 91.4 | 100.38 | 08ZIMRHP | AEP_P1-2_#5775_643_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S190 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 173.6 | 90.71 | 100.38 | 08ZIMRLP | AEP_P4_#10137_05COLE 345_B2_SRT-A | 131/173/136/178 | Yes
Active | 2025W1-IPD-S191 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 173 | 173.6 | 90.71 | 100.38 | 08ZIMRLP | AEP_P1-2_#10137_570_SRT-A | 131/173/136/178 | Yes