## Summer GenDeliv
Note 1: Scenario 4 results are provided for reference at this time and also to provide guidance (for consideration part of robustness evaluations) covering the event that the NJ and DE OSW generation were delayed beyond 2032.
2032 Scenario 4 RTEP PJM Generator Deliverability Result (Summer)
FG # Status | PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 5909.4 | 6328.2 | 145.19 | 155.48 | DVP_P1-2: LN 576_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1240.5 | 1307.8 | 147.16 | 155.14 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1233.2 | 1293 | 146.29 | 153.37 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5661 | 5869.3 | 143.72 | 149.01 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 4400.8 | 4691.2 | 136.69 | 145.71 | DVP_P1-2: LN 574_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3117 | 4252.6 | 4540.2 | 136.43 | 145.66 | DVP_P4-2: 562T578_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3985.6 | 4685.3 | 123.8 | 145.53 | DVP_P1-2: LN 9518_SRT-A | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3989.7 | 4664.7 | 123.92 | 144.89 | DVP_P1-2: LN 552_SRT-S | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5391 | 5642.8 | 136.86 | 143.26 | DVP_P4-2: 557T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3947.7 | 4607 | 122.62 | 143.1 | DVP_P1-2: LN 581_SRT-A | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 6735.8 | 7163.5 | 134.42 | 142.96 | DVP_P4-2: 57602_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 6735.7 | 7163.4 | 134.42 | 142.95 | DVP_P4-2: WT576_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 4120.8 | 4120.8 | 140.6 | 140.6 | DVP_P4-2: 56372_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 4110.4 | 4110.4 | 140.24 | 140.24 | DVP_P4-2: H6T563_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4754.7 | 5515.1 | 120.71 | 140.01 | DVP_P4-2: 568T581_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314282 | 6CARSON | 2 | 500/230 | 345 | 1056 | 1472.3 | 1472.3 | 139.42 | 139.42 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3117 | 4034.9 | 4335.5 | 129.45 | 139.09 | DVP_P4-2: 56272_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5175.4 | 5471.8 | 131.39 | 138.91 | DVP_P4-2: H2T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5160.4 | 5441.2 | 131.01 | 138.14 | DVP_P4-2: H1T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3117 | 3997.7 | 4298.2 | 128.25 | 137.89 | DVP_P4-2: 562T579_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 4018 | 4018 | 137.09 | 137.09 | DVP_P4-2: 562T563_SRT-S | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 4986.1 | 5570.5 | 122.5 | 136.86 | DVP_P1-2: LN 550_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 3323.1 | 3323.1 | 136.08 | 136.08 | DVP_P1-2: LN 563_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 5205.8 | 5295.2 | 132.16 | 134.43 | DVP_P4-2: 557T574_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 5439.5 | 5439.5 | 133.64 | 133.64 | DVP_P1-2: LN 563_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 6688.8 | 6688.8 | 133.48 | 133.48 | DVP_P4-2: H6T563_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3585.4 | 4290.4 | 111.36 | 133.26 | DVP_P1-2: LN 568_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 4578.7 | 5233.6 | 116.24 | 132.87 | DVP_P4-2: 568T581_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4568.6 | 5233.4 | 115.98 | 132.86 | DVP_P4-2: H1T581_SRT-S | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 3308.4 | 4109.4 | 106.76 | 132.61 | AP_P2-3_PE-500-019F_SRT-SL | Breaker | PEPCO: 2738/3099/3672: 3064/3567/4088 : 2738/3099/3672 DOM: 3803/3803/4373 : 4832/4832/5287 : 4668/4668/5141 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3714.3 | 3880 | 126.72 | 132.38 | DVP_P4-2: 57602_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3714.3 | 3880 | 126.72 | 132.38 | DVP_P4-2: WT576_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 3059.8 | 3219.2 | 125.29 | 131.82 | DVP_P1-2: LN 576_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3894.7 | 4235.2 | 120.97 | 131.55 | DVP_P1-2: LN 557_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 5012.1 | 5343.6 | 123.14 | 131.29 | AEP_P1-2_#18461_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 4819.1 | 5343.3 | 118.4 | 131.28 | DVP_P1-4: 6DAHLGREN_AF2-091 C_1_2_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3927.5 | 4222.3 | 121.99 | 131.15 | DVP_P1-2: LN 557_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1062 | 1105.4 | 125.98 | 131.13 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 4050.5 | 4204.1 | 125.81 | 130.58 | DVP_P1-2: LN 574_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 1041 | 1045.2 | 129.96 | 130.49 | PL_48_P42_101954_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4451.8 | 5138.1 | 113.02 | 130.44 | DVP_P4-2: 545T552_SRT-A | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1040.2 | 1044.4 | 129.86 | 130.39 | PL_08_P42_102683_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1040.2 | 1044.4 | 129.86 | 130.39 | PL_08_P42_101955_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1040.2 | 1044.4 | 129.86 | 130.38 | PL_08_P42_102684_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4777.5 | 5127.7 | 121.29 | 130.18 | DVP_P4-2: H2T557_SRT-S | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1056.8 | 1092.9 | 125.36 | 129.64 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4419.5 | 5100.5 | 112.2 | 129.49 | DVP_P4-2: H1T552_SRT-S | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4415.3 | 5093.8 | 112.09 | 129.32 | DVP_P4-2: H3T552_SRT-S | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 3183.1 | 4006.6 | 102.71 | 129.29 | AP_P2-3_PE-500-019B_SRT-A | Breaker | PEPCO: 2738/3099/3672: 3064/3567/4088 : 2738/3099/3672 DOM: 3803/3803/4373 : 4832/4832/5287 : 4668/4668/5141 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4757.5 | 5090.3 | 120.78 | 129.23 | DVP_P4-2: 56722_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3809.8 | 4154 | 118.33 | 129.03 | DVP_P1-2: LN 567_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 2 | 500/138 | 201 | 527 | 672.6 | 678.7 | 127.63 | 128.79 | AP_P2-3_MP-500-016_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 1 | 500/138 | 201 | 527 | 672.6 | 678.7 | 127.63 | 128.79 | AP_P2-3_MP-500-017_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4778.2 | 5068.9 | 121.31 | 128.69 | DVP_P4-2: G2T567_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4380.7 | 5044.4 | 111.21 | 128.06 | DVP_P4-2: H4T581_SRT-A | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4333 | 5038.3 | 110 | 127.91 | DVP_P4-2: 9517T581_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4976.2 | 5030.1 | 126.33 | 127.7 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 4107.8 | 4107.8 | 127.59 | 127.59 | DVP_P1-2: LN 567_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 1009.1 | 1013 | 125.97 | 126.47 | PL_48_P42_103291_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 1001.2 | 1005.2 | 124.99 | 125.5 | PL_48_P12_101741_SRT-A | Single | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 1 | 230 | 229 | 1079 | 1303 | 1353.5 | 120.76 | 125.44 | PL_48_P71_102649_SRT-A | Tower | 933/1079/998/1143 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1000.4 | 1004.5 | 124.89 | 125.41 | PL_08_P12_101740_SRT-A | Single | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3645.4 | 4251.9 | 107.16 | 124.99 | DVP_P1-2: LN 539_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1079 | 1303 | 1348 | 120.76 | 124.93 | PL_48_P42_000438_SRT-A | Breaker | 933/1079/998/1143 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3117 | 3361.1 | 3893 | 107.83 | 124.9 | DVP_P4-2: H1T541_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 2768 | 3036.3 | 113.35 | 124.33 | DVP_P1-2: LN 582_2_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5567.8 | 6215.6 | 111.11 | 124.04 | DVP_P4-2: 256T2410_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5621.7 | 6209 | 112.19 | 123.91 | DVP_P4-2: H1T550_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3605.4 | 4206.3 | 105.98 | 123.65 | DVP_P1-2: LN 569_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3579.8 | 3924.5 | 111.19 | 121.9 | DVP_P1-2: LN 2028_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3632.5 | 3919.2 | 112.83 | 121.73 | DVP_P1-2: LN 298_2_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4065.6 | 4782.9 | 103.21 | 121.42 | DVP_P4-2: H1T568_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3617.2 | 3903.9 | 112.35 | 121.26 | DVP_P1-2: LN 298_3_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 3314.9 | 3899.1 | 102.96 | 121.11 | DVP_P1-2: LN 568_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2598 | 2862.8 | 3142.2 | 110.19 | 120.95 | DVP_P2-2: SURRY B1_SRT-S | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 4146.8 | 4761.9 | 105.28 | 120.89 | DVP_P4-2: 9517T581_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3493 | 3885.7 | 108.5 | 120.69 | 315226 1N ANNA2 22.0_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1052 | 1353.6 | 1265.3 | 128.67 | 120.28 | DVP_P4-2: H1T574_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 1 | 230/500 | 345 | 1065 | 1282.5 | 1279.1 | 120.42 | 120.1 | DVP_P4-2: H2T557_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 3150.7 | 3415.4 | 110.78 | 120.09 | PN_P2-3_PN-500-001C-DRT_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3488.8 | 4076.7 | 102.56 | 119.84 | DVP_P1-2: LN 5007_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 3153.8 | 3408 | 110.89 | 119.83 | PL_10_P42_100569_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4010.5 | 4718.8 | 101.82 | 119.8 | DVP_P4-2: H2T568_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 3150.7 | 3404.6 | 110.78 | 119.71 | PL_10_P12_000086_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 3135.2 | 3386.9 | 110.24 | 119.09 | PL_10_P42_100572_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5569.2 | 5951.3 | 111.14 | 118.76 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3238.6 | 3821.6 | 100.59 | 118.7 | DVP_P1-2: LN 9518_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5389.4 | 5931.4 | 107.55 | 118.37 | DVP_P7-1: LN 2076-2145_4_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5403.8 | 5929.5 | 107.84 | 118.33 | DVP_P7-1: LN 2076-2145_2_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4332.6 | 4659.5 | 109.99 | 118.29 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5385 | 5926.4 | 107.46 | 118.27 | DVP_P7-1: LN 2076-2145_3_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3097 | 3636.7 | 3660.6 | 117.43 | 118.2 | AEP_P4_#7443_05DUMONT 765_A_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3097 | 3630.5 | 3657.9 | 117.23 | 118.11 | AEP_P4_#7442_05SORENS 765_K2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 2548.8 | 2879.7 | 104.37 | 117.92 | DVP_P1-2: LN 553_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3097 | 3623 | 3650.1 | 116.98 | 117.86 | AEP_P4_#7444_05DUMONT 765_A2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 314919 | 8OX | 1 | 500 | 345 | 3219.5 | 3201.7 | 3790.5 | 99.45 | 117.74 | DVP_P1-2: LN 568_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3491.6 | 3782.3 | 108.45 | 117.48 | DVP_P1-2: LN 552_SRT-S | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4330 | 4505.7 | 5081.7 | 104.06 | 117.36 | Base Case | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1057.5 | 1229.4 | 1229.4 | 116.25 | 116.25 | DVP_P1-2: LN 563_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4264.9 | 4577.1 | 108.27 | 116.2 | DVP_P7-1: LN 208-259_SRT-S | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 314919 | 8OX | 1 | 500 | 345 | 3219.5 | 3195.8 | 3734.5 | 99.26 | 116 | DVP_P1-2: LN 9533_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 6355 | 6403.9 | 115.06 | 115.95 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5205.7 | 5808.3 | 103.89 | 115.91 | DVP_P7-1: LN 2076-2145_1_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5205.8 | 5808.1 | 103.89 | 115.91 | DVP_P7-1: LN 2083-2145_1_SRT-S | Tower |  | No
N/A | See note 1 above | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1265 | 1464.3 | 1464.3 | 115.76 | 115.76 | DVP_P4-2: 562T563_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1265 | 1527 | 1459.9 | 120.71 | 115.41 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1265 | 1527 | 1459.9 | 120.71 | 115.41 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3085.3 | 3382.2 | 105.26 | 115.39 | DVP_P7-1: LN 211-228_SRT-S | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3114.5 | 3713.8 | 96.74 | 115.35 | DVP_P1-2: LN 9517_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3389 | 3922.4 | 99.62 | 115.3 | DVP_P1-2: LN 2101_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1079 | 1213.9 | 1243.9 | 112.5 | 115.28 | PL_48_P42_000439_SRT-A | Breaker | 933/1079/998/1143 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4842.6 | 4680.4 | 118.98 | 114.99 | DVP_P1-2: LN 585_3_SRT-A | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 2525.1 | 2807.4 | 103.4 | 114.96 | DVP_P1-2: LN 2154_2_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3083.1 | 3700.7 | 95.76 | 114.95 | DVP_P1-2: LN 550_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1057.5 | 1327.3 | 1213 | 125.51 | 114.7 | DVP_P1-2: LN 576_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1265 | 1450.7 | 1450.7 | 114.68 | 114.68 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4177.7 | 4514.7 | 106.06 | 114.62 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5174 | 5740.4 | 103.25 | 114.56 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4205.3 | 4511.3 | 106.76 | 114.53 | DVP_P7-1: LN 211-228_SRT-S | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4589 | 4661.4 | 112.75 | 114.53 | DVP_P1-4: 8CARSON_AE2-094 TAP_1_SRT-SW | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4294 | 4506.6 | 109.01 | 114.41 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4209.8 | 4495.7 | 106.88 | 114.13 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4070.2 | 4565.4 | 4640.2 | 112.17 | 114 | DVP_P1-2: LN 511_SRT-S | Single | 4295/4330/4996 : 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3053.7 | 3340.3 | 104.19 | 113.96 | DVP_P7-1: LN 177-2113_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3052.1 | 3338.5 | 104.13 | 113.9 | DVP_P7-1: LN 19-2154_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3035.2 | 3338.5 | 103.56 | 113.9 | DVP_P7-1: LN 2024-2102_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4160.7 | 4481.5 | 105.63 | 113.77 | DVP_P7-1: LN 2076-2145_4_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4157.5 | 4479.8 | 105.55 | 113.73 | DVP_P7-1: LN 2076-2145_3_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4169.8 | 4475.6 | 105.86 | 113.62 | DVP_P7-1: LN 2076-2145_2_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3022.7 | 3324.7 | 103.13 | 113.43 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5078.4 | 5680.5 | 101.34 | 113.36 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3028.6 | 3322 | 103.33 | 113.34 | DVP_P7-1: LN 169-2146_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5121.4 | 5679.5 | 102.2 | 113.34 | DVP_P2-2: GERMANNA_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4091.5 | 4462.9 | 103.87 | 113.3 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5092.4 | 5674.1 | 101.63 | 113.23 | AP_P2-2_PE-138-026_SRT-A | Bus |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 4146 | 4069.1 | 4693 | 98.14 | 113.19 | DVP_P7-1: LN 2101-569_SRT-A | Tower | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | No
N/A | See note 1 above | N/A | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4535.9 | 4599.3 | 111.44 | 113 | DVP_P1-2: LN 585_2_SRT-A | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3088.1 | 3632.8 | 95.92 | 112.84 | DVP_P1-2: LN 9534_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4086.2 | 4443.1 | 103.74 | 112.8 | DVP_P7-1: LN 2053-284_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4136 | 4441.8 | 105 | 112.76 | DVP_P2-2: BASIN B7_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4135.1 | 4440.9 | 104.98 | 112.74 | DVP_P7-1: LN 2065-259_SRT-S | Tower |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4138.9 | 4436.3 | 105.08 | 112.62 | DVP_P7-1: LN 249-69_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 247669 | 05JOSHUA 1EQ | 242515 | 05JOSHUA | 1 | 1.0/765 | 205 | 867 | 1135 | 975.1 | 130.91 | 112.47 | AEP_P4_#3174_05CLOVRD 765_AA2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3130.5 | 3620.2 | 97.24 | 112.45 | DVP_P1-2: LN 594_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3303.9 | 3817.5 | 97.12 | 112.22 | DVP_P1-2: LN 583_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4263.5 | 4411.5 | 108.24 | 112 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3117 | 3233.1 | 3484.5 | 103.72 | 111.79 | DVP_P2-2: MORRISVILLE B1_SRT-S | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2919.9 | 3178.4 | 102.67 | 111.76 | PN_P2-3_PN-500-DRT30_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2919.9 | 3178.4 | 102.67 | 111.76 | PN_P2-3_PN-500-004-DRT-009_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4012.1 | 4401.1 | 101.86 | 111.73 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4042.4 | 4400.7 | 102.62 | 111.72 | DVP_P2-2: BASIN B6_SRT-A | Bus |  | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 3796.5 | 4398.5 | 96.38 | 111.66 | DVP_P4-2: H1T568_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 3200.9 | 3457.8 | 103.29 | 111.58 | PEPCO_P4_PP41_SRT-A | Breaker | PEPCO: 2738/3099/3672: 3064/3567/4088 : 2738/3099/3672 DOM: 3803/3803/4373 : 4832/4832/5287 : 4668/4668/5141 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2979.7 | 3259.2 | 101.66 | 111.2 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 207973 | FRAC | 208072 | SIEG | 1 | 230 | 229 | 628 | 700 | 696.9 | 111.46 | 110.98 | PL_60_P71_000890_SRT-A | Tower | 513/628/564/682 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 200026 | HUNTERTN | 204501 | 27HUNTRSTN | 1 | 500/230 | 227 | 1169 | 1155 | 1296.5 | 98.8 | 110.9 | PJM_500_BG_P1_5013_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4020.3 | 4360.1 | 102.07 | 110.69 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 235105 | 01DOUBS | 200003 | BRIGHTON | 1 | 500 | 233/201 | 3099 | 3302.6 | 3429.4 | 106.57 | 110.66 | DVP_P4-2: H2T560_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235105 | 01DOUBS | 200003 | BRIGHTON | 1 | 500 | 233/201 | 3099 | 3302.6 | 3420.1 | 106.57 | 110.36 | DVP_P4-2: H1T560_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235105 | 01DOUBS | 200003 | BRIGHTON | 1 | 500 | 233/201 | 3099 | 3296 | 3418.9 | 106.36 | 110.32 | DVP_P1-2: LN 560_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 6026.2 | 6088 | 109.11 | 110.23 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3396 | 3380.6 | 3734.8 | 99.55 | 109.98 | Base Case | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 3742.8 | 4331.1 | 95.02 | 109.95 | DVP_P4-2: H2T568_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2930.6 | 3216.8 | 99.99 | 109.75 | DVP_P2-2: BASIN B7_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 6016.5 | 6060.4 | 108.94 | 109.73 | AEP_P4_#6189_05HANG R 765_D1_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | 4453 | 4394.2 | 4882 | 98.68 | 109.63 | AP_P7-1_PE-500-235098-003_SRT-SL | Tower |  | No
N/A | See note 1 above | N/A | 200026 | HUNTERTN | 204501 | 27HUNTRSTN | 1 | 500/230 | 227 | 1169 | 1142.9 | 1281.5 | 97.77 | 109.62 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235105 | 01DOUBS | 200003 | BRIGHTON | 1 | 500 | 233/201 | 3099 | 2791.2 | 3393.2 | 90.07 | 109.49 | PJM_500_BG_P1_5013_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 235105 | 01DOUBS | 200003 | BRIGHTON | 1 | 500 | 233/201 | 3099 | 2798.5 | 3392.9 | 90.3 | 109.48 | PJM_500_BG_P4_5_CNSTN_M_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2862.7 | 3111.9 | 100.66 | 109.42 | PN_P1-2_PN-500-001_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | 2078 | 2338.9 | 2269.9 | 112.55 | 109.23 | PN_P2-3_PN-500-DRT32_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | 2078 | 2338.9 | 2269.9 | 112.55 | 109.23 | PN_P2-3_PN-500-004-DRT-002_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4826.2 | 4985.3 | 105.58 | 109.06 | AEP_P4_#2942_05KAMMER 765_PP_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4086.4 | 4514.7 | 98.66 | 109 | AEP_P1-2_#17216_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200005 | CONEM-GH | 200009 | JUNI | 1 | 500 | 226/229 | 2844 | 2917.5 | 3097.8 | 102.58 | 108.92 | PN_P2-3_PN-500-004-DRT-008_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 200005 | CONEM-GH | 200009 | JUNI | 1 | 500 | 226/229 | 2844 | 2917.5 | 3097.8 | 102.58 | 108.92 | PN_P2-3_PN-500-DRT31_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 200005 | CONEM-GH | 200009 | JUNI | 1 | 500 | 226/229 | 2844 | 2922.3 | 3096.9 | 102.75 | 108.89 | PL_10_P42_100570_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4080.8 | 4508 | 98.52 | 108.84 | AEP_P4_#7217_05VASSEL 765_C1_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2876.6 | 3188.1 | 98.14 | 108.77 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus |  | No
N/A | See note 1 above | N/A | 243206 | 05DUMONT | 290606 | 05DUMONT_RS | Z1 | 765 | 205 | 5001 | 5427.3 | 5437.2 | 108.52 | 108.72 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | 4453 | 4355.3 | 4833.3 | 97.81 | 108.54 | AP_P7-1_PE-500-235098-002B_SRT-SL | Tower |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5935.3 | 5990.5 | 107.47 | 108.47 | AEP_P4_#709_05HANG R 765_D2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 200005 | CONEM-GH | 200009 | JUNI | 1 | 500 | 226/229 | 2844 | 2910.1 | 3084 | 102.33 | 108.44 | PL_10_P12_000085_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 3717.9 | 4264.6 | 94.39 | 108.27 | DVP_P4-2: 568T571_SRT-S | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3425 | 3408.6 | 3708 | 99.52 | 108.26 | Base Case | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 200005 | CONEM-GH | 200009 | JUNI | 1 | 500 | 226/229 | 2844 | 2895.9 | 3068.8 | 101.83 | 107.9 | PL_10_P42_103329_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 3180.1 | 3470.5 | 98.78 | 107.8 | DVP_P1-2: LN 581_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 6355 | 6422.9 | 106.56 | 107.69 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 3997.1 | 4444.8 | 96.5 | 107.31 | AEP_P4_#17219_05GUERNSEY 765_A_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5675.6 | 5924.8 | 102.76 | 107.27 | AEP_P4_#3139_05FLTLCK 765_B_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 3122.9 | 3449 | 97 | 107.13 | DVP_P1-2: LN 552_SRT-S | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 2944.6 | 3444.9 | 91.46 | 107 | DVP_P1-2: LN 9518_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 854.7 | 854.7 | 106.71 | 106.71 | PL_08_P42_102625_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 200018 | CHALK PT | 223983 | CHALK230 | 2 | 500/230 | 233 | 796 | 827.3 | 848.3 | 103.93 | 106.57 | PEPCO_P4_PP80_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4700.1 | 4864.6 | 102.82 | 106.42 | AEP_P4_#37_05MOUNTN 765_B1_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4700.3 | 4863.9 | 102.83 | 106.41 | AP_P2-3_MP-500-021_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 2 | 230 | 229 | 801 | 852.2 | 852.2 | 106.4 | 106.39 | PL_08_P42_102682_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4700.9 | 4862.8 | 102.84 | 106.38 | AP_P2-3_MP-500-020_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 3617.3 | 4186.7 | 91.83 | 106.29 | DVP_P7-1: LN 2-2199_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4373.3 | 4848.5 | 95.67 | 106.07 | 34506 34542_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 289543 | 05YEAT | 314919 | 8OX | 1 | 500 | 345 | 3219.5 | 2907.7 | 3411.8 | 90.32 | 105.97 | DVP_P1-2: LN 569_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314940 | 8ROGERS RD | 970672 | AG2-436 TP | 1 | 500 | 345 | 4070.2 | 4249 | 4311.4 | 104.39 | 105.93 | DVP_P1-2: LN 511_SRT-S | Single | 4295/4330/4996 : 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 847.4 | 847.6 | 105.79 | 105.82 | PL_08_P42_102623_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 847.4 | 847.6 | 105.79 | 105.82 | PL_08_P42_102075_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 3555.3 | 4166.9 | 90.26 | 105.78 | DVP_P7-1: LN 2039-2040_SRT-S | Tower |  | No
N/A | See note 1 above | N/A | 208109 | SUNB | 207970 | NESC230 | 1 | 230 | 229 | 624 | 675.1 | 659.9 | 108.2 | 105.75 | PL_08_P71_101751_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 235098 | WOODSIDE | 235105 | 01DOUBS | 1 | 500 | 201 | 4453 | 4245.6 | 4706.4 | 95.34 | 105.69 | AP_P2-3_PE-500-019J_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1107 | 1196.3 | 1169.8 | 108.06 | 105.68 | DVP_P4-2: 56702_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4257.6 | 4299.9 | 104.6 | 105.64 | DVP_P1-2: LN 585_SRT-A | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 935.3 | 1005.8 | 987.2 | 107.53 | 105.55 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 2 | 230 | 229 | 801 | 844.9 | 845.1 | 105.48 | 105.5 | PL_08_P42_102074_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5738.4 | 5819.6 | 103.9 | 105.37 | AEP_P7-1_#17567_SRT-SL | Tower |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5619.5 | 5811.1 | 101.75 | 105.22 | 34506 34542_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5701.9 | 5778.2 | 103.24 | 104.62 | AEP_P7-1_#17566_SRT-SL | Tower |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5686.9 | 5761.5 | 102.97 | 104.32 | AEP_P7-1_#16837_SRT-SL | Tower |  | No
N/A | See note 1 above | N/A | 314929 | 8FRONT ROYAL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3006.5 | 3352.5 | 93.38 | 104.13 | DVP_P1-2: LN 535_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2687.9 | 2956.9 | 94.51 | 103.97 | PN_P1-2_PN-500-010T_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200005 | CONEM-GH | 1 | 500 | 226 | 2771 | 2716.8 | 2877.9 | 98.04 | 103.86 | PN_P2-3_PN-500-004-DRT-008_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4093.8 | 4515 | 94.13 | 103.82 | AEP_P1-2_#17216_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2538 | 2358.9 | 2633.3 | 92.94 | 103.75 | Base Case | Single |  | No
N/A | See note 1 above | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 3999.8 | 4296.4 | 96.57 | 103.73 | AEP_P1-2_#7441_100545_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4088.2 | 4508.1 | 94 | 103.66 | AEP_P4_#7217_05VASSEL 765_C1_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208109 | SUNB | 207970 | NESC230 | 1 | 230 | 229 | 624 | 660.5 | 646.8 | 105.85 | 103.65 | PL_48_P71_101752_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 247669 | 05JOSHUA 1EQ | 242515 | 05JOSHUA | 1 | 1.0/765 | 205 | 867 | 1070.9 | 898.5 | 123.52 | 103.63 | AEP_P1-2_#3174_6_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 3987.2 | 4284.1 | 96.26 | 103.43 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 853.3 | 871.2 | 101.22 | 103.34 | PL:48:P42:000428 _SRT-A | Breaker | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5626.8 | 5697 | 101.88 | 103.15 | AEP_P7-1_#16838_SRT-SL | Tower |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 962.1 | 1064.3 | 93.05 | 102.93 | PL_48_P42_000438_SRT-A | Breaker | Same as base case | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 962.1 | 1064.3 | 93.05 | 102.93 | PL_48_P71_102649_SRT-A | Tower | Same as base case | No
N/A | See note 1 above | N/A | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 1107 | 1140.5 | 1139.2 | 103.02 | 102.91 | DVP_P4-2: H2T557_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4996 | 5299.8 | 5134.9 | 106.08 | 102.78 | DVP_P4-5: W72_SRT-A | Breaker | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4996 | 5299.4 | 5134.3 | 106.07 | 102.77 | DVP_P4-2: 58572_SRT-A | Breaker | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 235110 | 01MDWBRK | 289543 | 05YEAT | 1 | 500 | 201/345 | 3619 | 3346.8 | 3717.7 | 92.48 | 102.73 | DVP_P4-2: H1T541_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 6026.2 | 6114 | 101.04 | 102.52 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 841.6 | 864.1 | 99.83 | 102.5 | PL_40_P12_000182_SRT-A | Single | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4004.5 | 4444.8 | 92.08 | 102.2 | AEP_P4_#17219_05GUERNSEY 765_A_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314910 | 8CUNINGHAM | 314908 | 8ELMONT | 1 | 500 | 345 | 2857 | 2632.9 | 2919.1 | 92.16 | 102.17 | DVP_P4-2: H2T557_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4490 | 4668.2 | 98.23 | 102.13 | AEP_P4_#8089_05MARYSV 345_L1_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4996 | 5025.5 | 5101.3 | 100.59 | 102.11 | DVP_P4-2: 51192_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 816.6 | 816.7 | 101.94 | 101.96 | PL_08_P12_101739_SRT-A | Single | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 6016.5 | 6080.1 | 100.88 | 101.95 | AEP_P4_#6189_05HANG R 765_D1_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235105 | 01DOUBS | 200003 | BRIGHTON | 1 | 500 | 233/201 | 3099 | 3058.9 | 3158.1 | 98.71 | 101.91 | AP_P2-3_PE-500-237804-SB2_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 839.8 | 857.5 | 99.61 | 101.72 | PL_48_P12_102309_SRT-A | Single | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 835.4 | 857.4 | 99.1 | 101.71 | PL_48_P42_103276_SRT-A | Breaker | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 2 | 230 | 229 | 801 | 814.6 | 814.5 | 101.7 | 101.68 | PL_48_P42_101745_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 835.3 | 857.1 | 99.09 | 101.68 | PL_48_P42_001156_SRT-A | Breaker | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4996 | 5003.8 | 5079.1 | 100.16 | 101.66 | DVP_P4-2: 51172_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 208040 | MONT | 207915 | GLBR | 2 | 230 | 229 | 801 | 814.2 | 814.3 | 101.64 | 101.66 | PL_08_P12_101738_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 243206 | 05DUMONT | 290606 | 05DUMONT_RS | Z1 | 765 | 205 | 5001 | 5057.4 | 5082.1 | 101.13 | 101.62 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 3906.5 | 4197.8 | 94.31 | 101.35 | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200005 | CONEM-GH | 1 | 500 | 226 | 2844 | 2716.8 | 2877.9 | 95.53 | 101.19 | PN_P2-3_PN-500-DRT31_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 313483 | 8KRAKEN | 314922 | 8POSSUM | 1 | 500 | 345 | 3219.5 | 2987 | 3255.7 | 92.78 | 101.12 | DVP_P1-2: LN 594_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2611.8 | 2873.6 | 91.83 | 101.04 | PJM_500_BG_P1_5013_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 833.6 | 850.9 | 98.89 | 100.94 | PL_48_P42_103277_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 833.6 | 850.6 | 98.88 | 100.9 | PL_48_P42_102365_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 5935.3 | 6013.4 | 99.52 | 100.83 | AEP_P4_#709_05HANG R 765_D2_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 2892 | 3123 | 93.32 | 100.77 | AP_P1-2_PE-500-406T_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 5675.6 | 6006.3 | 95.16 | 100.71 | AEP_P4_#3139_05FLTLCK 765_B_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 823.4 | 848.5 | 97.68 | 100.65 | PL_48_P12_103307_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 829.4 | 847.5 | 98.38 | 100.53 | PL_48_P42_103275_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4996 | 4944.5 | 5020.3 | 98.97 | 100.49 | DVP_P4-2: 511T556_SRT-S | Breaker |  | No
N/A | See note 1 above | N/A | 313483 | 8KRAKEN | 314922 | 8POSSUM | 1 | 500 | 345 | 3219.5 | 2934.5 | 3232.2 | 91.15 | 100.39 | DVP_P1-2: LN 573_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | 2078 | 2157.8 | 2085.8 | 103.84 | 100.38 | PN_P2-2_PN-500-004B-DRT_SRT-SL | Bus |  | No
N/A | See note 1 above | N/A | 235118 | 01SOBEND | 200011 | KEYSTONE | 1 | 500 | 226/201 | 2078 | 2157.8 | 2085.7 | 103.84 | 100.37 | PN_P2-3_PN-500-DRT29_SRT-SL | Breaker |  | No
N/A | See note 1 above | N/A | 208013 | SUMT2_B4 | 208090 | SUMT | 2 | 230 | 229 | 801 | 799.2 | 803.2 | 99.77 | 100.28 | PL_02_P42_001053_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 200023 | WESC | 211321 | WESC | 3 | 500/138 | 229 | 502 | 507.1 | 502.6 | 101.03 | 100.13 | PL_20_P12_000092_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5460.8 | 5530.2 | 98.87 | 100.13 | AEP_P2-2_#16655_05GUNN RD SW 345_2_SRT-A | Bus |  | No
N/A | See note 1 above | N/A | 314913 | 8LOUDOUN | 314061 | 6LOUDOUN | 1 | 500/230 | 345 | 885.5 | 876.1 | 886.4 | 98.94 | 100.11 | DVP_P1-3: 8LOUDOUN-TX#2_SRT-A | Single |  | No