## Winter GenDeliv
Caused by deactivation generators
Interegional tie, will be handled throgh interregional process
2030 RTEP PJM Generator Deliverability Result (Winter)
FG # Status | FG Index | FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
N/A | 1 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 858.2 | 1410.8 | 1404.6 | 164.39 | 163.67 | DVP_P1-2: LN 588_SRT-A | Single | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 151 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1050 | 1405.8 | 1399.4 | 133.89 | 133.28 | DVP_P4-2: H2T588_SRT-A | Breaker | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 152 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1050 | 1405.8 | 1399.4 | 133.89 | 133.27 | DVP_P4-2: H5T588_SRT-A | Breaker | 721/721/829:913/913/1050:883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 157 | 2025W1-GD-W157 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 286 | 295.5 | 349.1 | 103.34 | 122.08 | ATSI_P2-4_OES-138-047_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 159 | 2025W1-GD-W159 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 260.1 | 263.3 | 118.25 | 119.66 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 370 | 2025-W1-GD-W370 | 272730 | WATERMAN ; R | 272445 | SANDWICH ; R | 1 | 138 | 222 | 376 | 443.3 | 443.1 | 117.89 | 117.85 | COMED_P7-1_138-L11106_B-R_+_345-L30003_B-R_SRT-A | Tower | 238/309/312/331/295/343/355/376 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 371 | 2025W1-GD-W371 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 257.7 | 259.1 | 117.15 | 117.78 | 34506 34542_SRT-A | Tower | 163/200/201/220 | Yes
Active | 18 | 2025W1-GD-W18 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 735.1 | 867.2 | 864.7 | 117.98 | 117.63 | DVP_P1-2: LN 563_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 161 | 2025W1-GD-W161 | 243469 | 05BEATTY | 241952 | 02DEERCREEK | 1 | 138 | 202/205 | 286 | 291.1 | 334.4 | 101.77 | 116.93 | ATSI_P2-4_OES-138-047_SRT-A | Breaker | ATSI: 200/242/226/286 (SN/SE/WN/WE) AEP: conductor owned by FirstEnergy | Yes |  | Overlap FE EOL candidate
N/A | 163 | N/A | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 2092 | 2427.1 | 2424.3 | 116.02 | 115.88 | AEP_P4_#2978_05DUMONT 765_B_SRT-A | Breaker | AEP: 1409/1887/1781/2144 | No |  | The most limiting rating is on NIPSCo side.
Active | 164 | 2025W1-GD-W164 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 253.7 | 254.9 | 115.3 | 115.85 | ATSI_P2-3_OES-138-024AT_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 19 | 2025W1-GD-W19 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 253.7 | 254.9 | 115.3 | 115.85 | ATSI_P1-2_OES-138-935TB_SRT-A | Single | 163/200/201/220 | Yes
Active | 21 | 2025W1-GD-W21 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 735.1 | 847.2 | 848.5 | 115.26 | 115.44 | DVP_P1-2: LN 217_SRT-W | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 22 | 2025W1-GD-W22 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 252.4 | 252.9 | 114.74 | 114.94 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | Single | 163/200/201/220 | Yes
Active | 375 | 2025W1-GD-W375 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 248.9 | 250.3 | 113.12 | 113.79 | ATSI_P7-1_OES-138-065T_SRT-A | Tower | 163/200/201/220 | Yes
Active | 166 | 2025W1-GD-W166 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 249.6 | 250.1 | 113.47 | 113.68 | DAY_GREENE_FB_GJ_I_SRT-A | Breaker | 163/200/201/220 | Yes
N/A | 23 | N/A | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 2092 | 2376 | 2374.2 | 113.58 | 113.49 | AEP_P1-2_#695_1681_SRT-A | Single | AEP: 1409/1887/1781/2144 | No |  | The most limiting rating is on NIPSCo side
N/A | 24 | N/A | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 2092 | 2372.3 | 2374.2 | 113.4 | 113.49 | 765-L11215__-S_SRT-A | Single | AEP: 1409/1887/1781/2144 | No |  | The most limiting rating is on NIPSCo side
N/A | 167 | N/A | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 2092 | 2371.6 | 2373.2 | 113.36 | 113.44 | COMED_P4_112-65-BT3-4___SRT-A | Breaker | AEP: 1409/1887/1781/2144 | No |  | The most limiting rating is on NIPSCo side
N/A | 168 | N/A | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 2092 | 2371.6 | 2373.2 | 113.36 | 113.44 | COMED_P4_112-65-BT4-5___SRT-A | Breaker | AEP: 1409/1887/1781/2144 | No |  | The most limiting rating is on NIPSCo side
Active | 169 | 2025W1-GD-W169 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 248.1 | 248.7 | 112.75 | 113.03 | DAY_GREENE_FB_GJ_H_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 377 | 2025W1-GD-W377 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 998.7 | 1003.1 | 111.71 | 112.21 | PL_48_P71_103285_SRT-A | Tower | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
Active | 170 | 2025-W1-GD-W170 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 306.3 | 317.9 | 107.49 | 111.55 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 322/449/407/504 | No | Substation Equipment Exclusion
N/A | 171 | N/A | 255113 | 17STILLWELL | 243219 | 05DUMONT | 1 | 345 | 205/217 | 2092 | 2322.2 | 2321.3 | 111 | 110.96 | AEP_P4_#1750_05DUMONT 765_B1_SRT-A | Breaker | AEP: 1409/1887/1781/2144 | No |  | The most limiting rating is on NIPSCo side
Active | 378 | 2025W1-GD-W378 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 991.5 | 991.7 | 110.91 | 110.93 | PL_48_P71_103285_SRT-A | Tower | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
Active | 175 | 2025W1-GD-W175 | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1512.3 | 1522.8 | 109.67 | 110.42 | COMED_P4_023-65-BT3-4___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 176 | 2025W1-GD-W176 | 270926 | WILTON ; B | 275232 | WILTON ;3M | 1 | 345 | 222 | 1379 | 1512.5 | 1522.8 | 109.68 | 110.42 | COMED_P4_023-65-BT3-4___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 27 | 2025W1-GD-W27 | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1512.3 | 1521.8 | 109.66 | 110.36 | 765-L11216__-S_SRT-A | Single | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 28 | 2025W1-GD-W28 | 270926 | WILTON ; B | 275232 | WILTON ;3M | 1 | 345 | 222 | 1379 | 1512.4 | 1521.8 | 109.68 | 110.36 | 765-L11216__-S_SRT-A | Single | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 177 | 2025W1-GD-W177 | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1511.4 | 1520.3 | 109.6 | 110.25 | COMED_P4_023-65-BT4-5___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 178 | 2025W1-GD-W178 | 270926 | WILTON ; B | 275232 | WILTON ;3M | 1 | 345 | 222 | 1379 | 1511.6 | 1520.3 | 109.62 | 110.25 | COMED_P4_023-65-BT4-5___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 185 | 2025W1-GD-W185 | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1493.5 | 1503 | 108.3 | 108.99 | COMED_P4_023-65-BT3-4___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 186 | 2025W1-GD-W186 | 270927 | WILTON ; R | 275233 | WILTON ;4M | 1 | 345 | 222 | 1379 | 1493.7 | 1503 | 108.32 | 108.99 | COMED_P4_023-65-BT3-4___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 38 | 2025W1-GD-W38 | 270927 | WILTON ; R | 275233 | WILTON ;4M | 1 | 345 | 222 | 1379 | 1493.6 | 1501.7 | 108.31 | 108.9 | 765-L11216__-S_SRT-A | Single | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 39 | 2025W1-GD-W39 | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1493.4 | 1501.7 | 108.3 | 108.9 | 765-L11216__-S_SRT-A | Single | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 188 | 2025W1-GD-W188 | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1492.6 | 1500.4 | 108.24 | 108.8 | COMED_P4_023-65-BT4-5___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 189 | 2025W1-GD-W189 | 270927 | WILTON ; R | 275233 | WILTON ;4M | 1 | 345 | 222 | 1379 | 1492.8 | 1500.4 | 108.25 | 108.8 | COMED_P4_023-65-BT4-5___SRT-A | Breaker | 1200/1379/1469/1601/1200/1379/1469/1601 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | Yes
Active | 193 | 2025W1-GD-W193 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 238.4 | 238.4 | 108.37 | 108.37 | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | Breaker | 163/200/201/220 | Yes
Active | 380 | 2025W1-GD-W380 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 232.5 | 237.6 | 105.67 | 108.02 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 163/200/201/220 | Yes
Active | 344 | 2025W1-GD-W344 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 232.3 | 236.8 | 105.6 | 107.66 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 163/200/201/220 | Yes
Active | 195 | 2025-W1-GD-W195 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 302.3 | 305.9 | 106.08 | 107.34 | AEP_P4_#2995_05E LIMA 345_M_SRT-A | Breaker | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 196 | 2025-W1-GD-W196 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 302 | 305.7 | 105.96 | 107.25 | AEP_P4_#6463_05E LIMA 345_M2_SRT-A | Breaker | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 41 | 2025-W1-GD-W41 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 302 | 305.7 | 105.96 | 107.25 | AEP_P1-2_#6463_16757_SRT-A | Single | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 197 | 2025-W1-GD-W197 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2475.6 | 2483.9 | 106.84 | 107.2 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
Active | 383 | 2025W1-GD-W383 | 243232 | 05SORENS | 243211 | 05ALLEN | 1 | 345 | 205 | 1138 | 1202.5 | 1214 | 105.67 | 106.68 | AEP_P7-1_#10901___SRT-A | Tower | 897/897/1138/1138 | Yes
N/A | 42 | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1263.4 | 1325.8 | 1342.8 | 104.94 | 106.29 | DVP_P1-2: LN 588_SRT-A | Single | 1133/1190/1323:1344/1344/1344: 1336/1338/1344 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 44 | 2025W1-GD-W44 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 233.8 | 232.5 | 106.25 | 105.66 | AEP_P1-2_#7441_100545_SRT-A | Single | 163/200/201/220 | Yes
Active | 201 | 2025-W1-GD-W201 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 296.8 | 300.1 | 104.14 | 105.3 | AEP_P4_#7363_05MADDOX 345_B1_SRT-A | Breaker | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 202 | 2025-W1-GD-W202 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 297.1 | 299.9 | 104.26 | 105.22 | AEP_P4_#6471_05MADDOX 345_B_SRT-A | Breaker | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 345 | 2025W1-GD-W345 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 230.7 | 231.1 | 104.86 | 105.06 | ATSI_P2-2_OES-138-054_SRT-A | Bus | 163/200/201/220 | Yes
N/A | 49 | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1263.4 | 1309.6 | 1326.5 | 103.66 | 104.99 | DVP_P1-2: LN 588_SRT-A | Single | 1122/1176/1302:1344/1344/1344:1324/1330/1344 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 50 | 2025-W1-GD-W50 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 335.7 | 359.1 | 97.87 | 104.71 | AP_P1-2_PE-138-035_SRT-A | Single | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 203 | 2025-W1-GD-W203 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 335.7 | 359.1 | 97.87 | 104.7 | AP_P2-3_PE-138-041_SRT-A | Breaker | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 346 | 2025-W1-GD-W346 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 335.7 | 359.1 | 97.87 | 104.7 | AP_P2-2_PE-138-009_SRT-A | Bus | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 384 | 2025-W1-GD-W384 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2449.6 | 2424.5 | 105.72 | 104.64 | DEOK_P7.1_4519BUFFCLIFTYPIERCEDEAR1OVEC_SRT-A | Tower | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
Active | 385 | 2025-W1-GD-W385 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2448.3 | 2424.2 | 105.67 | 104.63 | AEP_P7-1_#485___SRT-A | Tower | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
Active | 204 | 2025-W1-GD-W204 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 335.7 | 358.4 | 97.87 | 104.49 | AP_P2-3_PE-138-043_SRT-A | Breaker | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 51 | 2025-W1-GD-W51 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 291.8 | 297.7 | 102.39 | 104.44 | AEP_P1-2_#7441_100545_SRT-A | Single | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 52 | 2025-W1-GD-W52 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2413.2 | 2408.9 | 104.15 | 103.97 | AEP_P1-2_#7441_100545_SRT-A | Single | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
Active | 207 | 2025-W1-GD-W207 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2411.1 | 2406.4 | 104.06 | 103.86 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
Active | 208 | 2025-W1-GD-W208 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2410.9 | 2406.2 | 104.05 | 103.85 | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | Breaker | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
Active | 53 | 2025-W1-GD-W53 | 246950 | 05TIMBER SW | 246352 | 05HAVILAND2 | 1 | 138 | 205 | 285 | 293.1 | 295.2 | 102.84 | 103.58 | AEP_P1-2_#6457_16758_SRT-A | Single | 322/449/407/504 | No | Substation Equipment Exclusion
Active | 54 | 2025W1-GD-W54 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 228.5 | 227.5 | 103.86 | 103.43 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | Single | 163/200/201/220 | Yes
Active | 55 | 2025W1-GD-W55 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 228.5 | 227.4 | 103.86 | 103.37 | AEP_P1-2_#16635_SRT-A | Single | 163/200/201/220 | Yes
Active | 213 | 2025W1-GD-W213 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 272.6 | 293.4 | 95.3 | 102.6 | ATSI_P2-3_OES-138-065G_SRT-A | Breaker | 200/242/226/286 | Yes
Active | 61 | 2025-W1-GD-W61 | 272516 | STEWARD ; B | 271680 | HAUMESSER; B | 1 | 138 | 222 | 472 | 480.4 | 481.8 | 101.78 | 102.07 | COMED_P1-2_345-L15502_B-R_SRT-A | Single | 351/449/455/471/421/472/476/495 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 215 | 2025-W1-GD-W215 | 270889 | STATELINE; R | 272503 | STATELINE;4R | 1 | 345/138 | 222 | 361 | 363.3 | 367.6 | 100.63 | 101.84 | COMED_P4_177-45-BT9-10__SRT-A | Breaker | 308/361/361/415/308/361/361/415 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 216 | 2025-W1-GD-W216 | 246352 | 05HAVILAND2 | 243017 | 05HAVILAND1 | Z1 | 138 | 205 | 285 | 282.6 | 290 | 99.17 | 101.75 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | N/A | No | Substation Equipment Exclusion
Active | 217 | 2025-W1-GD-W217 | 272516 | STEWARD ; B | 271680 | HAUMESSER; B | 1 | 138 | 222 | 472 | 478.3 | 479.9 | 101.33 | 101.67 | COMED_P4_155-45-BT34-5__SRT-A | Breaker | 351/449/455/471/421/472/476/495 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 221 | 2025W1-GD-W221 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 285 | 266.1 | 288 | 93.38 | 101.05 | ATSI_P2-3_OES-138-065_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 222 | 2025W1-GD-W222 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 285 | 266.1 | 288 | 93.38 | 101.05 | ATSI_P2-3_OES-138-065B_SRT-A | Breaker | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
N/A | 225 | N/A | 255164 | 17NORTHPORT | 243241 | 05ALBION | 1 | 138 | 205/217 | 191 | 186.4 | 192.7 | 97.61 | 100.9 | AEP_P4_#10541_05CONCORD 138_A_SRT-A | Breaker | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 226 | 2025-W1-GD-W226 | 246352 | 05HAVILAND2 | 243017 | 05HAVILAND1 | Z1 | 138 | 205 | 285 | 280 | 287.4 | 98.23 | 100.83 | AEP_P4_#2995_05E LIMA 345_M_SRT-A | Breaker | N/A | No | Substation Equipment Exclusion
N/A | 349 | N/A | 255164 | 17NORTHPORT | 243241 | 05ALBION | 1 | 138 | 205/217 | 191 | 186.3 | 192.5 | 97.52 | 100.81 | AEP_P2-2_#8276_05CONCORD 138_1_SRT-A | Bus | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
N/A | 227 | N/A | 255164 | 17NORTHPORT | 243241 | 05ALBION | 1 | 138 | 205/217 | 191 | 186.3 | 192.5 | 97.52 | 100.81 | AEP_P4_#8276_05CONCORD 138_D_SRT-A | Breaker | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 228 | 2025-W1-GD-W228 | 246352 | 05HAVILAND2 | 243017 | 05HAVILAND1 | Z1 | 138 | 205 | 285 | 279.5 | 287.3 | 98.08 | 100.8 | AEP_P4_#6463_05E LIMA 345_M2_SRT-A | Breaker | N/A | No | Substation Equipment Exclusion
Active | 66 | 2025-W1-GD-W66 | 246352 | 05HAVILAND2 | 243017 | 05HAVILAND1 | Z1 | 138 | 205 | 285 | 279.5 | 287.3 | 98.08 | 100.8 | AEP_P1-2_#6463_16757_SRT-A | Single | N/A | No | Substation Equipment Exclusion
Active | 67 | 2025W1-GD-W67 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 272.6 | 287.2 | 95.3 | 100.4 | ATSI_P1-2_OES-138-002C_SRT-A | Single | 200/242/226/286 | Yes
Active | 231 | 2025-W1-GD-W231 | 270889 | STATELINE; R | 272503 | STATELINE;4R | 1 | 345/138 | 222 | 361 | 355.4 | 362.3 | 98.45 | 100.37 | COMED_P4_177-45-BT10-11_SRT-A | Breaker | 308/361/361/415/308/361/361/415 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 232 | 2025-W1-GD-W232 | 232117 | VIENNA 8 | 232127 | LORETTO | 1 | 138 | 235 | 289 | 289.1 | 289.9 | 100.04 | 100.32 | DPL_P4_2_DPIR235_SRT-A | Breaker | 315/409/388/484/375/471 (SN/SE/WN/WE/LLN/LLE) | No | Substation Equipment Exclusion
Active | 68 | 2025W1-GD-W68 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 735.1 | 735.7 | 736.8 | 100.08 | 100.23 | DVP_P1-2: LN 228_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Active | 233 | 2025-W1-GD-W233 | 243017 | 05HAVILAND1 | 242989 | 05E LIMA | 1 | 138 | 205 | 258 | 250.4 | 258.4 | 97.07 | 100.17 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 205/284/258/320 | No | Substation Equipment Exclusion
Active | 234 | 2025-W1-GD-W234 | 242933 | 05RPMONE | 246929 | 05MADDOX | 1 | 345 | 205 | 2237 | 2221.3 | 2240.7 | 99.3 | 100.17 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 1945/2802/2466/3122 | No | Substation Equipment Exclusion
Active | 69 | 2025-W1-GD-W69 | 243233 | 05TANNER | 249567 | 08M.FORT | 1 | 345 | 205/212 | 2317 | 2347.3 | 2319 | 101.31 | 100.09 | DEOK_P1_EAST BEND-TERMINAL 4516_SRT-A | Single | DEOK: 2403/2403/2604/2604 AEP: 2575/2575/2715/2715 | No | Substation Equipment Exclusion
N/A | 235 | N/A | 242865 | 05JEFRSO | 248000 | 06CLIFTY | 1 | 345 | 205/206 | 2991 | 2985.2 | 2991.4 | 99.81 | 100.01 | AEP_P4_#6189_05HANG R 765_D1_SRT-A | Breaker | 2354/2354/2992/2991 | No |  | Caused by deactivation generators

## Winter IPD
2030 RTEP PJM Individual Plant Deliverability Result (Winter)
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
Active | 2025W1-IPD-W1 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 286 | 366.1 | 109.63 | 127.99 | AD1-081 | ATSI_P2-4_OES-138-047_SRT-A | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-W2 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 258.2 | 115.88 | 117.36 | GM 55199 IA | AEP_P4_#7445_05MARYSV 765_B_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W3 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 257.9 | 116.62 | 117.23 | AE2-148 | 34506 34542_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W4 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 254.6 | 114.74 | 115.74 | GM 55199 IA | 34506 34542_SRT-A | 163/200/201/220 | Yes
N/A | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 858.2 | 941.5 | 110.99 | 109.7 | AF1-123 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 858.2 | 941.5 | 110.99 | 109.7 | AF1-124 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 858.2 | 941.5 | 110.99 | 109.7 | AF1-125 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
Active | 2025W1-IPD-W5 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 233.6 | 106.17 | 106.2 | GM 55199 IA | AEP_P4_#8075_05MARYSV 765_A2_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W6 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 228.5 | 104.33 | 103.87 | GM 55199 IA | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W7 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 227.7 | 103.95 | 103.5 | GM 55199 IA | AEP_P4_#7441_05SORENS 765_J1_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W8 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 227.7 | 103.95 | 103.5 | GM 55199 IA | AEP_P1-2_#7441_100545_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W9 | 243211 | 05ALLEN | 243232 | 05SORENS | 1 | 345 | 205 | 1138 | 1171.3 | 101.33 | 102.93 | GM 55199 IA | AEP_P7-1_#10901___SRT-A | 897/897/1138/1138 | Yes |  | This facility is listed in AEP's EOL facility list.
Active | 2025W1-IPD-W10 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 293.9 | 96.08 | 102.75 | AD2-163 | ATSI_P2-3_OES-138-065G_SRT-A | 200/242/226/286 | Yes
Active | 2025W1-IPD-W11 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 291.5 | 94.92 | 101.93 | AD1-140 | ATSI_P2-3_OES-138-065G_SRT-A | 200/242/226/286 | Yes
Active | 2025W1-IPD-W12 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 223.1 | 101.66 | 101.42 | GM 55199 IA | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W13 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 223 | 101.66 | 101.36 | GM 55199 IA | AEP_P1-2_#16635_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W14 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 223 | 101.66 | 101.36 | GM 55199 IA | DAY_MADISON_345KV_FB_JM_CC_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W15 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 222.9 | 101.57 | 101.32 | AE2-148 | AEP_P4_#8122_05BEATTY 345_302W_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W16 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 222.9 | 101.44 | 101.31 | AE2-148 | AEP_P4_#8121_05BEATTY 345_302C_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W17 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 222.8 | 101.58 | 101.26 | GM 55199 IA | DAY_MADISON_345KV_FB_JM_BB_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W18 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 285 | 288.4 | 94.14 | 101.19 | AD2-163 | ATSI_P2-3_OES-138-065_SRT-A | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-W19 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 285 | 288.4 | 94.14 | 101.19 | AD2-163 | ATSI_P2-3_OES-138-065B_SRT-A | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-W20 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 289.4 | 94.35 | 101.18 | AE2-305 | ATSI_P2-3_OES-138-065G_SRT-A | 200/242/226/286 | Yes
Active | 2025W1-IPD-W21 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 288.5 | 93.77 | 100.87 | AF1-053 | ATSI_P2-3_OES-138-065G_SRT-A | 200/242/226/286 | Yes
Active | 2025W1-IPD-W22 | 243211 | 05ALLEN | 243232 | 05SORENS | 1 | 345 | 205 | 1138 | 1147.6 | 99.78 | 100.85 | AF1-118 | AEP_P7-1_#10901___SRT-A | 897/897/1138/1138 | Yes |  | This facility is listed in AEP's EOL facility list.
Active | 2025W1-IPD-W23 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 221.5 | 100.91 | 100.67 | AE2-148 | AEP_P1-2_#18134_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W24 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 286 | 287.8 | 96.08 | 100.64 | AD2-163 | ATSI_P1-2_OES-138-002C_SRT-A | 200/242/226/286 | Yes
Active | 2025W1-IPD-W25 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 330 | 331.9 | 97.5 | 100.57 | AD1-140 | ATSI_P2-3_OES-138-060H_SRT-A | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
Active | 2025-W1-IPD-W26 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 344.9 | 94.06 | 100.56 | AG1-045 | AP_P1-2_PE-138-035_SRT-A | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025W1-IPD-W27 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 221.2 | 100.84 | 100.55 | AE2-148 | AEP_P4_#18234_05BIG PLAIN 345_CB1_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W28 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 221.2 | 100.79 | 100.55 | AE2-148 | AEP_P4_#18235_05BIG PLAIN 345_CB2_SRT-A | 163/200/201/220 | Yes
Active | 2025-W1-IPD-W29 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 344.9 | 94.06 | 100.55 | AG1-045 | AP_P2-2_PE-138-009_SRT-A | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025-W1-IPD-W30 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 344.9 | 94.06 | 100.55 | AG1-045 | AP_P2-3_PE-138-041_SRT-A | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025W1-IPD-W31 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 221.2 | 100.85 | 100.53 | AE2-148 | AEP_P4_#18236_05BIG PLAIN 345_CB3_SRT-A | 163/200/201/220 | Yes
Active | 2025W1-IPD-W32 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138 | 209 | 220 | 221.1 | 100.82 | 100.5 | AE2-148 | AEP_P1-2_#18232_SRT-A | 163/200/201/220 | Yes
Active | 2025-W1-IPD-W33 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 343 | 344.4 | 94.06 | 100.41 | AG1-045 | AP_P2-3_PE-138-043_SRT-A | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025W1-IPD-W34 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 285 | 286.1 | 93.01 | 100.4 | AD1-140 | ATSI_P2-3_OES-138-065_SRT-A | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-W35 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 285 | 286.1 | 93.01 | 100.4 | AD1-140 | ATSI_P2-3_OES-138-065B_SRT-A | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-IPD-W36 | 243211 | 05ALLEN | 243232 | 05SORENS | 1 | 345 | 205 | 1138 | 1140.5 | 98.99 | 100.22 | JOLIET 29;7U | AEP_P7-1_#10901___SRT-A | 897/897/1138/1138 | Yes |  | This facility is listed in AEP's EOL facility list.
Active | 2025W1-IPD-W37 | 243211 | 05ALLEN | 243232 | 05SORENS | 1 | 345 | 205 | 1138 | 1140.1 | 98.96 | 100.18 | JOLIET 29;8U | AEP_P7-1_#10901___SRT-A | 897/897/1138/1138 | Yes |  | This facility is listed in AEP's EOL facility list.
Active | 2025W1-IPD-W38 | 243211 | 05ALLEN | 243232 | 05SORENS | 1 | 345 | 205 | 1138 | 1139 | 98.87 | 100.08 | WILL CNTY;4U | AEP_P7-1_#10901___SRT-A | 897/897/1138/1138 | Yes |  | This facility is listed in AEP's EOL facility list.
Active | 2025W1-IPD-W39 | 243211 | 05ALLEN | 243232 | 05SORENS | 1 | 345 | 205 | 1138 | 1138 | 98.8 | 100 | AD1-100 | AEP_P7-1_#10901___SRT-A | 897/897/1138/1138 | Yes |  | This facility is listed in AEP's EOL facility list.