## Thermal
|  |  | Interegional tie, will be handled throgh interregional process | Potential interregional flowgate
PJM N-1-1 Thermal Result (Winter 2030 Case)
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2025W1-N11-WT1 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 131.4 | 129.01 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT2 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 131.17 | 128.83 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT3 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 131.24 | 124.37 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT4 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 131.4 | 123.96 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT5 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 226 | 286 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 122.15 | 121.96 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT6 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 122.15 | 121.83 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT7 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 121.29 | 121.51 | 160/192/180/228 | Yes
Active | 2025W1-N11-WT8 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 121.52 | 121.4 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT9 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 180 | 228 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 121.28 | 121.36 | 160/192/180/228 | Yes
Active | 2025W1-N11-WT10 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 121.51 | 121.3 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT11 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 226 | 286 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 121.23 | 120.93 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT12 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 226 | 286 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 121.18 | 120.63 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT13 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 119.25 | 118.47 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT14 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 226 | 286 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 118.69 | 118.44 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT15 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 119.25 | 118.41 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT16 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 226 | 286 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 118.69 | 118.35 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT17 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 226 | 286 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 117.77 | 117.59 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT18 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 226 | 286 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 117.75 | 117.2 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT19 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 115.69 | 114.98 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT20 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 226 | 286 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 115.61 | 114.84 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT21 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 226 | 286 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 115.61 | 114.78 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT22 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 114.52 | 114.02 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025-W1-N11-WT23 | 235457 | 01DTG | 235474 | 01GREENW | 1 | 138 | 201 | 315 | 401 | AP_P1-2_PE-138-056_SRT-A | Base Case | 112.68 | 112.68 | 278/339/315/401 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-N11-WT24 | 235502 | 01REDBUD | 235519 | 01W WINC | 1 | 138 | 201 | 250 | 317 | AP_P1-2_PE-138-035_SRT-A | Base Case | 111.49 | 111.49 | 221/268/250/317 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-2_#16595_SRT-A | AEP_P1-2_#8833_3300551_SRT-A | 125.41 | 111.18 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 2025W1-N11-WT25 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 301 | 330 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 111.18 | 111.06 | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-2_#2883_1708_SRT-A | AEP_P1-2_#8833_3300551_SRT-A | 116.55 | 110.27 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-2_#13805_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 115.35 | 108.77 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 2025W1-N11-WT26 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 301 | 330 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 111.16 | 108.19 | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
Active | 2025W1-N11-WT27 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 107.48 | 107.69 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-2_#5509_1730_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 118.1 | 107.68 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 2025W1-N11-WT28 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 107.48 | 107.62 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-2_#8833_3300551_SRT-A | AEP_P1-2_#16595_SRT-A | 125.42 | 107.4 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 2025W1-N11-WT29 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 180 | 228 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 108.12 | 107.2 | 160/192/180/228 | Yes
Active | 2025W1-N11-WT30 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 106.55 | 106.78 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT31 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 180 | 228 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 106.52 | 106.75 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT32 | 238703 | 02ESPRNG | 239278 | 02BRDVIE | 1 | 138 | 202 | 180 | 228 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 108.18 | 106.45 | 160/192/180/228 | Yes
Active | 2025W1-N11-WT33 | 210695 | GILB 2 | 211161 | SIEG | 2 | 138 | 229 | 222 | 283 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 106 | 106 | 192/251/222/283 | Yes
Active | 2025W1-N11-WT34 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 301 | 330 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 108.14 | 105.5 | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
Active | 2025W1-N11-WT35 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 115.73 | 105.2 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT36 | 210695 | GILB 2 | 211161 | SIEG | 2 | 138 | 229 | 222 | 283 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 105.19 | 105.19 | 192/251/222/283 | Yes
Active | 2025W1-N11-WT37 | 239278 | 02BRDVIE | 253085 | 09URBANA | 1 | 138 | 202/209 | 301 | 330 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 108.06 | 105.17 | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
Active | 2025W1-N11-WT38 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 263 | 330 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 108.47 | 105.09 | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-3_#7467_05ROB PK 345_5_SRT-A | AEP_P1-2_#5509_1730_SRT-A | 110.45 | 104.85 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 2025W1-N11-WT39 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 114.86 | 104.73 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT40 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 263 | 330 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 108.22 | 104.56 | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT41 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002C_SRT-A | Base Case | 122.9 | 104.48 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT42 | 210437 | BLMO | 211161 | SIEG | 1 | 138 | 229 | 222 | 283 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 103.52 | 103.52 | 192/251/222/283 | Yes
Active | 2025W1-N11-WT43 | 243485 | 05CLINTO | 243576 | 05ST.CLX | 1 | 138 | 205 | 139 | 178 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#10137_570_SRT-A | 104.03 | 103.42 | 142/180/139/184 | Yes
Active | 2025W1-N11-WT44 | 210437 | BLMO | 211161 | SIEG | 1 | 138 | 229 | 222 | 283 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 103.41 | 103.41 | 192/251/222/283 | Yes
Active | 2025W1-N11-WT45 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 136 | 178 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 105.78 | 103.29 | 131/173/136/178 | Yes
Active | 2025W1-N11-WT46 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 263 | 330 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | 103.12 | 103.12 | 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT47 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | ATSI_P1-2_OES-138-002D_SRT-A | Base Case | 120.69 | 103.04 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT48 | 243485 | 05CLINTO | 243576 | 05ST.CLX | 1 | 138 | 205 | 139 | 178 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#18125_SRT-A | 104.05 | 102.72 | 142/180/139/184 | Yes
Active | 2025W1-N11-WT49 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 136 | 178 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 105.9 | 102.63 | 131/173/136/178 | Yes
Active | 2025W1-N11-WT50 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 110.02 | 102.49 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT51 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 263 | 330 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 105.7 | 102.34 | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT52 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 226 | 286 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 109.51 | 101.96 | 200/242/226/286 | Yes
Active | 2025W1-N11-WT53 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138 | 205 | 136 | 178 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 104.67 | 101.78 | 131/173/136/178 | Yes
Active | 2025W1-N11-WT54 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 263 | 330 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 105.48 | 101.71 | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
N/A | N/A | 243241 | 05ALBION | 255164 | 17NORTHPORT | 1 | 138 | 205/217 | 188 | 191 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#5509_1730_SRT-A | 118.4 | 101.68 | AEP: 148/181/188/191 | No |  | The conductor is fully owned by NIPSCO and The most limiting rating is on NIPSCo side
Active | 2025-W1-N11-WT55 | 235445 | 01BEDNGT | 235546 | 01EAGLE | 1 | 138 | 201 | 148 | 148 | AP_P1-2_PE-138-020_SRT-A | AP_P1-2_PE-138-052_SRT-A | 101.6 | 101.59 | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025-W1-N11-WT56 | 235445 | 01BEDNGT | 235546 | 01EAGLE | 1 | 138 | 201 | 148 | 148 | AP_P1-2_PE-138-052_SRT-A | AP_P1-2_PE-138-020_SRT-A | 101.57 | 101.55 | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025W1-N11-WT57 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 109.07 | 101.51 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT58 | 210437 | BLMO | 210696 | GILB 1 | 1 | 138 | 229 | 222 | 283 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 101.51 | 101.51 | 192/251/222/283 | Yes
Active | 2025W1-N11-WT59 | 210437 | BLMO | 210696 | GILB 1 | 1 | 138 | 229 | 222 | 283 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 101.39 | 101.39 | 192/251/222/283 | Yes
Active | 2025W1-N11-WT60 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 226 | 285 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 108.53 | 100.98 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N11-WT61 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 263 | 330 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | 100.01 | 100.01 | 233/282/263/333 | Yes |  | Overlap FE EOL candidate

## Volt Mag
PJM N-1-1 Voltage Magnitude Result (Winter 2030 Case)
FG # Status | FG# | Bus # | Name | KV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | ContVolt | BaseVolt | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2025W1-N11-WVM207959 | 207959 | EPAL TR1 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.89317 | 1.0062 | Yes
Active | 2025W1-N11-WVM207959 | 207959 | EPAL TR1 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.89317 | 1.0062 | Yes
Active | 2025W1-N11-WVM207960 | 207960 | EPAL TR2 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.89298 | 1.0062 | Yes
Active | 2025W1-N11-WVM207960 | 207960 | EPAL TR2 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.89298 | 1.0062 | Yes
Active | 2025W1-N11-WVM207963 | 207963 | SLYK | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.83956 | 0.99305 | Yes
Active | 2025W1-N11-WVM207963 | 207963 | SLYK | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.83956 | 0.99305 | Yes
Active | 2025W1-N11-WVM207966 | 207966 | BWAY | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.83936 | 0.99288 | Yes
Active | 2025W1-N11-WVM207966 | 207966 | BWAY | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.83936 | 0.99288 | Yes
Active | 2025W1-N11-WVM207967 | 207967 | LOFT | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.83581 | 0.98939 | Yes
Active | 2025W1-N11-WVM207967 | 207967 | LOFT | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.83581 | 0.98939 | Yes
Active | 2025W1-N11-WVM207969 | 207969 | TRES | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.84076 | 0.99352 | Yes
Active | 2025W1-N11-WVM207969 | 207969 | TRES | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.84076 | 0.99352 | Yes
Active | 2025W1-N11-WVM208072 | 208072 | SIEG | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.9176 | 1.0058 | Yes
Active | 2025W1-N11-WVM208072 | 208072 | SIEG | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.9176 | 1.0058 | Yes
Active | 2025W1-N11-WVM210406 | 210406 | APPE TP | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90323 | 0.97821 | Yes
Active | 2025W1-N11-WVM210406 | 210406 | APPE TP | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.91316 | 0.97821 | Yes
Active | 2025W1-N11-WVM210406 | 210406 | APPE TP | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91058 | 0.99367 | Yes
Active | 2025W1-N11-WVM210406 | 210406 | APPE TP | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.91241 | 0.99632 | Yes
Active | 2025W1-N11-WVM210407 | 210407 | APPE | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90298 | 0.97799 | Yes
Active | 2025W1-N11-WVM210407 | 210407 | APPE | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.91292 | 0.97799 | Yes
Active | 2025W1-N11-WVM210407 | 210407 | APPE | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91033 | 0.99345 | Yes
Active | 2025W1-N11-WVM210407 | 210407 | APPE | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.91216 | 0.99611 | Yes
Active | 2025W1-N11-WVM210432 | 210432 | BART TP1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90227 | 0.97638 | Yes
Active | 2025W1-N11-WVM210432 | 210432 | BART TP1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90833 | 0.97638 | Yes
Active | 2025W1-N11-WVM210432 | 210432 | BART TP1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.90968 | 0.9962 | Yes
Active | 2025W1-N11-WVM210432 | 210432 | BART TP1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90752 | 0.99748 | Yes
Active | 2025W1-N11-WVM210433 | 210433 | BART 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90145 | 0.97568 | Yes
Active | 2025W1-N11-WVM210433 | 210433 | BART 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90752 | 0.97568 | Yes
Active | 2025W1-N11-WVM210433 | 210433 | BART 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.90887 | 0.99553 | Yes
Active | 2025W1-N11-WVM210433 | 210433 | BART 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.9067 | 0.99681 | Yes
Active | 2025W1-N11-WVM210434 | 210434 | BART TP2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90279 | 0.97682 | Yes
Active | 2025W1-N11-WVM210434 | 210434 | BART TP2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90885 | 0.97682 | Yes
Active | 2025W1-N11-WVM210434 | 210434 | BART TP2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.9102 | 0.99663 | Yes
Active | 2025W1-N11-WVM210434 | 210434 | BART TP2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90803 | 0.99791 | Yes
Active | 2025W1-N11-WVM210436 | 210436 | BART 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90274 | 0.97678 | Yes
Active | 2025W1-N11-WVM210436 | 210436 | BART 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.9088 | 0.97678 | Yes
Active | 2025W1-N11-WVM210436 | 210436 | BART 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91015 | 0.99659 | Yes
Active | 2025W1-N11-WVM210436 | 210436 | BART 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90798 | 0.99787 | Yes
Active | 2025W1-N11-WVM210596 | 210596 | EFMO TP1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90287 | 0.98409 | Yes
Active | 2025W1-N11-WVM210596 | 210596 | EFMO TP1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91023 | 0.99339 | Yes
Active | 2025W1-N11-WVM210597 | 210597 | EFMO | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90792 | 0.9822 | Yes
Active | 2025W1-N11-WVM210597 | 210597 | EFMO | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90712 | 0.99413 | Yes
Active | 2025W1-N11-WVM210599 | 210599 | EFMO TP2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90857 | 0.98275 | Yes
Active | 2025W1-N11-WVM210599 | 210599 | EFMO TP2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90777 | 0.99466 | Yes
Active | 2025W1-N11-WVM210600 | 210600 | EFMO DC | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90855 | 0.98273 | Yes
Active | 2025W1-N11-WVM210600 | 210600 | EFMO DC | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90775 | 0.99465 | Yes
Active | 2025W1-N11-WVM210693 | 210693 | GILB 1CB | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90288 | 0.98643 | Yes
Active | 2025W1-N11-WVM210693 | 210693 | GILB 1CB | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91023 | 0.9934 | Yes
Active | 2025W1-N11-WVM210694 | 210694 | GILB 2CB | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90858 | 0.98477 | Yes
Active | 2025W1-N11-WVM210694 | 210694 | GILB 2CB | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90778 | 0.99467 | Yes
Active | 2025W1-N11-WVM210748 | 210748 | JKSN | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.9037 | 0.977 | Yes
Active | 2025W1-N11-WVM210748 | 210748 | JKSN | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90968 | 0.977 | Yes
Active | 2025W1-N11-WVM210748 | 210748 | JKSN | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91104 | 0.99405 | Yes
Active | 2025W1-N11-WVM210748 | 210748 | JKSN | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90889 | 0.99553 | Yes
Active | 2025W1-N11-WVM210896 | 210896 | MCMI 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90892 | 0.97973 | Yes
Active | 2025W1-N11-WVM210896 | 210896 | MCMI 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.91291 | 0.97973 | Yes
Active | 2025W1-N11-WVM210896 | 210896 | MCMI 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90812 | 0.99493 | Yes
Active | 2025W1-N11-WVM210897 | 210897 | MCMI 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90282 | 0.9802 | Yes
Active | 2025W1-N11-WVM210897 | 210897 | MCMI 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.9188 | 0.9802 | Yes
Active | 2025W1-N11-WVM210897 | 210897 | MCMI 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91017 | 0.99334 | Yes
Active | 2025W1-N11-WVM210897 | 210897 | MCMI 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.9181 | 0.99764 | Yes
Active | 2025W1-N11-WVM210937 | 210937 | MONR | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90207 | 0.97689 | Yes
Active | 2025W1-N11-WVM210937 | 210937 | MONR | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.9082 | 0.97689 | Yes
Active | 2025W1-N11-WVM210937 | 210937 | MONR | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.90954 | 1.0047 | Yes
Active | 2025W1-N11-WVM210937 | 210937 | MONR | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90737 | 1.0056 | Yes
Active | 2025W1-N11-WVM210989 | 210989 | NSTR 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90294 | 0.97763 | Yes
Active | 2025W1-N11-WVM210989 | 210989 | NSTR 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90906 | 0.97763 | Yes
Active | 2025W1-N11-WVM210989 | 210989 | NSTR 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.9104 | 1.0007 | Yes
Active | 2025W1-N11-WVM210989 | 210989 | NSTR 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90822 | 1.0017 | Yes
Active | 2025W1-N11-WVM210990 | 210990 | NSTR 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90271 | 0.97743 | Yes
Active | 2025W1-N11-WVM210990 | 210990 | NSTR 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90883 | 0.97743 | Yes
Active | 2025W1-N11-WVM210990 | 210990 | NSTR 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91017 | 1.0005 | Yes
Active | 2025W1-N11-WVM210990 | 210990 | NSTR 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.908 | 1.0015 | Yes
Active | 2025W1-N11-WVM210991 | 210991 | NSTR CB1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90293 | 0.97762 | Yes
Active | 2025W1-N11-WVM210991 | 210991 | NSTR CB1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90905 | 0.97762 | Yes
Active | 2025W1-N11-WVM210991 | 210991 | NSTR CB1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91039 | 1.0007 | Yes
Active | 2025W1-N11-WVM210991 | 210991 | NSTR CB1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90821 | 1.0017 | Yes
Active | 2025W1-N11-WVM210992 | 210992 | NSTR CB2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.9027 | 0.97742 | Yes
Active | 2025W1-N11-WVM210992 | 210992 | NSTR CB2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90882 | 0.97742 | Yes
Active | 2025W1-N11-WVM210992 | 210992 | NSTR CB2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91017 | 1.0005 | Yes
Active | 2025W1-N11-WVM210992 | 210992 | NSTR CB2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90799 | 1.0015 | Yes
Active | 2025W1-N11-WVM211231 | 211231 | STRO 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90212 | 0.97693 | Yes
Active | 2025W1-N11-WVM211231 | 211231 | STRO 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90826 | 0.97693 | Yes
Active | 2025W1-N11-WVM211231 | 211231 | STRO 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.9096 | 1.0032 | Yes
Active | 2025W1-N11-WVM211231 | 211231 | STRO 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90742 | 1.0041 | Yes
Active | 2025W1-N11-WVM211232 | 211232 | STRO 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90201 | 0.97683 | Yes
Active | 2025W1-N11-WVM211232 | 211232 | STRO 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90814 | 0.97683 | Yes
Active | 2025W1-N11-WVM211232 | 211232 | STRO 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.90948 | 1.003 | Yes
Active | 2025W1-N11-WVM211232 | 211232 | STRO 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90731 | 1.004 | Yes
Active | 2025W1-N11-WVM211248 | 211248 | TANN 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90253 | 0.97639 | Yes
Active | 2025W1-N11-WVM211248 | 211248 | TANN 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90857 | 0.97639 | Yes
Active | 2025W1-N11-WVM211248 | 211248 | TANN 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.90992 | 0.99518 | Yes
Active | 2025W1-N11-WVM211248 | 211248 | TANN 1 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90776 | 0.99653 | Yes
Active | 2025W1-N11-WVM211249 | 211249 | TANN 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.90283 | 0.97663 | Yes
Active | 2025W1-N11-WVM211249 | 211249 | TANN 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.90887 | 0.97663 | Yes
Active | 2025W1-N11-WVM211249 | 211249 | TANN 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.91022 | 0.99543 | Yes
Active | 2025W1-N11-WVM211249 | 211249 | TANN 2 | 138 | 229 | 0.92 | 1.05 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.90806 | 0.99678 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77876 | 0.95329 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79241 | 0.95329 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85196 | 0.95329 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91856 | 0.95329 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91969 | 0.95329 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.83935 | 0.94489 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85391 | 0.94489 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.85557 | 0.94489 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.8719 | 0.94489 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91961 | 0.94489 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77875 | 0.9526 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.78386 | 0.9526 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79232 | 0.96035 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78284 | 0.95306 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91763 | 0.95606 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83927 | 0.96095 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81137 | 0.95263 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85548 | 0.95263 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.82012 | 0.95131 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87081 | 0.95131 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.81137 | 0.95357 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.82032 | 0.95357 | Yes
Active | 2025W1-N11-WVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85507 | 0.95357 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77652 | 0.95255 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79532 | 0.95255 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87099 | 0.95255 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77648 | 0.95629 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80341 | 0.95629 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7956 | 0.96576 | Yes
Active | 2025W1-N11-WVM238574 | 238574 | 02BELPT+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80244 | 0.96599 | Yes
Active | 2025W1-N11-WVM238605 | 238605 | 02CARDNT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89907 | 0.96975 | Yes
Active | 2025W1-N11-WVM238605 | 238605 | 02CARDNT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91081 | 0.96975 | Yes
Active | 2025W1-N11-WVM238605 | 238605 | 02CARDNT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89903 | 0.96949 | Yes
Active | 2025W1-N11-WVM238605 | 238605 | 02CARDNT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91192 | 0.96949 | Yes
Active | 2025W1-N11-WVM238605 | 238605 | 02CARDNT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91267 | 0.97418 | Yes
Active | 2025W1-N11-WVM238605 | 238605 | 02CARDNT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91048 | 0.96987 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78633 | 0.95826 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79996 | 0.95826 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85825 | 0.95826 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.85078 | 0.95096 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.86115 | 0.95096 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.86208 | 0.95096 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.87847 | 0.95096 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78633 | 0.95749 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79059 | 0.95749 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79985 | 0.96508 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78956 | 0.95752 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8507 | 0.96601 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81567 | 0.95729 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86199 | 0.95729 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.82478 | 0.95608 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87739 | 0.95608 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.81567 | 0.95798 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.82499 | 0.95798 | Yes
Active | 2025W1-N11-WVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86228 | 0.95798 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8434 | 0.97623 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.86172 | 0.97623 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91615 | 0.97623 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84335 | 0.97995 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8636 | 0.97995 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86303 | 0.98766 | Yes
Active | 2025W1-N11-WVM238640 | 238640 | 02CRISS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86214 | 0.98386 | Yes
Active | 2025W1-N11-WVM238667 | 238667 | 02DUALR+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85595 | 0.97711 | Yes
Active | 2025W1-N11-WVM238667 | 238667 | 02DUALR+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87287 | 0.97711 | Yes
Active | 2025W1-N11-WVM238667 | 238667 | 02DUALR+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8559 | 0.98061 | Yes
Active | 2025W1-N11-WVM238667 | 238667 | 02DUALR+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87427 | 0.98061 | Yes
Active | 2025W1-N11-WVM238667 | 238667 | 02DUALR+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87427 | 0.98778 | Yes
Active | 2025W1-N11-WVM238667 | 238667 | 02DUALR+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87276 | 0.98352 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75431 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.76825 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83228 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.898 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90085 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90449 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91103 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.91388 | 0.93724 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91932 | 0.95293 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.80338 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.83095 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.83339 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.84946 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.89678 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.90618 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90845 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91362 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91428 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91714 | 0.92536 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9194 | 0.94677 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9102 | 0.95504 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75431 | 0.93683 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.76294 | 0.93683 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90581 | 0.93683 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9137 | 0.93683 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91473 | 0.93683 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7682 | 0.94511 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76197 | 0.93908 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90799 | 0.93908 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89989 | 0.94118 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91353 | 0.94118 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91374 | 0.94118 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91769 | 0.94547 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91931 | 0.94648 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89686 | 0.94458 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91076 | 0.94458 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90628 | 0.94649 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91076 | 0.94649 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.80329 | 0.94478 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91289 | 0.94478 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.79705 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8333 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90514 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.906 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91305 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91466 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91478 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91758 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91907 | 0.93667 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91434 | 0.94456 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91504 | 0.94257 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91991 | 0.94257 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80442 | 0.93497 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84833 | 0.93497 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91129 | 0.93497 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91469 | 0.93497 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.79704 | 0.93934 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.8046 | 0.93934 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83222 | 0.93934 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90263 | 0.9445 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90604 | 0.9445 | Yes
Active | 2025W1-N11-WVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91479 | 0.9445 | Yes
Active | 2025W1-N11-WVM238745 | 238745 | 02GALION | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91066 | 0.98539 | Yes
Active | 2025W1-N11-WVM238745 | 238745 | 02GALION | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9106 | 0.98733 | Yes
Active | 2025W1-N11-WVM238745 | 238745 | 02GALION | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91918 | 0.98733 | Yes
Active | 2025W1-N11-WVM238745 | 238745 | 02GALION | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91754 | 0.98496 | Yes
Active | 2025W1-N11-WVM238746 | 238746 | 02GALION | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90833 | 0.97315 | Yes
Active | 2025W1-N11-WVM238746 | 238746 | 02GALION | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91873 | 0.97315 | Yes
Active | 2025W1-N11-WVM238746 | 238746 | 02GALION | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90829 | 0.97465 | Yes
Active | 2025W1-N11-WVM238746 | 238746 | 02GALION | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91932 | 0.97465 | Yes
Active | 2025W1-N11-WVM238746 | 238746 | 02GALION | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91791 | 0.97437 | Yes
Active | 2025W1-N11-WVM238777 | 238777 | 02HAMIL+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86109 | 0.97643 | Yes
Active | 2025W1-N11-WVM238777 | 238777 | 02HAMIL+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87738 | 0.97643 | Yes
Active | 2025W1-N11-WVM238777 | 238777 | 02HAMIL+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86104 | 0.97976 | Yes
Active | 2025W1-N11-WVM238777 | 238777 | 02HAMIL+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87859 | 0.97976 | Yes
Active | 2025W1-N11-WVM238777 | 238777 | 02HAMIL+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87884 | 0.98662 | Yes
Active | 2025W1-N11-WVM238777 | 238777 | 02HAMIL+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87709 | 0.98225 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82035 | 0.96827 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8409 | 0.96827 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90248 | 0.96827 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8203 | 0.97185 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84253 | 0.97185 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84175 | 0.97994 | Yes
Active | 2025W1-N11-WVM238861 | 238861 | 02KIRBY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8412 | 0.97765 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75308 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.76823 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83949 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89165 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9028 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90961 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91439 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.91463 | 0.9385 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91463 | 0.95623 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.78244 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.83285 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.83331 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.84774 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8916 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90545 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90835 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91074 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91125 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91296 | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.91999 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91789 | 0.9521 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91092 | 0.95721 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75308 | 0.9398 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.76898 | 0.9398 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89985 | 0.9398 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91591 | 0.9398 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91919 | 0.9398 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7683 | 0.94821 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76811 | 0.94502 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90502 | 0.94502 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90191 | 0.94538 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90848 | 0.94538 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91574 | 0.94538 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.79439 | 0.95456 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91272 | 0.95456 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.79439 | 0.9518 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90503 | 0.9518 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89354 | 0.94949 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90262 | 0.95143 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.78235 | 0.94611 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91547 | 0.94611 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91639 | 0.95661 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8306 | 0.94108 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83323 | 0.94108 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91022 | 0.94108 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91291 | 0.94108 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91561 | 0.94108 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91912 | 0.94108 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9179 | 0.95858 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9108 | 0.95101 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8354 | 0.94026 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84671 | 0.94026 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91464 | 0.94026 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91918 | 0.94026 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8306 | 0.94451 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83401 | 0.94451 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.83551 | 0.94451 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89765 | 0.9484 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91294 | 0.9484 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91925 | 0.9484 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91727 | 0.95254 | Yes
Active | 2025W1-N11-WVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91756 | 0.95323 | Yes
Active | 2025W1-N11-WVM238928 | 238928 | 02LTV+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85425 | 0.97733 | Yes
Active | 2025W1-N11-WVM238928 | 238928 | 02LTV+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87137 | 0.97733 | Yes
Active | 2025W1-N11-WVM238928 | 238928 | 02LTV+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85419 | 0.98088 | Yes
Active | 2025W1-N11-WVM238928 | 238928 | 02LTV+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87282 | 0.98088 | Yes
Active | 2025W1-N11-WVM238928 | 238928 | 02LTV+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87275 | 0.98816 | Yes
Active | 2025W1-N11-WVM238928 | 238928 | 02LTV+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87132 | 0.98392 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77632 | 0.95192 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79465 | 0.95192 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8691 | 0.95192 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77628 | 0.95528 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80148 | 0.95528 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79489 | 0.96455 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8005 | 0.96434 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91125 | 0.96616 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91332 | 0.96575 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91125 | 0.96817 | Yes
Active | 2025W1-N11-WVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91336 | 0.96817 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84641 | 0.97586 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.86433 | 0.97586 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91731 | 0.97586 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84635 | 0.97955 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86601 | 0.97955 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86567 | 0.98714 | Yes
Active | 2025W1-N11-WVM238969 | 238969 | 02MRGP + | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86452 | 0.98309 | Yes
Active | 2025W1-N11-WVM239073 | 239073 | 02ROBERT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85435 | 0.97734 | Yes
Active | 2025W1-N11-WVM239073 | 239073 | 02ROBERT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87146 | 0.97734 | Yes
Active | 2025W1-N11-WVM239073 | 239073 | 02ROBERT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85429 | 0.9809 | Yes
Active | 2025W1-N11-WVM239073 | 239073 | 02ROBERT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87291 | 0.9809 | Yes
Active | 2025W1-N11-WVM239073 | 239073 | 02ROBERT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87285 | 0.98818 | Yes
Active | 2025W1-N11-WVM239073 | 239073 | 02ROBERT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8714 | 0.98393 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77303 | 0.96028 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79325 | 0.96028 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8787 | 0.96028 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77299 | 0.96515 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80784 | 0.96515 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7934 | 0.97555 | Yes
Active | 2025W1-N11-WVM239133 | 239133 | 02TANGY | 345 | 202 | 0.95 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80707 | 0.9792 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77892 | 0.95519 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79831 | 0.95519 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87515 | 0.95519 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77888 | 0.95934 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80775 | 0.95934 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79863 | 0.96903 | Yes
Active | 2025W1-N11-WVM239134 | 239134 | 02TANGY | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80679 | 0.96968 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79025 | 0.95873 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80996 | 0.95873 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8826 | 0.95873 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79021 | 0.9627 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81723 | 0.9627 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81043 | 0.97195 | Yes
Active | 2025W1-N11-WVM239218 | 239218 | 02SSCIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81616 | 0.97182 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78794 | 0.95786 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80717 | 0.95786 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88079 | 0.95786 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7879 | 0.9619 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81551 | 0.9619 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80764 | 0.97128 | Yes
Active | 2025W1-N11-WVM239264 | 239264 | 02DBP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81447 | 0.97138 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78209 | 0.95342 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79638 | 0.95342 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85656 | 0.95342 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.85465 | 0.94808 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85589 | 0.94808 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.86494 | 0.94808 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.87892 | 0.94808 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78208 | 0.95269 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.78881 | 0.95269 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79627 | 0.96024 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78777 | 0.95389 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91919 | 0.95643 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85457 | 0.96158 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81125 | 0.95149 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86487 | 0.95149 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81935 | 0.9496 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87795 | 0.9496 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.81124 | 0.95337 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.81954 | 0.95337 | Yes
Active | 2025W1-N11-WVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85704 | 0.95337 | Yes
Active | 2025W1-N11-WVM239308 | 239308 | 02MR-ETH | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85525 | 0.97697 | Yes
Active | 2025W1-N11-WVM239308 | 239308 | 02MR-ETH | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87223 | 0.97697 | Yes
Active | 2025W1-N11-WVM239308 | 239308 | 02MR-ETH | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85519 | 0.98049 | Yes
Active | 2025W1-N11-WVM239308 | 239308 | 02MR-ETH | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87363 | 0.98049 | Yes
Active | 2025W1-N11-WVM239308 | 239308 | 02MR-ETH | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87363 | 0.9877 | Yes
Active | 2025W1-N11-WVM239308 | 239308 | 02MR-ETH | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87212 | 0.98343 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77348 | 0.95103 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79215 | 0.95103 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86885 | 0.95103 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77345 | 0.95492 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80105 | 0.95492 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79243 | 0.96439 | Yes
Active | 2025W1-N11-WVM240635 | 240635 | 02HARRIOT | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80009 | 0.96487 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7687 | 0.94763 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78652 | 0.94763 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86268 | 0.94763 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91719 | 0.94763 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91075 | 0.95378 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91318 | 0.95378 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91722 | 0.95378 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76868 | 0.95114 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.7945 | 0.95114 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78676 | 0.96031 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79356 | 0.96045 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9162 | 0.95869 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.90643 | 0.96955 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90643 | 0.96845 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90959 | 0.96147 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91071 | 0.96147 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91132 | 0.96116 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91676 | 0.96116 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90959 | 0.96436 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91136 | 0.96436 | Yes
Active | 2025W1-N11-WVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91367 | 0.96436 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75646 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77219 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84541 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89918 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90561 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9139 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.91701 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91804 | 0.93982 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.85086 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85172 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.86308 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89917 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90419 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91447 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91486 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91608 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9184 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91986 | 0.92733 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91325 | 0.95983 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75645 | 0.94189 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.77575 | 0.94189 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90735 | 0.94189 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91843 | 0.94189 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77231 | 0.95042 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77487 | 0.9486 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91446 | 0.9486 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90468 | 0.94783 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91618 | 0.94783 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91824 | 0.94783 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.82522 | 0.95759 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.82522 | 0.95531 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91457 | 0.95531 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90425 | 0.95313 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91238 | 0.95494 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85063 | 0.94514 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85079 | 0.94514 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91447 | 0.94514 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91995 | 0.94514 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91991 | 0.95474 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85449 | 0.94452 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86221 | 0.94452 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91827 | 0.94452 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.85063 | 0.94861 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85269 | 0.94861 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.85457 | 0.94861 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90689 | 0.95184 | Yes
Active | 2025W1-N11-WVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91997 | 0.95184 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91746 | 0.94221 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.74198 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.75598 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82145 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88606 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.89072 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#1274_589-2_SRT-A | 0.91947 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6497_SRT-A | 0.91953 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91965 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | 0.91966 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#728_584_SRT-A | 0.91992 | 0.92778 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91922 | 0.94761 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91981 | 0.94719 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91946 | 0.94352 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91975 | 0.94342 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91936 | 0.94364 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90827 | 0.94424 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.78581 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81888 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.82094 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.83714 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.88543 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8975 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9023 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.90335 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90577 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90656 | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.9143 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91913 | 0.94683 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9162 | 0.94092 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91977 | 0.94092 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90949 | 0.93793 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9194 | 0.93793 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89999 | 0.94618 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.74198 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.75204 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89415 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90394 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90504 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91039 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91789 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91865 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91972 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.91979 | 0.92773 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91878 | 0.93791 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91934 | 0.93791 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75596 | 0.93625 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91102 | 0.94739 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75111 | 0.93072 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89705 | 0.93072 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91536 | 0.93072 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91824 | 0.93072 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91858 | 0.93072 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91863 | 0.93072 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88974 | 0.93249 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90243 | 0.93249 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90376 | 0.93249 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91568 | 0.93249 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91943 | 0.93249 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91881 | 0.94374 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91881 | 0.94374 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91984 | 0.94644 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91938 | 0.94361 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91938 | 0.94361 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.7251 | 0.94204 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9063 | 0.94204 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.7251 | 0.93826 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89762 | 0.93826 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91747 | 0.93826 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91865 | 0.93826 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88552 | 0.93596 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.90306 | 0.93596 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91559 | 0.93596 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91748 | 0.93596 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89511 | 0.93796 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90307 | 0.93796 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91755 | 0.93796 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91961 | 0.93796 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.78572 | 0.9356 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90302 | 0.9356 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91066 | 0.9356 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91504 | 0.9356 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91565 | 0.9356 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91169 | 0.94606 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.78895 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82085 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89534 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.89603 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90318 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9135 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91576 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91755 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91837 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91898 | 0.9275 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91183 | 0.94751 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90341 | 0.93639 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91766 | 0.93639 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91983 | 0.93925 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90704 | 0.93446 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.9117 | 0.93446 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91574 | 0.93446 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.79575 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83598 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90129 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90445 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91045 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91081 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91187 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91732 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91892 | 0.92597 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.78894 | 0.93051 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.79592 | 0.93051 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82018 | 0.93051 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91098 | 0.93051 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91494 | 0.93051 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91679 | 0.93051 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89107 | 0.93561 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89607 | 0.93561 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90455 | 0.93561 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91471 | 0.93561 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91112 | 0.93963 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91449 | 0.93963 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91997 | 0.94453 | Yes
Active | 2025W1-N11-WVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91885 | 0.94386 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91734 | 0.94207 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.74184 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.75582 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82121 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88598 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.89056 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#1274_589-2_SRT-A | 0.91933 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6497_SRT-A | 0.91939 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91948 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | 0.91952 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#728_584_SRT-A | 0.91978 | 0.92765 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91907 | 0.94747 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91967 | 0.94706 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91933 | 0.94339 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91963 | 0.94328 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91922 | 0.9435 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90819 | 0.94409 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.78587 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8187 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.82079 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.83701 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.88533 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.89739 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90222 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.90325 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90569 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90648 | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.91422 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91899 | 0.94669 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91607 | 0.94078 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91962 | 0.94078 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90935 | 0.93778 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91926 | 0.93778 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89985 | 0.94604 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.74184 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.7518 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89407 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90378 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90489 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91769 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91851 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91956 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.91964 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91992 | 0.92757 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91854 | 0.93775 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9192 | 0.93775 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75579 | 0.93609 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91089 | 0.94726 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75088 | 0.93053 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89693 | 0.93053 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9152 | 0.93053 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91809 | 0.93053 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91835 | 0.93053 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91842 | 0.93053 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88958 | 0.93232 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90235 | 0.93232 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9036 | 0.93232 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91552 | 0.93232 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91922 | 0.93232 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91867 | 0.94361 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91867 | 0.94361 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9197 | 0.94631 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91925 | 0.94348 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91925 | 0.94348 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90746 | 0.93584 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91387 | 0.93584 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91757 | 0.93584 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91819 | 0.93584 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90915 | 0.93693 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91553 | 0.93693 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91883 | 0.93693 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91999 | 0.93693 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.72425 | 0.94189 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90621 | 0.94189 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.72425 | 0.93809 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89752 | 0.93809 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91728 | 0.93809 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91847 | 0.93809 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88542 | 0.93579 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.9028 | 0.93579 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91541 | 0.93579 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.9166 | 0.93579 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91733 | 0.93579 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91792 | 0.93579 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89501 | 0.93779 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9028 | 0.93779 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91735 | 0.93779 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91943 | 0.93779 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.78578 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90287 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91053 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91491 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91547 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91163 | 0.94593 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.78854 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8207 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89518 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.89588 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90303 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91333 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9156 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9174 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91818 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.9188 | 0.92736 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91175 | 0.94737 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90331 | 0.93619 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91747 | 0.93619 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91991 | 0.93964 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91965 | 0.93907 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9068 | 0.93426 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91147 | 0.93426 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91551 | 0.93426 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.79536 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83585 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90115 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90434 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91032 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91164 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91372 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91537 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91713 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91877 | 0.92582 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.78853 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.79554 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91084 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.9148 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91655 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91814 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.9199 | 0.93035 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89099 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89592 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90443 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91458 | 0.93546 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91103 | 0.93946 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91434 | 0.93946 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91982 | 0.94438 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91872 | 0.94373 | Yes
Active | 2025W1-N11-WVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91987 | 0.94406 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77138 | 0.95579 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78647 | 0.95579 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86216 | 0.95579 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91946 | 0.95579 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7714 | 0.9579 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.78987 | 0.9579 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78658 | 0.96538 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78907 | 0.96327 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91875 | 0.96283 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.87346 | 0.97214 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.87346 | 0.97039 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89072 | 0.96295 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89364 | 0.96261 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89072 | 0.96558 | Yes
Active | 2025W1-N11-WVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.89369 | 0.96558 | Yes
Active | 2025W1-N11-WVM241957 | 241957 | AC2-195 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8586 | 0.97683 | Yes
Active | 2025W1-N11-WVM241957 | 241957 | AC2-195 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87521 | 0.97683 | Yes
Active | 2025W1-N11-WVM241957 | 241957 | AC2-195 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85855 | 0.98024 | Yes
Active | 2025W1-N11-WVM241957 | 241957 | AC2-195 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87651 | 0.98024 | Yes
Active | 2025W1-N11-WVM241957 | 241957 | AC2-195 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87663 | 0.98726 | Yes
Active | 2025W1-N11-WVM241957 | 241957 | AC2-195 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.875 | 0.98294 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84031 | 0.97052 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85097 | 0.97052 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8877 | 0.97052 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91474 | 0.97027 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91829 | 0.97027 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83498 | 0.97055 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84031 | 0.97055 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85078 | 0.97599 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83404 | 0.96641 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91469 | 0.97874 | Yes
Active | 2025W1-N11-WVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91885 | 0.97194 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7818 | 0.95426 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79744 | 0.95426 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86288 | 0.95426 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.87856 | 0.95499 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.88419 | 0.95499 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88562 | 0.95499 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.89672 | 0.95499 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78178 | 0.95504 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79535 | 0.95504 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79745 | 0.96311 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79433 | 0.95932 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88414 | 0.96643 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.83493 | 0.9562 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88556 | 0.9562 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.84119 | 0.95493 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89595 | 0.95493 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.83493 | 0.95795 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.84131 | 0.95795 | Yes
Active | 2025W1-N11-WVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87946 | 0.95795 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.74714 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.76166 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8295 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88956 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.8966 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90681 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.90912 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91615 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9181 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91828 | 0.93311 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91208 | 0.95005 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.78573 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.82524 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.82664 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.84221 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88949 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90198 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90601 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.90757 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90926 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91037 | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.91788 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91492 | 0.94375 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90537 | 0.95165 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.74714 | 0.93358 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.75958 | 0.93358 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89771 | 0.93358 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90981 | 0.93358 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91111 | 0.93358 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91597 | 0.93358 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76167 | 0.9421 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91599 | 0.9527 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75868 | 0.93753 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90154 | 0.93753 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89566 | 0.93875 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90614 | 0.93875 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90963 | 0.93875 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91816 | 0.94517 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91964 | 0.94617 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.75038 | 0.94803 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91012 | 0.94803 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.75038 | 0.94461 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90179 | 0.94461 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88985 | 0.94221 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91216 | 0.94221 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89931 | 0.94426 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91216 | 0.94426 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.78563 | 0.94103 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90878 | 0.94103 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91593 | 0.94103 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9148 | 0.95122 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80324 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82656 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90167 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90244 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90893 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91105 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91522 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91805 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91943 | 0.93343 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91555 | 0.95298 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90763 | 0.94324 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9155 | 0.94149 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91963 | 0.94149 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80932 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8411 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90706 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.9101 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91573 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91637 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91982 | 0.9322 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.80324 | 0.93675 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.80948 | 0.93675 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82649 | 0.93675 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91655 | 0.93675 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89485 | 0.94152 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90248 | 0.94152 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91019 | 0.94152 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91491 | 0.94595 | Yes
Active | 2025W1-N11-WVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91596 | 0.94758 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91989 | 0.96 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.74264 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77302 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86204 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90235 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91257 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.91383 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.91822 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.91948 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.91972 | 0.93345 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91917 | 0.95983 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91998 | 0.95772 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91805 | 0.95902 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91159 | 0.95633 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91021 | 0.96572 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.74258 | 0.93911 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79505 | 0.93911 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91631 | 0.93911 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77324 | 0.96535 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91859 | 0.96317 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79474 | 0.96347 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9015 | 0.9546 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91627 | 0.9546 | Yes
Active | 2025W1-N11-WVM242926 | 242926 | 05MALIS | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91779 | 0.95959 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91968 | 0.95763 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91982 | 0.95726 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91959 | 0.95714 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91781 | 0.95632 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91813 | 0.95632 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9183 | 0.95704 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.73817 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86302 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87114 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90243 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.91036 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.91792 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91857 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18232_SRT-A | 0.91892 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | 0.91924 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91928 | 0.93047 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91583 | 0.95998 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91694 | 0.95618 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9176 | 0.95618 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91746 | 0.95646 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91837 | 0.95646 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91748 | 0.9546 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91914 | 0.9546 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91674 | 0.95474 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91907 | 0.95474 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91292 | 0.9525 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91639 | 0.9525 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91987 | 0.95869 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9162 | 0.95538 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91631 | 0.95538 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91018 | 0.95279 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91162 | 0.95279 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90689 | 0.96217 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.73808 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.78862 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8943 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90399 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91078 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#730_590_SRT-A | 0.91867 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.91868 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | 0.91903 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#16618_27957_SRT-A | 0.91956 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#10137_570_SRT-A | 0.91962 | 0.92721 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91007 | 0.95051 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91703 | 0.95051 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87096 | 0.95448 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89397 | 0.95448 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91557 | 0.96035 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91871 | 0.95651 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91988 | 0.95651 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91839 | 0.95689 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78815 | 0.96053 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90166 | 0.95118 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9039 | 0.95118 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9155 | 0.95568 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91874 | 0.95568 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91613 | 0.95572 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91665 | 0.95572 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91798 | 0.95709 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91904 | 0.95689 | Yes
Active | 2025W1-N11-WVM242928 | 242928 | 05MARYSV | 765 | 205 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91872 | 0.95679 | Yes
Active | 2025W1-N11-WVM242931 | 242931 | 05BEVERL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91843 | 1.0054 | Yes
Active | 2025W1-N11-WVM242931 | 242931 | 05BEVERL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91855 | 1.0086 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88555 | 0.97368 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91273 | 0.97368 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91484 | 0.97368 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87239 | 0.97387 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88544 | 0.97387 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91474 | 0.98008 | Yes
Active | 2025W1-N11-WVM242935 | 242935 | 05E LIMA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87041 | 0.96011 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7821 | 0.96166 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.83145 | 0.96166 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88187 | 0.96166 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78203 | 0.96344 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81068 | 0.96344 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8314 | 0.9755 | Yes
Active | 2025W1-N11-WVM242939 | 242939 | 05MARYSV | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80963 | 0.97836 | Yes
Active | 2025W1-N11-WVM242940 | 242940 | 05MUSKNG | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91207 | 1.0013 | Yes
Active | 2025W1-N11-WVM242940 | 242940 | 05MUSKNG | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9122 | 1.0045 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84062 | 0.98136 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85357 | 0.98136 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91904 | 0.98136 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84069 | 0.98562 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8665 | 0.98562 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85419 | 0.99159 | Yes
Active | 2025W1-N11-WVM242941 | 242941 | 05OHIOCT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8659 | 0.99063 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86461 | 0.96793 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89536 | 0.96793 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90284 | 0.96793 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85538 | 0.96838 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86452 | 0.96838 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89521 | 0.97509 | Yes
Active | 2025W1-N11-WVM242945 | 242945 | 05SW LIM | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85359 | 0.96033 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78775 | 0.96694 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80263 | 0.96694 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88838 | 0.96694 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78783 | 0.97337 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82263 | 0.97337 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80303 | 0.98394 | Yes
Active | 2025W1-N11-WVM242949 | 242949 | 05WMILLP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8223 | 0.9841 | Yes
Active | 2025W1-N11-WVM242979 | 242979 | 05CANNELV SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88158 | 0.99536 | Yes
Active | 2025W1-N11-WVM242979 | 242979 | 05CANNELV SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89436 | 0.99536 | Yes
Active | 2025W1-N11-WVM242979 | 242979 | 05CANNELV SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88171 | 0.99846 | Yes
Active | 2025W1-N11-WVM242979 | 242979 | 05CANNELV SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90524 | 0.99846 | Yes
Active | 2025W1-N11-WVM242979 | 242979 | 05CANNELV SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89498 | 1.0031 | Yes
Active | 2025W1-N11-WVM242979 | 242979 | 05CANNELV SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90493 | 1.0028 | Yes
Active | 2025W1-N11-WVM242986 | 242986 | 05CROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87387 | 0.99417 | Yes
Active | 2025W1-N11-WVM242986 | 242986 | 05CROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88732 | 0.99417 | Yes
Active | 2025W1-N11-WVM242986 | 242986 | 05CROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.874 | 0.99708 | Yes
Active | 2025W1-N11-WVM242986 | 242986 | 05CROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89831 | 0.99708 | Yes
Active | 2025W1-N11-WVM242986 | 242986 | 05CROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88786 | 1.0026 | Yes
Active | 2025W1-N11-WVM242986 | 242986 | 05CROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89795 | 1.0022 | Yes
Active | 2025W1-N11-WVM242989 | 242989 | 05E LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90946 | 0.98834 | Yes
Active | 2025W1-N11-WVM242989 | 242989 | 05E LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89629 | 0.98825 | Yes
Active | 2025W1-N11-WVM242989 | 242989 | 05E LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90935 | 0.98825 | Yes
Active | 2025W1-N11-WVM242989 | 242989 | 05E LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8943 | 0.97515 | Yes
Active | 2025W1-N11-WVM242991 | 242991 | 05E SIDE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90025 | 0.98477 | Yes
Active | 2025W1-N11-WVM242991 | 242991 | 05E SIDE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88378 | 0.98487 | Yes
Active | 2025W1-N11-WVM242991 | 242991 | 05E SIDE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90014 | 0.98487 | Yes
Active | 2025W1-N11-WVM242991 | 242991 | 05E SIDE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88176 | 0.97017 | Yes
Active | 2025W1-N11-WVM242995 | 242995 | 05EASTOW | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89419 | 0.98229 | Yes
Active | 2025W1-N11-WVM242995 | 242995 | 05EASTOW | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88093 | 0.98246 | Yes
Active | 2025W1-N11-WVM242995 | 242995 | 05EASTOW | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89408 | 0.98246 | Yes
Active | 2025W1-N11-WVM242995 | 242995 | 05EASTOW | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87889 | 0.96994 | Yes
Active | 2025W1-N11-WVM242998 | 242998 | 05EPOINT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88192 | 0.99714 | Yes
Active | 2025W1-N11-WVM242998 | 242998 | 05EPOINT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89458 | 0.99714 | Yes
Active | 2025W1-N11-WVM242998 | 242998 | 05EPOINT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88202 | 0.99973 | Yes
Active | 2025W1-N11-WVM242998 | 242998 | 05EPOINT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9057 | 0.99973 | Yes
Active | 2025W1-N11-WVM242998 | 242998 | 05EPOINT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89537 | 1.0029 | Yes
Active | 2025W1-N11-WVM242998 | 242998 | 05EPOINT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9053 | 1.0026 | Yes
Active | 2025W1-N11-WVM243001 | 243001 | 05EZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88491 | 0.99702 | Yes
Active | 2025W1-N11-WVM243001 | 243001 | 05EZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89748 | 0.99702 | Yes
Active | 2025W1-N11-WVM243001 | 243001 | 05EZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88503 | 0.99986 | Yes
Active | 2025W1-N11-WVM243001 | 243001 | 05EZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90845 | 0.99986 | Yes
Active | 2025W1-N11-WVM243001 | 243001 | 05EZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89823 | 1.0034 | Yes
Active | 2025W1-N11-WVM243001 | 243001 | 05EZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9081 | 1.0031 | Yes
Active | 2025W1-N11-WVM243007 | 243007 | 05FRAZEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87619 | 0.99818 | Yes
Active | 2025W1-N11-WVM243007 | 243007 | 05FRAZEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88934 | 0.99818 | Yes
Active | 2025W1-N11-WVM243007 | 243007 | 05FRAZEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87628 | 1.0003 | Yes
Active | 2025W1-N11-WVM243007 | 243007 | 05FRAZEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90152 | 1.0003 | Yes
Active | 2025W1-N11-WVM243007 | 243007 | 05FRAZEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89027 | 1.0036 | Yes
Active | 2025W1-N11-WVM243007 | 243007 | 05FRAZEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90097 | 1.0032 | Yes
Active | 2025W1-N11-WVM243016 | 243016 | 05HANTHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89844 | 0.98606 | Yes
Active | 2025W1-N11-WVM243016 | 243016 | 05HANTHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88371 | 0.98623 | Yes
Active | 2025W1-N11-WVM243016 | 243016 | 05HANTHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89833 | 0.98623 | Yes
Active | 2025W1-N11-WVM243016 | 243016 | 05HANTHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8817 | 0.9729 | Yes
Active | 2025W1-N11-WVM243018 | 243018 | 05HEATH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83898 | 0.98649 | Yes
Active | 2025W1-N11-WVM243018 | 243018 | 05HEATH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85313 | 0.98649 | Yes
Active | 2025W1-N11-WVM243018 | 243018 | 05HEATH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83906 | 0.99013 | Yes
Active | 2025W1-N11-WVM243018 | 243018 | 05HEATH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86969 | 0.99013 | Yes
Active | 2025W1-N11-WVM243018 | 243018 | 05HEATH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85388 | 0.99743 | Yes
Active | 2025W1-N11-WVM243018 | 243018 | 05HEATH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8691 | 0.99699 | Yes
Active | 2025W1-N11-WVM243023 | 243023 | 05HOCKNG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84374 | 0.98669 | Yes
Active | 2025W1-N11-WVM243023 | 243023 | 05HOCKNG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85799 | 0.98669 | Yes
Active | 2025W1-N11-WVM243023 | 243023 | 05HOCKNG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84388 | 0.99008 | Yes
Active | 2025W1-N11-WVM243023 | 243023 | 05HOCKNG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86888 | 0.99008 | Yes
Active | 2025W1-N11-WVM243023 | 243023 | 05HOCKNG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85817 | 0.99768 | Yes
Active | 2025W1-N11-WVM243023 | 243023 | 05HOCKNG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86852 | 0.997 | Yes
Active | 2025W1-N11-WVM243025 | 243025 | 05JUNCTN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85753 | 0.99252 | Yes
Active | 2025W1-N11-WVM243025 | 243025 | 05JUNCTN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87155 | 0.99252 | Yes
Active | 2025W1-N11-WVM243025 | 243025 | 05JUNCTN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85766 | 0.99647 | Yes
Active | 2025W1-N11-WVM243025 | 243025 | 05JUNCTN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88497 | 0.99647 | Yes
Active | 2025W1-N11-WVM243025 | 243025 | 05JUNCTN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87208 | 1.0028 | Yes
Active | 2025W1-N11-WVM243025 | 243025 | 05JUNCTN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88458 | 1.0023 | Yes
Active | 2025W1-N11-WVM243030 | 243030 | 05LIMAOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89553 | 0.9858 | Yes
Active | 2025W1-N11-WVM243030 | 243030 | 05LIMAOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88099 | 0.98606 | Yes
Active | 2025W1-N11-WVM243030 | 243030 | 05LIMAOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89542 | 0.98606 | Yes
Active | 2025W1-N11-WVM243030 | 243030 | 05LIMAOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87898 | 0.97313 | Yes
Active | 2025W1-N11-WVM243044 | 243044 | 05MILLWO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91386 | 1.0018 | Yes
Active | 2025W1-N11-WVM243044 | 243044 | 05MILLWO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9139 | 1.0032 | Yes
Active | 2025W1-N11-WVM243051 | 243051 | 05NDELPH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91462 | 0.98117 | Yes
Active | 2025W1-N11-WVM243051 | 243051 | 05NDELPH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89583 | 0.98082 | Yes
Active | 2025W1-N11-WVM243051 | 243051 | 05NDELPH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91453 | 0.98082 | Yes
Active | 2025W1-N11-WVM243051 | 243051 | 05NDELPH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89395 | 0.96311 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8048 | 0.97562 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81956 | 0.97562 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90439 | 0.97562 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80486 | 0.98021 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83746 | 0.98021 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82011 | 0.98901 | Yes
Active | 2025W1-N11-WVM243058 | 243058 | 05NEWARK CTR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83688 | 0.98882 | Yes
Active | 2025W1-N11-WVM243062 | 243062 | 05NMUSKG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91067 | 0.99286 | Yes
Active | 2025W1-N11-WVM243062 | 243062 | 05NMUSKG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91949 | 0.99286 | Yes
Active | 2025W1-N11-WVM243062 | 243062 | 05NMUSKG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9108 | 0.9965 | Yes
Active | 2025W1-N11-WVM243062 | 243062 | 05NMUSKG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91994 | 0.99865 | Yes
Active | 2025W1-N11-WVM243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87056 | 0.99099 | Yes
Active | 2025W1-N11-WVM243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88437 | 0.99099 | Yes
Active | 2025W1-N11-WVM243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87064 | 0.99312 | Yes
Active | 2025W1-N11-WVM243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8976 | 0.99312 | Yes
Active | 2025W1-N11-WVM243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88533 | 0.99843 | Yes
Active | 2025W1-N11-WVM243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89695 | 0.99785 | Yes
Active | 2025W1-N11-WVM243066 | 243066 | 05NW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89754 | 0.98377 | Yes
Active | 2025W1-N11-WVM243066 | 243066 | 05NW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88429 | 0.9839 | Yes
Active | 2025W1-N11-WVM243066 | 243066 | 05NW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89743 | 0.9839 | Yes
Active | 2025W1-N11-WVM243066 | 243066 | 05NW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88226 | 0.97123 | Yes
Active | 2025W1-N11-WVM243068 | 243068 | 05NZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88313 | 1.002 | Yes
Active | 2025W1-N11-WVM243068 | 243068 | 05NZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89609 | 1.002 | Yes
Active | 2025W1-N11-WVM243068 | 243068 | 05NZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88323 | 1.0046 | Yes
Active | 2025W1-N11-WVM243068 | 243068 | 05NZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90765 | 1.0046 | Yes
Active | 2025W1-N11-WVM243068 | 243068 | 05NZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89689 | 1.0079 | Yes
Active | 2025W1-N11-WVM243068 | 243068 | 05NZANEV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90723 | 1.0076 | Yes
Active | 2025W1-N11-WVM243070 | 243070 | 05OHIOCT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87943 | 1.0011 | Yes
Active | 2025W1-N11-WVM243070 | 243070 | 05OHIOCT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89225 | 1.0011 | Yes
Active | 2025W1-N11-WVM243070 | 243070 | 05OHIOCT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87952 | 1.0031 | Yes
Active | 2025W1-N11-WVM243070 | 243070 | 05OHIOCT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90367 | 1.0031 | Yes
Active | 2025W1-N11-WVM243070 | 243070 | 05OHIOCT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89314 | 1.0055 | Yes
Active | 2025W1-N11-WVM243070 | 243070 | 05OHIOCT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90316 | 1.0052 | Yes
Active | 2025W1-N11-WVM243074 | 243074 | 05PHILO1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8883 | 0.99661 | Yes
Active | 2025W1-N11-WVM243074 | 243074 | 05PHILO1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90054 | 0.99661 | Yes
Active | 2025W1-N11-WVM243074 | 243074 | 05PHILO1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88843 | 0.99975 | Yes
Active | 2025W1-N11-WVM243074 | 243074 | 05PHILO1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91107 | 0.99975 | Yes
Active | 2025W1-N11-WVM243074 | 243074 | 05PHILO1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90122 | 1.0036 | Yes
Active | 2025W1-N11-WVM243074 | 243074 | 05PHILO1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91079 | 1.0035 | Yes
Active | 2025W1-N11-WVM243075 | 243075 | 05POWELS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88147 | 1.0014 | Yes
Active | 2025W1-N11-WVM243075 | 243075 | 05POWELS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89437 | 1.0014 | Yes
Active | 2025W1-N11-WVM243075 | 243075 | 05POWELS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88157 | 1.0038 | Yes
Active | 2025W1-N11-WVM243075 | 243075 | 05POWELS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90589 | 1.0038 | Yes
Active | 2025W1-N11-WVM243075 | 243075 | 05POWELS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89521 | 1.0068 | Yes
Active | 2025W1-N11-WVM243075 | 243075 | 05POWELS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90543 | 1.0065 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82077 | 0.97577 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.83502 | 0.97577 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90937 | 0.97577 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82084 | 0.98018 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85108 | 0.98018 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8357 | 0.98678 | Yes
Active | 2025W1-N11-WVM243076 | 243076 | 05CONESPREPZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8505 | 0.98632 | Yes
Active | 2025W1-N11-WVM243079 | 243079 | 05REFORM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87329 | 0.99499 | Yes
Active | 2025W1-N11-WVM243079 | 243079 | 05REFORM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88672 | 0.99499 | Yes
Active | 2025W1-N11-WVM243079 | 243079 | 05REFORM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87337 | 0.99715 | Yes
Active | 2025W1-N11-WVM243079 | 243079 | 05REFORM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89944 | 0.99715 | Yes
Active | 2025W1-N11-WVM243079 | 243079 | 05REFORM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88766 | 1.0013 | Yes
Active | 2025W1-N11-WVM243079 | 243079 | 05REFORM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89885 | 1.0008 | Yes
Active | 2025W1-N11-WVM243080 | 243080 | 05RILEYC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91609 | 0.98412 | Yes
Active | 2025W1-N11-WVM243080 | 243080 | 05RILEYC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9143 | 0.97345 | Yes
Active | 2025W1-N11-WVM243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90295 | 0.9849 | Yes
Active | 2025W1-N11-WVM243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88958 | 0.98491 | Yes
Active | 2025W1-N11-WVM243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90284 | 0.98491 | Yes
Active | 2025W1-N11-WVM243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88756 | 0.97178 | Yes
Active | 2025W1-N11-WVM243083 | 243083 | 05CAMPSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91623 | 0.98669 | Yes
Active | 2025W1-N11-WVM243083 | 243083 | 05CAMPSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90401 | 0.98662 | Yes
Active | 2025W1-N11-WVM243083 | 243083 | 05CAMPSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91612 | 0.98662 | Yes
Active | 2025W1-N11-WVM243083 | 243083 | 05CAMPSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9021 | 0.97447 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80848 | 0.98361 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8236 | 0.98361 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90863 | 0.98361 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80856 | 0.98917 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84146 | 0.98917 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82402 | 0.99854 | Yes
Active | 2025W1-N11-WVM243089 | 243089 | 05SBALTM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84102 | 0.99845 | Yes
Active | 2025W1-N11-WVM243099 | 243099 | 05SHAWNR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89292 | 0.98573 | Yes
Active | 2025W1-N11-WVM243099 | 243099 | 05SHAWNR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87934 | 0.98603 | Yes
Active | 2025W1-N11-WVM243099 | 243099 | 05SHAWNR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89281 | 0.98603 | Yes
Active | 2025W1-N11-WVM243099 | 243099 | 05SHAWNR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87736 | 0.97412 | Yes
Active | 2025W1-N11-WVM243104 | 243104 | 05SLANCS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82914 | 0.9904 | Yes
Active | 2025W1-N11-WVM243104 | 243104 | 05SLANCS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84413 | 0.9904 | Yes
Active | 2025W1-N11-WVM243104 | 243104 | 05SLANCS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82926 | 0.99519 | Yes
Active | 2025W1-N11-WVM243104 | 243104 | 05SLANCS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85928 | 0.99519 | Yes
Active | 2025W1-N11-WVM243104 | 243104 | 05SLANCS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84455 | 1.0031 | Yes
Active | 2025W1-N11-WVM243104 | 243104 | 05SLANCS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85884 | 1.0027 | Yes
Active | 2025W1-N11-WVM243107 | 243107 | 05SPENCR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87411 | 0.99429 | Yes
Active | 2025W1-N11-WVM243107 | 243107 | 05SPENCR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88744 | 0.99429 | Yes
Active | 2025W1-N11-WVM243107 | 243107 | 05SPENCR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87425 | 0.99689 | Yes
Active | 2025W1-N11-WVM243107 | 243107 | 05SPENCR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89662 | 0.99689 | Yes
Active | 2025W1-N11-WVM243107 | 243107 | 05SPENCR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88776 | 1.0028 | Yes
Active | 2025W1-N11-WVM243107 | 243107 | 05SPENCR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89628 | 1.0022 | Yes
Active | 2025W1-N11-WVM243108 | 243108 | 05STRLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89752 | 0.98615 | Yes
Active | 2025W1-N11-WVM243108 | 243108 | 05STRLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8826 | 0.98636 | Yes
Active | 2025W1-N11-WVM243108 | 243108 | 05STRLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89741 | 0.98636 | Yes
Active | 2025W1-N11-WVM243108 | 243108 | 05STRLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88058 | 0.97301 | Yes
Active | 2025W1-N11-WVM243122 | 243122 | 05SW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89008 | 0.98637 | Yes
Active | 2025W1-N11-WVM243122 | 243122 | 05SW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87768 | 0.98672 | Yes
Active | 2025W1-N11-WVM243122 | 243122 | 05SW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88998 | 0.98672 | Yes
Active | 2025W1-N11-WVM243122 | 243122 | 05SW LIM | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87573 | 0.97595 | Yes
Active | 2025W1-N11-WVM243125 | 243125 | 05THAYER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90574 | 0.98731 | Yes
Active | 2025W1-N11-WVM243125 | 243125 | 05THAYER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89208 | 0.98729 | Yes
Active | 2025W1-N11-WVM243125 | 243125 | 05THAYER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90563 | 0.98729 | Yes
Active | 2025W1-N11-WVM243125 | 243125 | 05THAYER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89008 | 0.97411 | Yes
Active | 2025W1-N11-WVM243136 | 243136 | 05W LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89016 | 0.98143 | Yes
Active | 2025W1-N11-WVM243136 | 243136 | 05W LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91984 | 0.98143 | Yes
Active | 2025W1-N11-WVM243136 | 243136 | 05W LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87696 | 0.9817 | Yes
Active | 2025W1-N11-WVM243136 | 243136 | 05W LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89004 | 0.9817 | Yes
Active | 2025W1-N11-WVM243136 | 243136 | 05W LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91973 | 0.9874 | Yes
Active | 2025W1-N11-WVM243136 | 243136 | 05W LIMA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87492 | 0.96947 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79237 | 0.97563 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8076 | 0.97563 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89717 | 0.97563 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79244 | 0.9814 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82672 | 0.9814 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80804 | 0.99162 | Yes
Active | 2025W1-N11-WVM243146 | 243146 | 05WHEBRO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82625 | 0.99167 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82141 | 0.98903 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.83657 | 0.98903 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91762 | 0.98903 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82152 | 0.99394 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85191 | 0.99394 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83696 | 1.0022 | Yes
Active | 2025W1-N11-WVM243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85145 | 1.0018 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80325 | 0.98188 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81832 | 0.98188 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90517 | 0.98188 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80333 | 0.98776 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8374 | 0.98776 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81876 | 0.99765 | Yes
Active | 2025W1-N11-WVM243150 | 243150 | 05WMILLP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83697 | 0.99768 | Yes
Active | 2025W1-N11-WVM243152 | 243152 | 05W.MOULTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8918 | 0.98267 | Yes
Active | 2025W1-N11-WVM243152 | 243152 | 05W.MOULTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91899 | 0.98267 | Yes
Active | 2025W1-N11-WVM243152 | 243152 | 05W.MOULTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87903 | 0.98312 | Yes
Active | 2025W1-N11-WVM243152 | 243152 | 05W.MOULTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89171 | 0.98312 | Yes
Active | 2025W1-N11-WVM243152 | 243152 | 05W.MOULTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91879 | 0.988 | Yes
Active | 2025W1-N11-WVM243152 | 243152 | 05W.MOULTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87719 | 0.97528 | Yes
Active | 2025W1-N11-WVM243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91638 | 0.99423 | Yes
Active | 2025W1-N11-WVM243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91437 | 0.98443 | Yes
Active | 2025W1-N11-WVM243157 | 243157 | 05WOODLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89136 | 0.98175 | Yes
Active | 2025W1-N11-WVM243157 | 243157 | 05WOODLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87815 | 0.98199 | Yes
Active | 2025W1-N11-WVM243157 | 243157 | 05WOODLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89125 | 0.98199 | Yes
Active | 2025W1-N11-WVM243157 | 243157 | 05WOODLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87611 | 0.96968 | Yes
Active | 2025W1-N11-WVM243160 | 243160 | 05WTRNWY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88513 | 1.0012 | Yes
Active | 2025W1-N11-WVM243160 | 243160 | 05WTRNWY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89798 | 1.0012 | Yes
Active | 2025W1-N11-WVM243160 | 243160 | 05WTRNWY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88521 | 1.003 | Yes
Active | 2025W1-N11-WVM243160 | 243160 | 05WTRNWY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90855 | 1.003 | Yes
Active | 2025W1-N11-WVM243160 | 243160 | 05WTRNWY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89905 | 1.0054 | Yes
Active | 2025W1-N11-WVM243160 | 243160 | 05WTRNWY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90797 | 1.0049 | Yes
Active | 2025W1-N11-WVM243161 | 243161 | 05ZANESV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88715 | 1.004 | Yes
Active | 2025W1-N11-WVM243161 | 243161 | 05ZANESV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9002 | 1.004 | Yes
Active | 2025W1-N11-WVM243161 | 243161 | 05ZANESV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88726 | 1.007 | Yes
Active | 2025W1-N11-WVM243161 | 243161 | 05ZANESV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91182 | 1.007 | Yes
Active | 2025W1-N11-WVM243161 | 243161 | 05ZANESV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90093 | 1.011 | Yes
Active | 2025W1-N11-WVM243161 | 243161 | 05ZANESV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91145 | 1.0107 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79796 | 0.97193 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81042 | 0.97193 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88699 | 0.97193 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.798 | 0.97587 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81564 | 0.97587 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81053 | 0.9821 | Yes
Active | 2025W1-N11-WVM243453 | 243453 | 05BEATTY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81486 | 0.97936 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7972 | 0.97271 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81053 | 0.97271 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89108 | 0.97271 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79727 | 0.97727 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82128 | 0.97727 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81078 | 0.98503 | Yes
Active | 2025W1-N11-WVM243454 | 243454 | 05BIXBY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82067 | 0.98352 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81767 | 0.97962 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.83214 | 0.97962 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90861 | 0.97962 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81773 | 0.98473 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84874 | 0.98473 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83268 | 0.99295 | Yes
Active | 2025W1-N11-WVM243455 | 243455 | 05CONES | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84814 | 0.99262 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76457 | 0.9615 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78361 | 0.9615 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87825 | 0.9615 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76457 | 0.96791 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80536 | 0.96791 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78388 | 0.98293 | Yes
Active | 2025W1-N11-WVM243456 | 243456 | 05CORRID | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80487 | 0.9837 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7733 | 0.96369 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78892 | 0.96369 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87627 | 0.96369 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77331 | 0.96864 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80122 | 0.96864 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78907 | 0.97647 | Yes
Active | 2025W1-N11-WVM243457 | 243457 | 05HAYDEN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80049 | 0.97698 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76966 | 0.95993 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78855 | 0.95993 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87775 | 0.95993 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76964 | 0.96525 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80616 | 0.96525 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78871 | 0.97672 | Yes
Active | 2025W1-N11-WVM243458 | 243458 | 05HYATT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80548 | 0.97971 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77862 | 0.96617 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79395 | 0.96617 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88342 | 0.96617 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77867 | 0.97227 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81266 | 0.97227 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79428 | 0.98349 | Yes
Active | 2025W1-N11-WVM243459 | 243459 | 05KIRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8122 | 0.98341 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77219 | 0.96413 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78775 | 0.96413 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87603 | 0.96413 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7722 | 0.96914 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80028 | 0.96914 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78791 | 0.97652 | Yes
Active | 2025W1-N11-WVM243460 | 243460 | 05ROBRT2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79956 | 0.97713 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77278 | 0.96462 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78836 | 0.96462 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87658 | 0.96462 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77279 | 0.96963 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80089 | 0.96963 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78852 | 0.97702 | Yes
Active | 2025W1-N11-WVM243461 | 243461 | 05ROBRT1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80017 | 0.97762 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78395 | 0.9722 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7986 | 0.9722 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88755 | 0.9722 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78401 | 0.97762 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81366 | 0.97762 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79889 | 0.98601 | Yes
Active | 2025W1-N11-WVM243466 | 243466 | 05ASTOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81307 | 0.98593 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78334 | 0.97254 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79805 | 0.97254 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88794 | 0.97254 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7834 | 0.9781 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81398 | 0.9781 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79836 | 0.98696 | Yes
Active | 2025W1-N11-WVM243467 | 243467 | 05E.BROAD3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8134 | 0.98691 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79407 | 0.97678 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80781 | 0.97678 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88974 | 0.97678 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79411 | 0.98091 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81528 | 0.98091 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80795 | 0.98711 | Yes
Active | 2025W1-N11-WVM243469 | 243469 | 05BEATTY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81453 | 0.98556 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76806 | 0.96913 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78508 | 0.96913 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87835 | 0.96913 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76807 | 0.97455 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79942 | 0.97455 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78526 | 0.98248 | Yes
Active | 2025W1-N11-WVM243471 | 243471 | 05BETHEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79874 | 0.98351 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78859 | 0.98373 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8041 | 0.98373 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89366 | 0.98373 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78863 | 0.98913 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81801 | 0.98913 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80435 | 0.99477 | Yes
Active | 2025W1-N11-WVM243472 | 243472 | 05BEXLEY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81737 | 0.99613 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79315 | 0.97598 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80736 | 0.97598 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89212 | 0.97598 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79321 | 0.98089 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81954 | 0.98089 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80761 | 0.98789 | Yes
Active | 2025W1-N11-WVM243473 | 243473 | 05BIXBY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81892 | 0.98744 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77736 | 0.9782 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79371 | 0.9782 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89002 | 0.9782 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7774 | 0.98413 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81042 | 0.98413 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79398 | 0.99341 | Yes
Active | 2025W1-N11-WVM243474 | 243474 | 05BLACKL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80984 | 0.99437 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76985 | 0.97223 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78763 | 0.97223 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88377 | 0.97223 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76986 | 0.97832 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80589 | 0.97832 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78787 | 0.98924 | Yes
Active | 2025W1-N11-WVM243475 | 243475 | 05BLENDO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80532 | 0.99039 | Yes
Active | 2025W1-N11-WVM243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8876 | 0.99269 | Yes
Active | 2025W1-N11-WVM243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89976 | 0.99269 | Yes
Active | 2025W1-N11-WVM243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88776 | 0.99361 | Yes
Active | 2025W1-N11-WVM243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9019 | 0.99361 | Yes
Active | 2025W1-N11-WVM243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89914 | 0.99985 | Yes
Active | 2025W1-N11-WVM243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90164 | 0.99832 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77542 | 0.96459 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7931 | 0.96459 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8826 | 0.96459 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77543 | 0.97034 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80854 | 0.97034 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79335 | 0.9823 | Yes
Active | 2025W1-N11-WVM243478 | 243478 | 05BRKSHR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80785 | 0.98203 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76517 | 0.96531 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78271 | 0.96531 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87572 | 0.96531 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76517 | 0.97075 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.7976 | 0.97075 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78289 | 0.97986 | Yes
Active | 2025W1-N11-WVM243479 | 243479 | 05BROOKS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79694 | 0.98094 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78906 | 0.97941 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80359 | 0.97941 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89168 | 0.97941 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78912 | 0.98438 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81536 | 0.98438 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80381 | 0.9901 | Yes
Active | 2025W1-N11-WVM243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81469 | 0.9902 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78767 | 0.98088 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80229 | 0.98088 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89166 | 0.98088 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78772 | 0.98588 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8139 | 0.98588 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8025 | 0.99105 | Yes
Active | 2025W1-N11-WVM243481 | 243481 | 05CANAL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8132 | 0.99138 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78952 | 0.97155 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80673 | 0.97155 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89493 | 0.97155 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78953 | 0.97724 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82275 | 0.97724 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80705 | 0.98843 | Yes
Active | 2025W1-N11-WVM243482 | 243482 | 05CENTBG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82207 | 0.98807 | Yes
Active | 2025W1-N11-WVM243483 | 243483 | 05CRCLVS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83447 | 0.98619 | Yes
Active | 2025W1-N11-WVM243483 | 243483 | 05CRCLVS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83459 | 0.98886 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7847 | 0.98609 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8006 | 0.98609 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89398 | 0.98609 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78474 | 0.99146 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81388 | 0.99146 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8008 | 0.99509 | Yes
Active | 2025W1-N11-WVM243484 | 243484 | 05CITYCO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81319 | 0.99709 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77794 | 0.97907 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79433 | 0.97907 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88808 | 0.97907 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77796 | 0.98456 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80882 | 0.98456 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79454 | 0.9902 | Yes
Active | 2025W1-N11-WVM243485 | 243485 | 05CLINTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80815 | 0.99183 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78167 | 0.98251 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79748 | 0.98251 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89058 | 0.98251 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78169 | 0.98788 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81102 | 0.98788 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79767 | 0.99269 | Yes
Active | 2025W1-N11-WVM243486 | 243486 | 05CLINTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81032 | 0.99399 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77363 | 0.9758 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79015 | 0.9758 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88479 | 0.9758 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77365 | 0.98145 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80553 | 0.98145 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79036 | 0.98834 | Yes
Active | 2025W1-N11-WVM243487 | 243487 | 05CHK TAP Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80488 | 0.98987 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81451 | 0.97309 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.82895 | 0.97309 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90496 | 0.97309 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81458 | 0.97773 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84539 | 0.97773 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8296 | 0.98485 | Yes
Active | 2025W1-N11-WVM243488 | 243488 | 05CONESVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84481 | 0.9844 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76726 | 0.96886 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78565 | 0.96886 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88212 | 0.96886 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76726 | 0.97519 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8057 | 0.97519 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78591 | 0.98848 | Yes
Active | 2025W1-N11-WVM243491 | 243491 | 05CORRID | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80517 | 0.98935 | Yes
Active | 2025W1-N11-WVM243492 | 243492 | 05CORWIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91233 | 0.99282 | Yes
Active | 2025W1-N11-WVM243492 | 243492 | 05CORWIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91249 | 0.99281 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76915 | 0.96055 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78706 | 0.96055 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8765 | 0.96055 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76914 | 0.96627 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80209 | 0.96627 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78727 | 0.97854 | Yes
Active | 2025W1-N11-WVM243493 | 243493 | 05CRVERD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8014 | 0.97832 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77811 | 0.97966 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79392 | 0.97966 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88764 | 0.97966 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77814 | 0.98515 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80713 | 0.98515 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79413 | 0.98881 | Yes
Active | 2025W1-N11-WVM243494 | 243494 | 05CTYPLN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80645 | 0.99074 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76395 | 0.96454 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78074 | 0.96454 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87361 | 0.96454 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76396 | 0.96991 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.7946 | 0.96991 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78092 | 0.97762 | Yes
Active | 2025W1-N11-WVM243495 | 243495 | 05DAVIDS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79393 | 0.9786 | Yes
Active | 2025W1-N11-WVM243497 | 243497 | 05DELANO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87152 | 0.98479 | Yes
Active | 2025W1-N11-WVM243497 | 243497 | 05DELANO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88247 | 0.98479 | Yes
Active | 2025W1-N11-WVM243497 | 243497 | 05DELANO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87168 | 0.98631 | Yes
Active | 2025W1-N11-WVM243497 | 243497 | 05DELANO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88282 | 0.98631 | Yes
Active | 2025W1-N11-WVM243497 | 243497 | 05DELANO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88236 | 0.9923 | Yes
Active | 2025W1-N11-WVM243497 | 243497 | 05DELANO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88235 | 0.98892 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76567 | 0.95828 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78371 | 0.95828 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87297 | 0.95828 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76566 | 0.96398 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79845 | 0.96398 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7839 | 0.97643 | Yes
Active | 2025W1-N11-WVM243498 | 243498 | 05DLAWAR2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79776 | 0.97624 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76083 | 0.96059 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77782 | 0.96059 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8704 | 0.96059 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76083 | 0.96597 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79201 | 0.96597 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.778 | 0.97457 | Yes
Active | 2025W1-N11-WVM243499 | 243499 | 05DUBLIN CS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79134 | 0.97565 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7811 | 0.98177 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79718 | 0.98177 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89353 | 0.98177 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78114 | 0.98762 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8132 | 0.98762 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79746 | 0.99636 | Yes
Active | 2025W1-N11-WVM243502 | 243502 | 05E.BROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81261 | 0.9973 | Yes
Active | 2025W1-N11-WVM243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87913 | 0.98495 | Yes
Active | 2025W1-N11-WVM243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89152 | 0.98495 | Yes
Active | 2025W1-N11-WVM243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8793 | 0.98554 | Yes
Active | 2025W1-N11-WVM243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.895 | 0.98554 | Yes
Active | 2025W1-N11-WVM243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89132 | 0.99222 | Yes
Active | 2025W1-N11-WVM243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89483 | 0.9917 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78267 | 0.98264 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79852 | 0.98264 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89102 | 0.98264 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7827 | 0.9879 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81155 | 0.9879 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79871 | 0.99262 | Yes
Active | 2025W1-N11-WVM243507 | 243507 | 05FIFTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81085 | 0.99382 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78754 | 0.98852 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80347 | 0.98852 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89667 | 0.98852 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78757 | 0.99389 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81688 | 0.99389 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80367 | 0.99726 | Yes
Active | 2025W1-N11-WVM243508 | 243508 | 05ITALNV | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81619 | 0.99946 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77814 | 0.97167 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79312 | 0.97167 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88117 | 0.97167 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77817 | 0.97646 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80358 | 0.97646 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79329 | 0.98227 | Yes
Active | 2025W1-N11-WVM243509 | 243509 | 05FISHRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80285 | 0.98195 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77458 | 0.97513 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79145 | 0.97513 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88735 | 0.97513 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7746 | 0.98118 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80933 | 0.98118 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79173 | 0.99136 | Yes
Active | 2025W1-N11-WVM243510 | 243510 | 05GAHANN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80877 | 0.99234 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78767 | 0.9816 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80232 | 0.9816 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89196 | 0.9816 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78771 | 0.98661 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81394 | 0.98661 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80252 | 0.99169 | Yes
Active | 2025W1-N11-WVM243511 | 243511 | 05GAY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81325 | 0.99207 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76901 | 0.97149 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.786 | 0.97149 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88068 | 0.97149 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76902 | 0.97712 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8014 | 0.97712 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7862 | 0.98516 | Yes
Active | 2025W1-N11-WVM243512 | 243512 | 05DIAMONDISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80075 | 0.98656 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76517 | 0.96677 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78485 | 0.96677 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88033 | 0.96677 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76516 | 0.97281 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80378 | 0.97281 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78508 | 0.98666 | Yes
Active | 2025W1-N11-WVM243513 | 243513 | 05GENOA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80323 | 0.98737 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7592 | 0.95601 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77782 | 0.95601 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86984 | 0.95601 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75919 | 0.96148 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79407 | 0.96148 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77801 | 0.9728 | Yes
Active | 2025W1-N11-WVM243516 | 243516 | 05GREIF | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79344 | 0.97408 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79427 | 0.98014 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80895 | 0.98014 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89521 | 0.98014 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79432 | 0.98527 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82186 | 0.98527 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80921 | 0.99202 | Yes
Active | 2025W1-N11-WVM243518 | 243518 | 05GROVES1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82123 | 0.99212 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7815 | 0.97188 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79601 | 0.97188 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88225 | 0.97188 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78154 | 0.97645 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80545 | 0.97645 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79617 | 0.98241 | Yes
Active | 2025W1-N11-WVM243519 | 243519 | 05HALLRD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80472 | 0.98165 | Yes
Active | 2025W1-N11-WVM243522 | 243522 | 05HARRISON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81241 | 0.98564 | Yes
Active | 2025W1-N11-WVM243522 | 243522 | 05HARRISON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8125 | 0.9894 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77321 | 0.97558 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79052 | 0.97558 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88635 | 0.97558 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77323 | 0.98154 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80784 | 0.98154 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79077 | 0.99104 | Yes
Active | 2025W1-N11-WVM243523 | 243523 | 05HCREAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80725 | 0.99232 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78275 | 0.98308 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79861 | 0.98308 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89135 | 0.98308 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78278 | 0.98837 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81178 | 0.98837 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79881 | 0.99303 | Yes
Active | 2025W1-N11-WVM243524 | 243524 | 05HESS NORTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81108 | 0.9943 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76821 | 0.97073 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78529 | 0.97073 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87998 | 0.97073 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76822 | 0.97636 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8007 | 0.97636 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78549 | 0.98461 | Yes
Active | 2025W1-N11-WVM243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80005 | 0.98599 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7582 | 0.95315 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77732 | 0.95315 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86836 | 0.95315 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91901 | 0.95315 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75818 | 0.95856 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79379 | 0.95856 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7775 | 0.97076 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79316 | 0.97196 | Yes
Active | 2025W1-N11-WVM243526 | 243526 | 05HYATT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91807 | 0.9662 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76476 | 0.95804 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78301 | 0.95804 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87268 | 0.95804 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76475 | 0.96366 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79809 | 0.96366 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7832 | 0.97606 | Yes
Active | 2025W1-N11-WVM243527 | 243527 | 05HYATTX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79741 | 0.97611 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77334 | 0.97586 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78996 | 0.97586 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8852 | 0.97586 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77335 | 0.98164 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8061 | 0.98164 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79018 | 0.98921 | Yes
Active | 2025W1-N11-WVM243528 | 243528 | 05KARL ROAD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80546 | 0.99071 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77792 | 0.97834 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79432 | 0.97834 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88741 | 0.97834 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77794 | 0.98374 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80832 | 0.98374 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79452 | 0.98928 | Yes
Active | 2025W1-N11-WVM243529 | 243529 | 05KENNY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80764 | 0.99065 | Yes
Active | 2025W1-N11-WVM243531 | 243531 | 05KIMBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88563 | 0.99361 | Yes
Active | 2025W1-N11-WVM243531 | 243531 | 05KIMBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88533 | 0.9997 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78367 | 0.97539 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79911 | 0.97539 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89187 | 0.97539 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78372 | 0.98138 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81794 | 0.98138 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79947 | 0.99216 | Yes
Active | 2025W1-N11-WVM243532 | 243532 | 05KIRK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81742 | 0.99228 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76731 | 0.96933 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78438 | 0.96933 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87848 | 0.96933 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76732 | 0.97487 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79927 | 0.97487 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78457 | 0.98301 | Yes
Active | 2025W1-N11-WVM243535 | 243535 | 05LINWRT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79861 | 0.98422 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78928 | 0.97727 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80368 | 0.97727 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89077 | 0.97727 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78934 | 0.9822 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8155 | 0.9822 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80391 | 0.98841 | Yes
Active | 2025W1-N11-WVM243536 | 243536 | 05LS-II | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81485 | 0.98829 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7563 | 0.95303 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7779 | 0.95303 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87069 | 0.95303 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91924 | 0.95303 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75628 | 0.95873 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79698 | 0.95873 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77811 | 0.97496 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79645 | 0.97526 | Yes
Active | 2025W1-N11-WVM243537 | 243537 | 05MALIS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91832 | 0.96829 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75621 | 0.9529 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77787 | 0.9529 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87062 | 0.9529 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91912 | 0.9529 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75619 | 0.9586 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79694 | 0.9586 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77808 | 0.97489 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79642 | 0.97517 | Yes
Active | 2025W1-N11-WVM243538 | 243538 | 05MALISX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91819 | 0.96817 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78775 | 0.98033 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8023 | 0.98033 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89146 | 0.98033 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78781 | 0.98525 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81375 | 0.98525 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8025 | 0.99061 | Yes
Active | 2025W1-N11-WVM243539 | 243539 | 05MARION RD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81307 | 0.99085 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79572 | 0.98674 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81 | 0.98674 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89713 | 0.98674 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79577 | 0.99135 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81966 | 0.99135 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81017 | 0.9971 | Yes
Active | 2025W1-N11-WVM243540 | 243540 | 05MCCOMB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81893 | 0.99648 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77623 | 0.97864 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79322 | 0.97864 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88854 | 0.97864 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77625 | 0.98447 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80962 | 0.98447 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79346 | 0.99212 | Yes
Active | 2025W1-N11-WVM243542 | 243542 | 05MIFFLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.809 | 0.99384 | Yes
Active | 2025W1-N11-WVM243545 | 243545 | 05MILTON SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91382 | 0.99328 | Yes
Active | 2025W1-N11-WVM243545 | 243545 | 05MILTON SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91398 | 0.99325 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77314 | 0.97574 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79051 | 0.97574 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88632 | 0.97574 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77316 | 0.98169 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80776 | 0.98169 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79075 | 0.99109 | Yes
Active | 2025W1-N11-WVM243547 | 243547 | 05MORSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80716 | 0.99242 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78825 | 0.98226 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80303 | 0.98226 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89285 | 0.98226 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7883 | 0.98728 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81485 | 0.98728 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80323 | 0.99221 | Yes
Active | 2025W1-N11-WVM243548 | 243548 | 05MOUND ST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81417 | 0.99281 | Yes
Active | 2025W1-N11-WVM243549 | 243549 | 05MULBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8865 | 0.98478 | Yes
Active | 2025W1-N11-WVM243549 | 243549 | 05MULBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89643 | 0.98478 | Yes
Active | 2025W1-N11-WVM243549 | 243549 | 05MULBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88666 | 0.98578 | Yes
Active | 2025W1-N11-WVM243549 | 243549 | 05MULBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89498 | 0.98578 | Yes
Active | 2025W1-N11-WVM243549 | 243549 | 05MULBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89624 | 0.99122 | Yes
Active | 2025W1-N11-WVM243549 | 243549 | 05MULBRY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89455 | 0.98752 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8007 | 0.98267 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81463 | 0.98267 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89857 | 0.98267 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80077 | 0.98692 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82364 | 0.98692 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81478 | 0.99263 | Yes
Active | 2025W1-N11-WVM243550 | 243550 | 05OBETZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82298 | 0.9919 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7823 | 0.98271 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79821 | 0.98271 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89093 | 0.98271 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78233 | 0.988 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81137 | 0.988 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7984 | 0.99273 | Yes
Active | 2025W1-N11-WVM243551 | 243551 | 05OSU | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81066 | 0.99396 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80202 | 0.97711 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.817 | 0.97711 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90034 | 0.97711 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80211 | 0.98205 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83131 | 0.98205 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81734 | 0.98986 | Yes
Active | 2025W1-N11-WVM243552 | 243552 | 05PICKR8 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83078 | 0.98944 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75683 | 0.9555 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77778 | 0.9555 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87159 | 0.9555 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75681 | 0.96135 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79666 | 0.96135 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77799 | 0.97682 | Yes
Active | 2025W1-N11-WVM243553 | 243553 | 05POLARS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79613 | 0.97724 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77758 | 0.97599 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79381 | 0.97599 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88537 | 0.97599 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7776 | 0.98121 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80687 | 0.98121 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79399 | 0.98638 | Yes
Active | 2025W1-N11-WVM243560 | 243560 | 05ROBERT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80617 | 0.98723 | Yes
Active | 2025W1-N11-WVM243562 | 243562 | 05ROSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8789 | 0.98579 | Yes
Active | 2025W1-N11-WVM243562 | 243562 | 05ROSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8897 | 0.98579 | Yes
Active | 2025W1-N11-WVM243562 | 243562 | 05ROSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87906 | 0.98713 | Yes
Active | 2025W1-N11-WVM243562 | 243562 | 05ROSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88962 | 0.98713 | Yes
Active | 2025W1-N11-WVM243562 | 243562 | 05ROSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88954 | 0.99303 | Yes
Active | 2025W1-N11-WVM243562 | 243562 | 05ROSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88917 | 0.98961 | Yes
Active | 2025W1-N11-WVM243563 | 243563 | 05ROZELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90892 | 0.99385 | Yes
Active | 2025W1-N11-WVM243563 | 243563 | 05ROZELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91764 | 0.99385 | Yes
Active | 2025W1-N11-WVM243563 | 243563 | 05ROZELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90908 | 0.99445 | Yes
Active | 2025W1-N11-WVM243563 | 243563 | 05ROZELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91471 | 0.99445 | Yes
Active | 2025W1-N11-WVM243563 | 243563 | 05ROZELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91742 | 0.99916 | Yes
Active | 2025W1-N11-WVM243563 | 243563 | 05ROZELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91431 | 0.99524 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76327 | 0.96229 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78138 | 0.96229 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87404 | 0.96229 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76326 | 0.96775 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79687 | 0.96775 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78156 | 0.97808 | Yes
Active | 2025W1-N11-WVM243566 | 243566 | 05SAWMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79622 | 0.97922 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83738 | 0.981 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84958 | 0.981 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91675 | 0.981 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83751 | 0.98339 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85245 | 0.98339 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84959 | 0.98957 | Yes
Active | 2025W1-N11-WVM243568 | 243568 | 05SCIOTO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85191 | 0.98685 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83634 | 0.98281 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84864 | 0.98281 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91684 | 0.98281 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83647 | 0.9853 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85179 | 0.9853 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84866 | 0.99148 | Yes
Active | 2025W1-N11-WVM243569 | 243569 | 05SCIPPO | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85125 | 0.98885 | Yes
Active | 2025W1-N11-WVM243570 | 243570 | 05CLAYBN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87233 | 0.98482 | Yes
Active | 2025W1-N11-WVM243570 | 243570 | 05CLAYBN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88326 | 0.98482 | Yes
Active | 2025W1-N11-WVM243570 | 243570 | 05CLAYBN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87249 | 0.98632 | Yes
Active | 2025W1-N11-WVM243570 | 243570 | 05CLAYBN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88355 | 0.98632 | Yes
Active | 2025W1-N11-WVM243570 | 243570 | 05CLAYBN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88315 | 0.9923 | Yes
Active | 2025W1-N11-WVM243570 | 243570 | 05CLAYBN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88309 | 0.98892 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78964 | 0.9753 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80409 | 0.9753 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89071 | 0.9753 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7897 | 0.98043 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81737 | 0.98043 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80436 | 0.98775 | Yes
Active | 2025W1-N11-WVM243572 | 243572 | 05SHANON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81675 | 0.98758 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77922 | 0.96726 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79683 | 0.96726 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88623 | 0.96726 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77923 | 0.97301 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81243 | 0.97301 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7971 | 0.98483 | Yes
Active | 2025W1-N11-WVM243574 | 243574 | 05SUNBURY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81174 | 0.98454 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79015 | 0.99107 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80622 | 0.99107 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89947 | 0.99107 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79018 | 0.99649 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82005 | 0.99649 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80643 | 0.99903 | Yes
Active | 2025W1-N11-WVM243575 | 243575 | 05ST.CLR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81937 | 1.0019 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78469 | 0.98511 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80087 | 0.98511 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89437 | 0.98511 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78472 | 0.99056 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81519 | 0.99056 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80108 | 0.99465 | Yes
Active | 2025W1-N11-WVM243576 | 243576 | 05ST.CLX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81452 | 0.99699 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77402 | 0.97658 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79129 | 0.97658 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88696 | 0.97658 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77404 | 0.98249 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80829 | 0.98249 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79152 | 0.99141 | Yes
Active | 2025W1-N11-WVM243577 | 243577 | 05STELZR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80769 | 0.99284 | Yes
Active | 2025W1-N11-WVM243579 | 243579 | 05STROUD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87492 | 0.99302 | Yes
Active | 2025W1-N11-WVM243579 | 243579 | 05STROUD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88801 | 0.99302 | Yes
Active | 2025W1-N11-WVM243579 | 243579 | 05STROUD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87508 | 0.99466 | Yes
Active | 2025W1-N11-WVM243579 | 243579 | 05STROUD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89344 | 0.99466 | Yes
Active | 2025W1-N11-WVM243579 | 243579 | 05STROUD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88791 | 1.0014 | Yes
Active | 2025W1-N11-WVM243579 | 243579 | 05STROUD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89317 | 1.0005 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78851 | 0.98218 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80315 | 0.98218 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89256 | 0.98218 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78855 | 0.98715 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81458 | 0.98715 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80334 | 0.99231 | Yes
Active | 2025W1-N11-WVM243580 | 243580 | 05SULVNT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81388 | 0.99259 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77934 | 0.97735 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79517 | 0.97735 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89054 | 0.97735 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77938 | 0.98327 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81224 | 0.98327 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79548 | 0.99278 | Yes
Active | 2025W1-N11-WVM243581 | 243581 | 05TAYLOR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81168 | 0.99343 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77555 | 0.97228 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7911 | 0.97228 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88114 | 0.97228 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77557 | 0.9773 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80279 | 0.9773 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79127 | 0.98291 | Yes
Active | 2025W1-N11-WVM243582 | 243582 | 05TRABUE1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80207 | 0.98315 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78313 | 0.97 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80066 | 0.97 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88993 | 0.97 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78313 | 0.97575 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81641 | 0.97575 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80095 | 0.98743 | Yes
Active | 2025W1-N11-WVM243583 | 243583 | 05TRENT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81572 | 0.98712 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78682 | 0.98779 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80271 | 0.98779 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89588 | 0.98779 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78685 | 0.99314 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81599 | 0.99314 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80292 | 0.99676 | Yes
Active | 2025W1-N11-WVM243584 | 243584 | 05VINE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8153 | 0.99876 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79295 | 0.97425 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80662 | 0.97425 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88925 | 0.97425 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79299 | 0.97852 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81479 | 0.97852 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80678 | 0.98492 | Yes
Active | 2025W1-N11-WVM243586 | 243586 | 05WHITER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81405 | 0.9834 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78046 | 0.97763 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79597 | 0.97763 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88668 | 0.97763 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78049 | 0.98269 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80804 | 0.98269 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79615 | 0.98784 | Yes
Active | 2025W1-N11-WVM243588 | 243588 | 05WILSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80732 | 0.9884 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76196 | 0.96258 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78208 | 0.96258 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.877 | 0.96258 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76195 | 0.96856 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80099 | 0.96856 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78231 | 0.98298 | Yes
Active | 2025W1-N11-WVM243590 | 243590 | 05WESTAR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80044 | 0.98359 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76759 | 0.96969 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78634 | 0.96969 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.882 | 0.96969 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7676 | 0.97569 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80453 | 0.97569 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78657 | 0.98775 | Yes
Active | 2025W1-N11-WVM243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80396 | 0.9887 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78656 | 0.98297 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8022 | 0.98297 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89327 | 0.98297 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7866 | 0.98848 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81657 | 0.98848 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80245 | 0.99479 | Yes
Active | 2025W1-N11-WVM243592 | 243592 | 05YEARLG | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81595 | 0.99606 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79945 | 0.97842 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8132 | 0.97842 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89436 | 0.97842 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79952 | 0.98237 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82055 | 0.98237 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81332 | 0.98848 | Yes
Active | 2025W1-N11-WVM243593 | 243593 | 05ZUBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81985 | 0.987 | Yes
Active | 2025W1-N11-WVM243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9041 | 0.98514 | Yes
Active | 2025W1-N11-WVM243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89078 | 0.98512 | Yes
Active | 2025W1-N11-WVM243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90399 | 0.98512 | Yes
Active | 2025W1-N11-WVM243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88877 | 0.97199 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79053 | 0.98339 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80502 | 0.98339 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8937 | 0.98339 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79058 | 0.98823 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81584 | 0.98823 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80521 | 0.9936 | Yes
Active | 2025W1-N11-WVM243854 | 243854 | 05REAVER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81513 | 0.99356 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76255 | 0.96027 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78023 | 0.96027 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87531 | 0.96027 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76256 | 0.96676 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80135 | 0.96676 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78052 | 0.98089 | Yes
Active | 2025W1-N11-WVM243855 | 243855 | 05JUG ST | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80087 | 0.98141 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75958 | 0.96795 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77748 | 0.96795 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87811 | 0.96795 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75959 | 0.97476 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79861 | 0.97476 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77775 | 0.98989 | Yes
Active | 2025W1-N11-WVM243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79811 | 0.99045 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78637 | 0.98268 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80125 | 0.98268 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89205 | 0.98268 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78642 | 0.98783 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81352 | 0.98783 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80146 | 0.99236 | Yes
Active | 2025W1-N11-WVM243876 | 243876 | 05ST.CXX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81284 | 0.99327 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8509 | 0.97535 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89031 | 0.97535 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90191 | 0.97535 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8478 | 0.97615 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85079 | 0.97615 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89019 | 0.98527 | Yes
Active | 2025W1-N11-WVM243902 | 243902 | 05HARDIN SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84587 | 0.97028 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84019 | 0.97433 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88194 | 0.97433 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8983 | 0.97433 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84007 | 0.9753 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84079 | 0.9753 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88182 | 0.98509 | Yes
Active | 2025W1-N11-WVM243903 | 243903 | 05GUNN RD SW | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83892 | 0.97207 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77041 | 0.96139 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78828 | 0.96139 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87777 | 0.96139 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77041 | 0.96712 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80341 | 0.96712 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7885 | 0.97932 | Yes
Active | 2025W1-N11-WVM243915 | 243915 | 05BERRYWOOD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80272 | 0.97909 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7796 | 0.97506 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79523 | 0.97506 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8896 | 0.97506 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77964 | 0.98103 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81314 | 0.98103 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79556 | 0.99115 | Yes
Active | 2025W1-N11-WVM244020 | 244020 | 05MINK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8126 | 0.99155 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78227 | 0.96692 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79664 | 0.96692 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87972 | 0.96692 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7823 | 0.97146 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8057 | 0.97146 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79678 | 0.97872 | Yes
Active | 2025W1-N11-WVM244022 | 244022 | 05COLE | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80494 | 0.9777 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77419 | 0.96413 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78937 | 0.96413 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87569 | 0.96413 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77421 | 0.96894 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80007 | 0.96894 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78952 | 0.9769 | Yes
Active | 2025W1-N11-WVM244023 | 244023 | 05COLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79934 | 0.9766 | Yes
Active | 2025W1-N11-WVM244198 | 244198 | 05LEMASTER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87423 | 0.99404 | Yes
Active | 2025W1-N11-WVM244198 | 244198 | 05LEMASTER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8873 | 0.99404 | Yes
Active | 2025W1-N11-WVM244198 | 244198 | 05LEMASTER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87438 | 0.9958 | Yes
Active | 2025W1-N11-WVM244198 | 244198 | 05LEMASTER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89292 | 0.9958 | Yes
Active | 2025W1-N11-WVM244198 | 244198 | 05LEMASTER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8872 | 1.0025 | Yes
Active | 2025W1-N11-WVM244198 | 244198 | 05LEMASTER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89264 | 1.0016 | Yes
Active | 2025W1-N11-WVM244230 | 244230 | 05SUNDAY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87398 | 0.9941 | Yes
Active | 2025W1-N11-WVM244230 | 244230 | 05SUNDAY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88724 | 0.9941 | Yes
Active | 2025W1-N11-WVM244230 | 244230 | 05SUNDAY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87412 | 0.99648 | Yes
Active | 2025W1-N11-WVM244230 | 244230 | 05SUNDAY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89541 | 0.99648 | Yes
Active | 2025W1-N11-WVM244230 | 244230 | 05SUNDAY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88744 | 1.0026 | Yes
Active | 2025W1-N11-WVM244230 | 244230 | 05SUNDAY SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89509 | 1.0019 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78966 | 0.9753 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80411 | 0.9753 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89072 | 0.9753 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78972 | 0.98043 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81738 | 0.98043 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80437 | 0.98774 | Yes
Active | 2025W1-N11-WVM244232 | 244232 | 05SHANNONRSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81676 | 0.98757 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79484 | 0.97354 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8084 | 0.97354 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89166 | 0.97354 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7949 | 0.97799 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81744 | 0.97799 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80859 | 0.9846 | Yes
Active | 2025W1-N11-WVM244258 | 244258 | 05PARSONS1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81672 | 0.98311 | Yes
Active | 2025W1-N11-WVM244283 | 244283 | 05MINERAL SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87837 | 0.99358 | Yes
Active | 2025W1-N11-WVM244283 | 244283 | 05MINERAL SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89115 | 0.99358 | Yes
Active | 2025W1-N11-WVM244283 | 244283 | 05MINERAL SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87852 | 0.99506 | Yes
Active | 2025W1-N11-WVM244283 | 244283 | 05MINERAL SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89561 | 0.99506 | Yes
Active | 2025W1-N11-WVM244283 | 244283 | 05MINERAL SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89088 | 1.0016 | Yes
Active | 2025W1-N11-WVM244283 | 244283 | 05MINERAL SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89534 | 1.0005 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78545 | 0.98259 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80116 | 0.98259 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8931 | 0.98259 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7855 | 0.98815 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81581 | 0.98815 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80142 | 0.99485 | Yes
Active | 2025W1-N11-WVM244338 | 244338 | 05POTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81519 | 0.99607 | Yes
Active | 2025W1-N11-WVM244540 | 244540 | 05RHODES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91448 | 0.9935 | Yes
Active | 2025W1-N11-WVM244540 | 244540 | 05RHODES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91464 | 0.99346 | Yes
Active | 2025W1-N11-WVM244560 | 244560 | 05ISABELLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87334 | 0.99386 | Yes
Active | 2025W1-N11-WVM244560 | 244560 | 05ISABELLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88688 | 0.99386 | Yes
Active | 2025W1-N11-WVM244560 | 244560 | 05ISABELLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87346 | 0.99665 | Yes
Active | 2025W1-N11-WVM244560 | 244560 | 05ISABELLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89823 | 0.99665 | Yes
Active | 2025W1-N11-WVM244560 | 244560 | 05ISABELLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88749 | 1.0022 | Yes
Active | 2025W1-N11-WVM244560 | 244560 | 05ISABELLA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89784 | 1.0017 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76096 | 0.97016 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77845 | 0.97016 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8795 | 0.97016 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76097 | 0.97702 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79952 | 0.97702 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77874 | 0.99191 | Yes
Active | 2025W1-N11-WVM244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79903 | 0.9924 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78556 | 0.97302 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80013 | 0.97302 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88836 | 0.97302 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78562 | 0.97835 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81462 | 0.97835 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80042 | 0.98639 | Yes
Active | 2025W1-N11-WVM244868 | 244868 | 05BRICE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81403 | 0.98628 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79727 | 0.97552 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.81221 | 0.97552 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89992 | 0.97552 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79732 | 0.98062 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83052 | 0.98062 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81269 | 0.99011 | Yes
Active | 2025W1-N11-WVM244871 | 244871 | 05RIDGELY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82997 | 0.99003 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75521 | 0.96771 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77281 | 0.96771 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87547 | 0.96771 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75522 | 0.97469 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79381 | 0.97469 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77309 | 0.99008 | Yes
Active | 2025W1-N11-WVM245358 | 245358 | 05EMPEROR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79332 | 0.99059 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76092 | 0.97015 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77841 | 0.97015 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87948 | 0.97015 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76093 | 0.97701 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79948 | 0.97701 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7787 | 0.99191 | Yes
Active | 2025W1-N11-WVM245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79899 | 0.9924 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76147 | 0.9704 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77894 | 0.9704 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87987 | 0.9704 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76149 | 0.97725 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80002 | 0.97725 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77924 | 0.9921 | Yes
Active | 2025W1-N11-WVM245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79953 | 0.99258 | Yes
Active | 2025W1-N11-WVM245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90295 | 0.9849 | Yes
Active | 2025W1-N11-WVM245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88958 | 0.98492 | Yes
Active | 2025W1-N11-WVM245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90284 | 0.98492 | Yes
Active | 2025W1-N11-WVM245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88755 | 0.97179 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81811 | 0.97838 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.82887 | 0.97838 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89815 | 0.97838 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81817 | 0.98133 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83032 | 0.98133 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82894 | 0.98604 | Yes
Active | 2025W1-N11-WVM245769 | 245769 | 05ADKINS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82952 | 0.98249 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78276 | 0.98309 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79862 | 0.98309 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89135 | 0.98309 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78279 | 0.98837 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81178 | 0.98837 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79881 | 0.99304 | Yes
Active | 2025W1-N11-WVM245853 | 245853 | 05HESS SOUTH | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81108 | 0.9943 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76567 | 0.95828 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78371 | 0.95828 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87298 | 0.95828 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76566 | 0.96398 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79846 | 0.96398 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7839 | 0.97643 | Yes
Active | 2025W1-N11-WVM245952 | 245952 | 05DLAWAR1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79777 | 0.97625 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76569 | 0.9583 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78373 | 0.9583 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.873 | 0.9583 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76568 | 0.964 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79848 | 0.964 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78392 | 0.97645 | Yes
Active | 2025W1-N11-WVM245962 | 245962 | 05DLAWAR3 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79778 | 0.97626 | Yes
Active | 2025W1-N11-WVM245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87048 | 0.99098 | Yes
Active | 2025W1-N11-WVM245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88429 | 0.99098 | Yes
Active | 2025W1-N11-WVM245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87056 | 0.99311 | Yes
Active | 2025W1-N11-WVM245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89753 | 0.99311 | Yes
Active | 2025W1-N11-WVM245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88525 | 0.99843 | Yes
Active | 2025W1-N11-WVM245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89688 | 0.99786 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86671 | 0.96649 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89432 | 0.96649 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9034 | 0.96649 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85681 | 0.96685 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86663 | 0.96685 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89415 | 0.97307 | Yes
Active | 2025W1-N11-WVM245977 | 245977 | 05GRISTMILL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85517 | 0.95969 | Yes
Active | 2025W1-N11-WVM245983 | 245983 | 05GRISTMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89277 | 0.98998 | Yes
Active | 2025W1-N11-WVM245983 | 245983 | 05GRISTMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8816 | 0.99038 | Yes
Active | 2025W1-N11-WVM245983 | 245983 | 05GRISTMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89268 | 0.99038 | Yes
Active | 2025W1-N11-WVM245983 | 245983 | 05GRISTMILL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87985 | 0.98535 | Yes
Active | 2025W1-N11-WVM245994 | 245994 | 05GEMINI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89335 | 0.98712 | Yes
Active | 2025W1-N11-WVM245994 | 245994 | 05GEMINI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88164 | 0.98753 | Yes
Active | 2025W1-N11-WVM245994 | 245994 | 05GEMINI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89326 | 0.98753 | Yes
Active | 2025W1-N11-WVM245994 | 245994 | 05GEMINI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87985 | 0.98422 | Yes
Active | 2025W1-N11-WVM246010 | 246010 | 05PHILO2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88831 | 0.99665 | Yes
Active | 2025W1-N11-WVM246010 | 246010 | 05PHILO2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90056 | 0.99665 | Yes
Active | 2025W1-N11-WVM246010 | 246010 | 05PHILO2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88844 | 0.9998 | Yes
Active | 2025W1-N11-WVM246010 | 246010 | 05PHILO2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91108 | 0.9998 | Yes
Active | 2025W1-N11-WVM246010 | 246010 | 05PHILO2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90123 | 1.0037 | Yes
Active | 2025W1-N11-WVM246010 | 246010 | 05PHILO2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91081 | 1.0035 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82143 | 0.98906 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8366 | 0.98906 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91764 | 0.98906 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82154 | 0.99397 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85193 | 0.99397 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83698 | 1.0022 | Yes
Active | 2025W1-N11-WVM246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85147 | 1.0018 | Yes
Active | 2025W1-N11-WVM246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90411 | 0.98514 | Yes
Active | 2025W1-N11-WVM246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8908 | 0.98512 | Yes
Active | 2025W1-N11-WVM246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.904 | 0.98512 | Yes
Active | 2025W1-N11-WVM246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88878 | 0.97199 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7557 | 0.96814 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77331 | 0.96814 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87594 | 0.96814 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75571 | 0.97512 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79432 | 0.97512 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77359 | 0.9905 | Yes
Active | 2025W1-N11-WVM246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79384 | 0.99102 | Yes
Active | 2025W1-N11-WVM246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87136 | 0.99209 | Yes
Active | 2025W1-N11-WVM246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88513 | 0.99209 | Yes
Active | 2025W1-N11-WVM246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87145 | 0.99443 | Yes
Active | 2025W1-N11-WVM246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89781 | 0.99443 | Yes
Active | 2025W1-N11-WVM246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88598 | 0.99983 | Yes
Active | 2025W1-N11-WVM246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89724 | 0.9993 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7628 | 0.96026 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77997 | 0.96026 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87491 | 0.96026 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76282 | 0.96675 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80079 | 0.96675 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78027 | 0.98047 | Yes
Active | 2025W1-N11-WVM246312 | 246312 | 05BABBITT | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80032 | 0.9809 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76823 | 0.97075 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78531 | 0.97075 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87999 | 0.97075 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76824 | 0.97638 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80072 | 0.97638 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78551 | 0.98463 | Yes
Active | 2025W1-N11-WVM246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80006 | 0.98601 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75956 | 0.96795 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77745 | 0.96795 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87809 | 0.96795 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75957 | 0.97476 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79858 | 0.97476 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77773 | 0.98989 | Yes
Active | 2025W1-N11-WVM246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79809 | 0.99044 | Yes
Active | 2025W1-N11-WVM246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91728 | 0.99243 | Yes
Active | 2025W1-N11-WVM246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9174 | 0.99598 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76988 | 0.95994 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7888 | 0.95994 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8778 | 0.95994 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76985 | 0.96523 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80627 | 0.96523 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78896 | 0.97661 | Yes
Active | 2025W1-N11-WVM246523 | 246523 | 05HYATT SW1 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80558 | 0.97967 | Yes
Active | 2025W1-N11-WVM246526 | 246526 | 05GUERNSEY | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88322 | 0.97044 | Yes
Active | 2025W1-N11-WVM246526 | 246526 | 05GUERNSEY | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88344 | 0.97799 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78088 | 0.97717 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79621 | 0.97717 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88634 | 0.97717 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78091 | 0.98217 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8079 | 0.98217 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79639 | 0.98741 | Yes
Active | 2025W1-N11-WVM246716 | 246716 | 05PHILLIPI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80719 | 0.98777 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91918 | 0.96011 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.74223 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77133 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8603 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90139 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91189 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.91753 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.91882 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.91899 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91949 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18232_SRT-A | 0.9199 | 0.9329 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91843 | 0.95999 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91936 | 0.96032 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91967 | 0.9583 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91735 | 0.95916 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91088 | 0.95654 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90941 | 0.96523 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.74218 | 0.94087 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79699 | 0.94087 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91888 | 0.94087 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77156 | 0.96392 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91436 | 0.96479 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79677 | 0.96263 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90053 | 0.95489 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91886 | 0.95489 | Yes
Active | 2025W1-N11-WVM246751 | 246751 | 05VASSEL | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91709 | 0.9598 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76313 | 0.96028 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78375 | 0.96028 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87829 | 0.96028 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76312 | 0.96686 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80627 | 0.96686 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.784 | 0.9834 | Yes
Active | 2025W1-N11-WVM246752 | 246752 | 05VASSEL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80581 | 0.98391 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76397 | 0.96034 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78393 | 0.96034 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8775 | 0.96034 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76396 | 0.96675 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80488 | 0.96675 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78417 | 0.98239 | Yes
Active | 2025W1-N11-WVM246753 | 246753 | 05VASSEL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80437 | 0.98276 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79313 | 0.9763 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80737 | 0.9763 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89231 | 0.9763 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79319 | 0.98123 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81963 | 0.98123 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80763 | 0.9882 | Yes
Active | 2025W1-N11-WVM246761 | 246761 | 05THREEC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81901 | 0.98781 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77907 | 0.9798 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79531 | 0.9798 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89162 | 0.9798 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7791 | 0.98569 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8117 | 0.98569 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79558 | 0.99473 | Yes
Active | 2025W1-N11-WVM246765 | 246765 | 05OUTERB | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81112 | 0.99568 | Yes
Active | 2025W1-N11-WVM246851 | 246851 | 05CULBERTSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88208 | 0.99692 | Yes
Active | 2025W1-N11-WVM246851 | 246851 | 05CULBERTSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89474 | 0.99692 | Yes
Active | 2025W1-N11-WVM246851 | 246851 | 05CULBERTSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88219 | 0.99954 | Yes
Active | 2025W1-N11-WVM246851 | 246851 | 05CULBERTSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90584 | 0.99954 | Yes
Active | 2025W1-N11-WVM246851 | 246851 | 05CULBERTSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89552 | 1.0027 | Yes
Active | 2025W1-N11-WVM246851 | 246851 | 05CULBERTSON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90545 | 1.0025 | Yes
Active | 2025W1-N11-WVM246888 | 246888 | 05BIERSR | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86298 | 0.98251 | Yes
Active | 2025W1-N11-WVM246888 | 246888 | 05BIERSR | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87199 | 0.98251 | Yes
Active | 2025W1-N11-WVM246888 | 246888 | 05BIERSR | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8631 | 0.98393 | Yes
Active | 2025W1-N11-WVM246888 | 246888 | 05BIERSR | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87191 | 0.98393 | Yes
Active | 2025W1-N11-WVM246888 | 246888 | 05BIERSR | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87205 | 0.98967 | Yes
Active | 2025W1-N11-WVM246888 | 246888 | 05BIERSR | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87148 | 0.98576 | Yes
Active | 2025W1-N11-WVM246889 | 246889 | 05BIERSR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86755 | 0.98957 | Yes
Active | 2025W1-N11-WVM246889 | 246889 | 05BIERSR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87762 | 0.98957 | Yes
Active | 2025W1-N11-WVM246889 | 246889 | 05BIERSR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8677 | 0.99114 | Yes
Active | 2025W1-N11-WVM246889 | 246889 | 05BIERSR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87796 | 0.99114 | Yes
Active | 2025W1-N11-WVM246889 | 246889 | 05BIERSR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87762 | 0.99698 | Yes
Active | 2025W1-N11-WVM246889 | 246889 | 05BIERSR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8775 | 0.99343 | Yes
Active | 2025W1-N11-WVM246890 | 246890 | 05HOPETN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86897 | 0.98673 | Yes
Active | 2025W1-N11-WVM246890 | 246890 | 05HOPETN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87949 | 0.98673 | Yes
Active | 2025W1-N11-WVM246890 | 246890 | 05HOPETN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86912 | 0.98827 | Yes
Active | 2025W1-N11-WVM246890 | 246890 | 05HOPETN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87982 | 0.98827 | Yes
Active | 2025W1-N11-WVM246890 | 246890 | 05HOPETN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87943 | 0.99419 | Yes
Active | 2025W1-N11-WVM246890 | 246890 | 05HOPETN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87935 | 0.99072 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78188 | 0.98201 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79783 | 0.98201 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8904 | 0.98201 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78191 | 0.98729 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81098 | 0.98729 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79802 | 0.99208 | Yes
Active | 2025W1-N11-WVM246907 | 246907 | 05W.CAMPUS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81028 | 0.99326 | Yes
Active | 2025W1-N11-WVM246929 | 246929 | 05MADDOX | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91094 | 0.99013 | Yes
Active | 2025W1-N11-WVM246929 | 246929 | 05MADDOX | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90926 | 0.96972 | Yes
Active | 2025W1-N11-WVM246999 | 246999 | 05SORENS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85153 | 0.9489 | Yes
Active | 2025W1-N11-WVM246999 | 246999 | 05SORENS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85142 | 0.94381 | Yes
Active | 2025W1-N11-WVM246999 | 246999 | 05SORENS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | 0.91933 | 0.94381 | Yes
Active | 2025W1-N11-WVM246999 | 246999 | 05SORENS | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91831 | 0.95344 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83765 | 0.98081 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84984 | 0.98081 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91684 | 0.98081 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83779 | 0.98319 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85266 | 0.98319 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84985 | 0.98937 | Yes
Active | 2025W1-N11-WVM247019 | 247019 | 05NEVILLE SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85212 | 0.98664 | Yes
Active | 2025W1-N11-WVM247067 | 247067 | 05GOODHP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84467 | 0.99161 | Yes
Active | 2025W1-N11-WVM247067 | 247067 | 05GOODHP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85835 | 0.99161 | Yes
Active | 2025W1-N11-WVM247067 | 247067 | 05GOODHP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8448 | 0.99433 | Yes
Active | 2025W1-N11-WVM247067 | 247067 | 05GOODHP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86498 | 0.99433 | Yes
Active | 2025W1-N11-WVM247067 | 247067 | 05GOODHP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85836 | 1.001 | Yes
Active | 2025W1-N11-WVM247067 | 247067 | 05GOODHP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86455 | 0.99987 | Yes
Active | 2025W1-N11-WVM247083 | 247083 | 05NPHISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88835 | 0.99678 | Yes
Active | 2025W1-N11-WVM247083 | 247083 | 05NPHISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9006 | 0.99678 | Yes
Active | 2025W1-N11-WVM247083 | 247083 | 05NPHISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88847 | 0.99992 | Yes
Active | 2025W1-N11-WVM247083 | 247083 | 05NPHISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91113 | 0.99992 | Yes
Active | 2025W1-N11-WVM247083 | 247083 | 05NPHISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90128 | 1.0038 | Yes
Active | 2025W1-N11-WVM247083 | 247083 | 05NPHISS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91085 | 1.0036 | Yes
Active | 2025W1-N11-WVM247148 | 247148 | 05SBLMSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87693 | 0.99021 | Yes
Active | 2025W1-N11-WVM247148 | 247148 | 05SBLMSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8888 | 0.99021 | Yes
Active | 2025W1-N11-WVM247148 | 247148 | 05SBLMSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87709 | 0.99173 | Yes
Active | 2025W1-N11-WVM247148 | 247148 | 05SBLMSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89136 | 0.99173 | Yes
Active | 2025W1-N11-WVM247148 | 247148 | 05SBLMSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88867 | 0.99802 | Yes
Active | 2025W1-N11-WVM247148 | 247148 | 05SBLMSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89099 | 0.99573 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75743 | 0.95515 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7744 | 0.95515 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86586 | 0.95515 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9196 | 0.95515 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75743 | 0.96049 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.7887 | 0.96049 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77456 | 0.97008 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78802 | 0.97128 | Yes
Active | 2025W1-N11-WVM247199 | 247199 | 05AMLIN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91865 | 0.96648 | Yes
Active | 2025W1-N11-WVM247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91731 | 0.99245 | Yes
Active | 2025W1-N11-WVM247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91743 | 0.99599 | Yes
Active | 2025W1-N11-WVM247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91728 | 0.99245 | Yes
Active | 2025W1-N11-WVM247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9174 | 0.996 | Yes
Active | 2025W1-N11-WVM247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91725 | 0.99244 | Yes
Active | 2025W1-N11-WVM247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91737 | 0.99599 | Yes
Active | 2025W1-N11-WVM247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91725 | 0.99244 | Yes
Active | 2025W1-N11-WVM247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91737 | 0.99599 | Yes
Active | 2025W1-N11-WVM247497 | 247497 | 05CLOUSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86692 | 0.99372 | Yes
Active | 2025W1-N11-WVM247497 | 247497 | 05CLOUSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88068 | 0.99372 | Yes
Active | 2025W1-N11-WVM247497 | 247497 | 05CLOUSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86705 | 0.99734 | Yes
Active | 2025W1-N11-WVM247497 | 247497 | 05CLOUSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89336 | 0.99734 | Yes
Active | 2025W1-N11-WVM247497 | 247497 | 05CLOUSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88123 | 1.0031 | Yes
Active | 2025W1-N11-WVM247497 | 247497 | 05CLOUSE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89297 | 1.0027 | Yes
Active | 2025W1-N11-WVM247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91663 | 0.9924 | Yes
Active | 2025W1-N11-WVM247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91675 | 0.99594 | Yes
Active | 2025W1-N11-WVM247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91663 | 0.9924 | Yes
Active | 2025W1-N11-WVM247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91675 | 0.99594 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76123 | 0.95723 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77773 | 0.95723 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86795 | 0.95723 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76123 | 0.96243 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79107 | 0.96243 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77789 | 0.97162 | Yes
Active | 2025W1-N11-WVM247509 | 247509 | 05HAYDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79038 | 0.97241 | Yes
Active | 2025W1-N11-WVM247513 | 247513 | 05BOUTWELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91312 | 0.99026 | Yes
Active | 2025W1-N11-WVM247513 | 247513 | 05BOUTWELL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91119 | 0.9785 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8143 | 0.98716 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.82791 | 0.98716 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90742 | 0.98716 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81438 | 0.99089 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83514 | 0.99089 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82801 | 0.99686 | Yes
Active | 2025W1-N11-WVM247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83449 | 0.99547 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79432 | 0.98022 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80902 | 0.98022 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89529 | 0.98022 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79438 | 0.98536 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82194 | 0.98536 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80927 | 0.9921 | Yes
Active | 2025W1-N11-WVM247623 | 247623 | 05GROVES2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82131 | 0.99221 | Yes
Active | 2025W1-N11-WVM247679 | 247679 | 05LEE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89718 | 0.98658 | Yes
Active | 2025W1-N11-WVM247679 | 247679 | 05LEE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90814 | 0.98658 | Yes
Active | 2025W1-N11-WVM247679 | 247679 | 05LEE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89734 | 0.9863 | Yes
Active | 2025W1-N11-WVM247679 | 247679 | 05LEE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90956 | 0.9863 | Yes
Active | 2025W1-N11-WVM247679 | 247679 | 05LEE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90781 | 0.99234 | Yes
Active | 2025W1-N11-WVM247679 | 247679 | 05LEE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90946 | 0.99204 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76308 | 0.9602 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78384 | 0.9602 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87831 | 0.9602 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76307 | 0.96678 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80635 | 0.96678 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78409 | 0.98343 | Yes
Active | 2025W1-N11-WVM247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8059 | 0.9839 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76932 | 0.95972 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78824 | 0.95972 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87763 | 0.95972 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76929 | 0.96505 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80606 | 0.96505 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78841 | 0.97675 | Yes
Active | 2025W1-N11-WVM247741 | 247741 | 05HYATT SW2 | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80538 | 0.97965 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77557 | 0.97341 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79147 | 0.97341 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88725 | 0.97341 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77561 | 0.97973 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81127 | 0.97973 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79182 | 0.9918 | Yes
Active | 2025W1-N11-WVM247767 | 247767 | 05HAZELTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81076 | 0.99204 | Yes
Active | 2025W1-N11-WVM247791 | 247791 | 05ELK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89613 | 0.99242 | Yes
Active | 2025W1-N11-WVM247791 | 247791 | 05ELK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90776 | 0.99242 | Yes
Active | 2025W1-N11-WVM247791 | 247791 | 05ELK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89629 | 0.99296 | Yes
Active | 2025W1-N11-WVM247791 | 247791 | 05ELK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90818 | 0.99296 | Yes
Active | 2025W1-N11-WVM247791 | 247791 | 05ELK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90686 | 0.99887 | Yes
Active | 2025W1-N11-WVM247791 | 247791 | 05ELK | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90793 | 0.99706 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83938 | 0.98025 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85148 | 0.98025 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91763 | 0.98025 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83951 | 0.98256 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85408 | 0.98256 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85148 | 0.98875 | Yes
Active | 2025W1-N11-WVM247862 | 247862 | 05TUSCANY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85355 | 0.98595 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76297 | 0.96358 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77977 | 0.96358 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87268 | 0.96358 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76298 | 0.96896 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79367 | 0.96896 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77995 | 0.97681 | Yes
Active | 2025W1-N11-WVM247873 | 247873 | 05BRITTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.793 | 0.9778 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78745 | 0.97396 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80153 | 0.97396 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88557 | 0.97396 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78749 | 0.9783 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8099 | 0.9783 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80167 | 0.9844 | Yes
Active | 2025W1-N11-WVM247896 | 247896 | 05BOLTON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80916 | 0.9832 | Yes
Active | 2025W1-N11-WVM247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87608 | 0.99157 | Yes
Active | 2025W1-N11-WVM247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88835 | 0.99157 | Yes
Active | 2025W1-N11-WVM247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87624 | 0.99316 | Yes
Active | 2025W1-N11-WVM247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8919 | 0.99316 | Yes
Active | 2025W1-N11-WVM247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88823 | 0.9996 | Yes
Active | 2025W1-N11-WVM247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89156 | 0.99774 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78684 | 0.98167 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80158 | 0.98167 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89161 | 0.98167 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78689 | 0.98672 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81334 | 0.98672 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80178 | 0.9917 | Yes
Active | 2025W1-N11-WVM247931 | 247931 | 05VINE_GS_X | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81265 | 0.99217 | Yes
Active | 2025W1-N11-WVM247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87914 | 0.98499 | Yes
Active | 2025W1-N11-WVM247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89153 | 0.98499 | Yes
Active | 2025W1-N11-WVM247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8793 | 0.98558 | Yes
Active | 2025W1-N11-WVM247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89501 | 0.98558 | Yes
Active | 2025W1-N11-WVM247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89132 | 0.99226 | Yes
Active | 2025W1-N11-WVM247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89484 | 0.99174 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78681 | 0.97092 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80416 | 0.97092 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89282 | 0.97092 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78682 | 0.97664 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82007 | 0.97664 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80447 | 0.98804 | Yes
Active | 2025W1-N11-WVM247972 | 247972 | 05CONDIT SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81939 | 0.9877 | Yes
Active | 2025W1-N11-WVM247979 | 247979 | 05NORFLD SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91364 | 0.99546 | Yes
Active | 2025W1-N11-WVM247979 | 247979 | 05NORFLD SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91376 | 0.99874 | Yes
Active | 2025W1-N11-WVM247980 | 247980 | 05RUSTIC SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90027 | 0.99559 | Yes
Active | 2025W1-N11-WVM247980 | 247980 | 05RUSTIC SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91137 | 0.99559 | Yes
Active | 2025W1-N11-WVM247980 | 247980 | 05RUSTIC SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90039 | 0.99883 | Yes
Active | 2025W1-N11-WVM247980 | 247980 | 05RUSTIC SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91204 | 1.0024 | Yes
Active | 2025W1-N11-WVM247980 | 247980 | 05RUSTIC SS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91992 | 1.0023 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89065 | 0.98671 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89777 | 0.98671 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91475 | 0.98671 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88444 | 0.98711 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89065 | 0.98711 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89828 | 0.99216 | Yes
Active | 2025W1-N11-WVM253002 | 253002 | 09AIRWAY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88366 | 0.98186 | Yes
Active | 2025W1-N11-WVM253004 | 253004 | 09AMSTRD | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89584 | 0.986 | Yes
Active | 2025W1-N11-WVM253004 | 253004 | 09AMSTRD | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.883 | 0.98633 | Yes
Active | 2025W1-N11-WVM253004 | 253004 | 09AMSTRD | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89577 | 0.98633 | Yes
Active | 2025W1-N11-WVM253004 | 253004 | 09AMSTRD | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88131 | 0.97805 | Yes
Active | 2025W1-N11-WVM253005 | 253005 | 09BATH | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89507 | 0.99183 | Yes
Active | 2025W1-N11-WVM253005 | 253005 | 09BATH | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90589 | 0.99183 | Yes
Active | 2025W1-N11-WVM253005 | 253005 | 09BATH | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88573 | 0.99229 | Yes
Active | 2025W1-N11-WVM253005 | 253005 | 09BATH | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89506 | 0.99229 | Yes
Active | 2025W1-N11-WVM253005 | 253005 | 09BATH | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90512 | 0.99582 | Yes
Active | 2025W1-N11-WVM253005 | 253005 | 09BATH | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88486 | 0.98714 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88896 | 0.97412 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89843 | 0.97412 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91853 | 0.97412 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87922 | 0.97468 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88893 | 0.97468 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89806 | 0.97796 | Yes
Active | 2025W1-N11-WVM253006 | 253006 | 09BATH | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87834 | 0.96937 | Yes
Active | 2025W1-N11-WVM253007 | 253007 | 09BELLBR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90988 | 0.99389 | Yes
Active | 2025W1-N11-WVM253007 | 253007 | 09BELLBR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91811 | 0.99389 | Yes
Active | 2025W1-N11-WVM253007 | 253007 | 09BELLBR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89955 | 0.99429 | Yes
Active | 2025W1-N11-WVM253007 | 253007 | 09BELLBR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90992 | 0.99429 | Yes
Active | 2025W1-N11-WVM253007 | 253007 | 09BELLBR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9176 | 0.99739 | Yes
Active | 2025W1-N11-WVM253007 | 253007 | 09BELLBR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89883 | 0.98899 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88077 | 0.97408 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89038 | 0.97408 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91036 | 0.97408 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.873 | 0.97441 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88077 | 0.97441 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89015 | 0.97736 | Yes
Active | 2025W1-N11-WVM253010 | 253010 | 09BURDOX | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87225 | 0.96929 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8791 | 0.97235 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8891 | 0.97235 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90899 | 0.97235 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87097 | 0.97266 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8791 | 0.97266 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88886 | 0.97577 | Yes
Active | 2025W1-N11-WVM253011 | 253011 | 09CARGIL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87019 | 0.96751 | Yes
Active | 2025W1-N11-WVM253012 | 253012 | 09CENTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91888 | 0.99641 | Yes
Active | 2025W1-N11-WVM253012 | 253012 | 09CENTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91821 | 0.99126 | Yes
Active | 2025W1-N11-WVM253014 | 253014 | 09CLINTO | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91584 | 0.99231 | Yes
Active | 2025W1-N11-WVM253014 | 253014 | 09CLINTO | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9081 | 0.99274 | Yes
Active | 2025W1-N11-WVM253014 | 253014 | 09CLINTO | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91561 | 0.99274 | Yes
Active | 2025W1-N11-WVM253014 | 253014 | 09CLINTO | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90738 | 0.98857 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76807 | 0.95257 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78563 | 0.95257 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86358 | 0.95257 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9174 | 0.95257 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9194 | 0.95644 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76805 | 0.95761 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79076 | 0.95761 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78566 | 0.9676 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78984 | 0.96608 | Yes
Active | 2025W1-N11-WVM253021 | 253021 | 09DARBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91646 | 0.96484 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87172 | 0.98096 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89502 | 0.98096 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91387 | 0.98096 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86244 | 0.98139 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87167 | 0.98139 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89484 | 0.98705 | Yes
Active | 2025W1-N11-WVM253024 | 253024 | 09ESIDNY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86095 | 0.97406 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78666 | 0.95141 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80169 | 0.95141 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86109 | 0.95141 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9194 | 0.95141 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.8893 | 0.95402 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89058 | 0.95402 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90036 | 0.95402 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78665 | 0.95267 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79379 | 0.95267 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80153 | 0.96005 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79273 | 0.95383 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91852 | 0.9567 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88925 | 0.96393 | Yes
Active | 2025W1-N11-WVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89053 | 0.95274 | Yes
Active | 2025W1-N11-WVM253026 | 253026 | 09GREENE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89512 | 0.98944 | Yes
Active | 2025W1-N11-WVM253026 | 253026 | 09GREENE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90416 | 0.98944 | Yes
Active | 2025W1-N11-WVM253026 | 253026 | 09GREENE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88707 | 0.98986 | Yes
Active | 2025W1-N11-WVM253026 | 253026 | 09GREENE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89513 | 0.98986 | Yes
Active | 2025W1-N11-WVM253026 | 253026 | 09GREENE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90393 | 0.99352 | Yes
Active | 2025W1-N11-WVM253026 | 253026 | 09GREENE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88627 | 0.98507 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8871 | 0.97549 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89585 | 0.97549 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91848 | 0.97549 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87821 | 0.9762 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88707 | 0.9762 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89549 | 0.97943 | Yes
Active | 2025W1-N11-WVM253027 | 253027 | 09GREENE | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87736 | 0.97107 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86972 | 0.97335 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88836 | 0.97335 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90511 | 0.97335 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8593 | 0.97356 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86968 | 0.97356 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88814 | 0.97915 | Yes
Active | 2025W1-N11-WVM253031 | 253031 | 09HALTER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85807 | 0.96618 | Yes
Active | 2025W1-N11-WVM253040 | 253040 | 09KNOLLW | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88926 | 0.98493 | Yes
Active | 2025W1-N11-WVM253040 | 253040 | 09KNOLLW | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89836 | 0.98493 | Yes
Active | 2025W1-N11-WVM253040 | 253040 | 09KNOLLW | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88186 | 0.98532 | Yes
Active | 2025W1-N11-WVM253040 | 253040 | 09KNOLLW | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88927 | 0.98532 | Yes
Active | 2025W1-N11-WVM253040 | 253040 | 09KNOLLW | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89817 | 0.98852 | Yes
Active | 2025W1-N11-WVM253040 | 253040 | 09KNOLLW | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88112 | 0.98077 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84043 | 0.96632 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8654 | 0.96632 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89728 | 0.96632 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83581 | 0.96721 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84037 | 0.96721 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86528 | 0.97223 | Yes
Active | 2025W1-N11-WVM253042 | 253042 | 09LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83418 | 0.9604 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77859 | 0.95128 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79449 | 0.95128 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86104 | 0.95128 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91798 | 0.95128 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9034 | 0.95876 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90377 | 0.95876 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91198 | 0.95876 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77858 | 0.95397 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79138 | 0.95397 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7944 | 0.96233 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79036 | 0.95781 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91708 | 0.95922 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90373 | 0.96729 | Yes
Active | 2025W1-N11-WVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90335 | 0.95705 | Yes
Active | 2025W1-N11-WVM253046 | 253046 | 09MIAMI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89098 | 0.98128 | Yes
Active | 2025W1-N11-WVM253046 | 253046 | 09MIAMI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90379 | 0.98128 | Yes
Active | 2025W1-N11-WVM253046 | 253046 | 09MIAMI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88035 | 0.98152 | Yes
Active | 2025W1-N11-WVM253046 | 253046 | 09MIAMI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89097 | 0.98152 | Yes
Active | 2025W1-N11-WVM253046 | 253046 | 09MIAMI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90351 | 0.98575 | Yes
Active | 2025W1-N11-WVM253046 | 253046 | 09MIAMI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87943 | 0.97618 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88478 | 0.96775 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89886 | 0.96775 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9126 | 0.96775 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87327 | 0.96793 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88475 | 0.96793 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89858 | 0.97211 | Yes
Active | 2025W1-N11-WVM253047 | 253047 | 09MIAMI | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87225 | 0.96205 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88451 | 0.97782 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89388 | 0.97782 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91437 | 0.97782 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87688 | 0.97815 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88451 | 0.97815 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89365 | 0.98115 | Yes
Active | 2025W1-N11-WVM253049 | 253049 | 09MONUM1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87613 | 0.97317 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88259 | 0.97748 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89187 | 0.97748 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91336 | 0.97748 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87543 | 0.97782 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88259 | 0.97782 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89168 | 0.98057 | Yes
Active | 2025W1-N11-WVM253050 | 253050 | 09MONUM2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87472 | 0.9731 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87971 | 0.97299 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88954 | 0.97299 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90947 | 0.97299 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87172 | 0.97331 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8797 | 0.97331 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88931 | 0.97635 | Yes
Active | 2025W1-N11-WVM253053 | 253053 | 09NEEDMO | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87096 | 0.96817 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88001 | 0.97292 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89043 | 0.97292 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91015 | 0.97292 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8715 | 0.97322 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88001 | 0.97322 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89019 | 0.9765 | Yes
Active | 2025W1-N11-WVM253056 | 253056 | 09NORTHR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8707 | 0.96803 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88676 | 0.98033 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89606 | 0.98033 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91708 | 0.98033 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87903 | 0.98068 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88676 | 0.98068 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89583 | 0.98384 | Yes
Active | 2025W1-N11-WVM253062 | 253062 | 09OVERL1 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87827 | 0.97575 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88235 | 0.97963 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89148 | 0.97963 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91492 | 0.97963 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87575 | 0.97997 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88235 | 0.97997 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89135 | 0.98258 | Yes
Active | 2025W1-N11-WVM253063 | 253063 | 09OVERL2 | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87507 | 0.97571 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85959 | 0.9755 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88355 | 0.9755 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90726 | 0.9755 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85185 | 0.97611 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85954 | 0.97611 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88339 | 0.98153 | Yes
Active | 2025W1-N11-WVM253065 | 253065 | 09QUINCY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85029 | 0.96883 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87813 | 0.98354 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90104 | 0.98354 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91711 | 0.98354 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86798 | 0.98386 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87808 | 0.98386 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90084 | 0.98966 | Yes
Active | 2025W1-N11-WVM253068 | 253068 | 09SHELBY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86653 | 0.97649 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86839 | 0.96437 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89093 | 0.96437 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90292 | 0.96437 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85783 | 0.96459 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86834 | 0.96459 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89072 | 0.97022 | Yes
Active | 2025W1-N11-WVM253069 | 253069 | 09SHELBY | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85645 | 0.95783 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86092 | 0.9722 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88243 | 0.9722 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90013 | 0.9722 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85045 | 0.97248 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86087 | 0.97248 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88223 | 0.97873 | Yes
Active | 2025W1-N11-WVM253071 | 253071 | 09SIDNEY | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84905 | 0.96427 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86904 | 0.97315 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88787 | 0.97315 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90467 | 0.97315 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85862 | 0.97336 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.869 | 0.97336 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88765 | 0.979 | Yes
Active | 2025W1-N11-WVM253072 | 253072 | 09SPRING | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85738 | 0.96593 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87841 | 0.9763 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89163 | 0.9763 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91114 | 0.9763 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86886 | 0.97653 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87839 | 0.97653 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89137 | 0.98127 | Yes
Active | 2025W1-N11-WVM253074 | 253074 | 09STATAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86788 | 0.96996 | Yes
Active | 2025W1-N11-WVM253078 | 253078 | 09SUGRCK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91764 | 0.99616 | Yes
Active | 2025W1-N11-WVM253078 | 253078 | 09SUGRCK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90709 | 0.99657 | Yes
Active | 2025W1-N11-WVM253078 | 253078 | 09SUGRCK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91769 | 0.99657 | Yes
Active | 2025W1-N11-WVM253078 | 253078 | 09SUGRCK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90638 | 0.99102 | Yes
Active | 2025W1-N11-WVM253079 | 253079 | 09SUGRCK | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90012 | 0.97683 | Yes
Active | 2025W1-N11-WVM253079 | 253079 | 09SUGRCK | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90781 | 0.97683 | Yes
Active | 2025W1-N11-WVM253079 | 253079 | 09SUGRCK | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88985 | 0.97735 | Yes
Active | 2025W1-N11-WVM253079 | 253079 | 09SUGRCK | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90011 | 0.97735 | Yes
Active | 2025W1-N11-WVM253079 | 253079 | 09SUGRCK | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90743 | 0.98004 | Yes
Active | 2025W1-N11-WVM253079 | 253079 | 09SUGRCK | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88903 | 0.97203 | Yes
Active | 2025W1-N11-WVM253083 | 253083 | 09TREBEI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89752 | 0.98972 | Yes
Active | 2025W1-N11-WVM253083 | 253083 | 09TREBEI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90673 | 0.98972 | Yes
Active | 2025W1-N11-WVM253083 | 253083 | 09TREBEI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88947 | 0.99013 | Yes
Active | 2025W1-N11-WVM253083 | 253083 | 09TREBEI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89753 | 0.99013 | Yes
Active | 2025W1-N11-WVM253083 | 253083 | 09TREBEI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90643 | 0.99373 | Yes
Active | 2025W1-N11-WVM253083 | 253083 | 09TREBEI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88865 | 0.98547 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79113 | 0.95119 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80573 | 0.95119 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86096 | 0.95119 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91994 | 0.95119 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.88078 | 0.95099 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88308 | 0.95099 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.89354 | 0.95099 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79112 | 0.95163 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79513 | 0.95163 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80553 | 0.95843 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79405 | 0.95128 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91907 | 0.95494 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88073 | 0.96169 | Yes
Active | 2025W1-N11-WVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88302 | 0.94998 | Yes
Active | 2025W1-N11-WVM253089 | 253089 | 09WMILTN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91705 | 0.98986 | Yes
Active | 2025W1-N11-WVM253089 | 253089 | 09WMILTN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90641 | 0.98999 | Yes
Active | 2025W1-N11-WVM253089 | 253089 | 09WMILTN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91703 | 0.98999 | Yes
Active | 2025W1-N11-WVM253089 | 253089 | 09WMILTN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90553 | 0.98468 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89194 | 0.96825 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90497 | 0.96825 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91625 | 0.96825 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87949 | 0.96834 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89192 | 0.96834 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90469 | 0.97222 | Yes
Active | 2025W1-N11-WVM253090 | 253090 | 09WMILTN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8785 | 0.96248 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88179 | 0.97513 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.8912 | 0.97513 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91123 | 0.97513 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87422 | 0.97546 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88178 | 0.97546 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89098 | 0.97834 | Yes
Active | 2025W1-N11-WVM253093 | 253093 | 09WEBSTR | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87348 | 0.97038 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87345 | 0.97415 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88639 | 0.97415 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90695 | 0.97415 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8643 | 0.9744 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87343 | 0.9744 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88613 | 0.97927 | Yes
Active | 2025W1-N11-WVM253098 | 253098 | 09STAUNT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86332 | 0.96746 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83298 | 0.9813 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84236 | 0.9813 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90431 | 0.9813 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83305 | 0.98399 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84118 | 0.98399 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8424 | 0.98832 | Yes
Active | 2025W1-N11-WVM253100 | 253100 | 09ATLNTA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84039 | 0.98377 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82904 | 0.97022 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85631 | 0.97022 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91211 | 0.97022 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82898 | 0.9727 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84416 | 0.9727 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85675 | 0.97841 | Yes
Active | 2025W1-N11-WVM253101 | 253101 | 09BLUJK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84259 | 0.975 | Yes
Active | 2025W1-N11-WVM253106 | 253106 | 09NCARLI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89974 | 0.98432 | Yes
Active | 2025W1-N11-WVM253106 | 253106 | 09NCARLI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91136 | 0.98432 | Yes
Active | 2025W1-N11-WVM253106 | 253106 | 09NCARLI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89018 | 0.98462 | Yes
Active | 2025W1-N11-WVM253106 | 253106 | 09NCARLI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89972 | 0.98462 | Yes
Active | 2025W1-N11-WVM253106 | 253106 | 09NCARLI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91105 | 0.98817 | Yes
Active | 2025W1-N11-WVM253106 | 253106 | 09NCARLI | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88928 | 0.97969 | Yes
Active | 2025W1-N11-WVM253107 | 253107 | 09ALPHA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90169 | 0.99142 | Yes
Active | 2025W1-N11-WVM253107 | 253107 | 09ALPHA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91034 | 0.99142 | Yes
Active | 2025W1-N11-WVM253107 | 253107 | 09ALPHA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89163 | 0.99182 | Yes
Active | 2025W1-N11-WVM253107 | 253107 | 09ALPHA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90171 | 0.99182 | Yes
Active | 2025W1-N11-WVM253107 | 253107 | 09ALPHA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90995 | 0.99548 | Yes
Active | 2025W1-N11-WVM253107 | 253107 | 09ALPHA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8909 | 0.98681 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88327 | 0.97753 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89832 | 0.97753 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91405 | 0.97753 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87307 | 0.97769 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88324 | 0.97769 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89808 | 0.98242 | Yes
Active | 2025W1-N11-WVM253139 | 253139 | 09ELDEAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87203 | 0.97125 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87127 | 0.97614 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89396 | 0.97614 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90892 | 0.97614 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86028 | 0.97647 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87121 | 0.97647 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89376 | 0.98217 | Yes
Active | 2025W1-N11-WVM253150 | 253150 | 09FRANKL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85878 | 0.96842 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77665 | 0.95139 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79281 | 0.95139 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86128 | 0.95139 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91777 | 0.95139 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9071 | 0.96019 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90791 | 0.96019 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91535 | 0.96019 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77663 | 0.95446 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79103 | 0.95446 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79273 | 0.9631 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79003 | 0.95906 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91685 | 0.96004 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90787 | 0.96833 | Yes
Active | 2025W1-N11-WVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90706 | 0.95837 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8472 | 0.9798 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85618 | 0.9798 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90422 | 0.9798 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8472 | 0.98215 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84732 | 0.98215 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85601 | 0.98647 | Yes
Active | 2025W1-N11-WVM253248 | 253248 | 09MADISN | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84639 | 0.97913 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78205 | 0.96163 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.83136 | 0.96163 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88181 | 0.96163 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 0.91157 | 0.96163 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78197 | 0.96341 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81062 | 0.96341 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 0.91508 | 0.96341 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83131 | 0.97547 | Yes
Active | 2025W1-N11-WVM253251 | 253251 | 09PEORIA | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80957 | 0.97834 | Yes
Active | 2025W1-N11-WVM253255 | 253255 | 09GEBHRT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9103 | 0.99467 | Yes
Active | 2025W1-N11-WVM253255 | 253255 | 09GEBHRT | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90962 | 0.98928 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86038 | 0.97118 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88169 | 0.97118 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89933 | 0.97118 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84989 | 0.97146 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86033 | 0.97146 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88149 | 0.97766 | Yes
Active | 2025W1-N11-WVM253258 | 253258 | 09MLLCRK | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8485 | 0.96331 | Yes
Active | 2025W1-N11-WVM253266 | 253266 | 09HAAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89652 | 0.98318 | Yes
Active | 2025W1-N11-WVM253266 | 253266 | 09HAAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90857 | 0.98318 | Yes
Active | 2025W1-N11-WVM253266 | 253266 | 09HAAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88657 | 0.98346 | Yes
Active | 2025W1-N11-WVM253266 | 253266 | 09HAAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8965 | 0.98346 | Yes
Active | 2025W1-N11-WVM253266 | 253266 | 09HAAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90827 | 0.98726 | Yes
Active | 2025W1-N11-WVM253266 | 253266 | 09HAAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88566 | 0.97838 | Yes
Active | 2025W1-N11-WVM253268 | 253268 | 09FURNAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89866 | 0.98344 | Yes
Active | 2025W1-N11-WVM253268 | 253268 | 09FURNAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91119 | 0.98344 | Yes
Active | 2025W1-N11-WVM253268 | 253268 | 09FURNAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88797 | 0.98365 | Yes
Active | 2025W1-N11-WVM253268 | 253268 | 09FURNAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89864 | 0.98365 | Yes
Active | 2025W1-N11-WVM253268 | 253268 | 09FURNAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91091 | 0.98765 | Yes
Active | 2025W1-N11-WVM253268 | 253268 | 09FURNAS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88706 | 0.97828 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82468 | 0.96874 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84973 | 0.96874 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90775 | 0.96874 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82462 | 0.97163 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84261 | 0.97163 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85033 | 0.97834 | Yes
Active | 2025W1-N11-WVM253283 | 253283 | 09E.LOGAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84113 | 0.97534 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86043 | 0.97084 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88161 | 0.97084 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89918 | 0.97084 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84994 | 0.9711 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86038 | 0.9711 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88141 | 0.97729 | Yes
Active | 2025W1-N11-WVM253284 | 253284 | 09SMCRP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84856 | 0.963 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86254 | 0.97702 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88636 | 0.97702 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90903 | 0.97702 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85446 | 0.97759 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86248 | 0.97759 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88619 | 0.98306 | Yes
Active | 2025W1-N11-WVM253373 | 253373 | 09KISER | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85292 | 0.9703 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80042 | 0.96597 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84822 | 0.96597 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88546 | 0.96597 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80032 | 0.96749 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81798 | 0.96749 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84813 | 0.97907 | Yes
Active | 2025W1-N11-WVM270280 | 270280 | AF1-227 MAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81657 | 0.97552 | Yes
Active | 2025W1-N11-WVM270584 | 270584 | AE1-091_POI | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9189 | 0.98648 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76489 | 0.96359 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78415 | 0.96359 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87977 | 0.96359 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76489 | 0.97013 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8063 | 0.97013 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78442 | 0.98562 | Yes
Active | 2025W1-N11-WVM288569 | 288569 | 05BERMUDA | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80581 | 0.98622 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76147 | 0.96917 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77954 | 0.96917 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87978 | 0.96917 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76148 | 0.97593 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80064 | 0.97593 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77982 | 0.99106 | Yes
Active | 2025W1-N11-WVM288579 | 288579 | 05FIESTA | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80014 | 0.99165 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76347 | 0.97177 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78193 | 0.97177 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88253 | 0.97177 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76347 | 0.97858 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80337 | 0.97858 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7822 | 0.99426 | Yes
Active | 2025W1-N11-WVM288603 | 288603 | 05TASJAN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80288 | 0.99481 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75477 | 0.96731 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77236 | 0.96731 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87504 | 0.96731 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75479 | 0.9743 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79335 | 0.9743 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77264 | 0.98969 | Yes
Active | 2025W1-N11-WVM288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79286 | 0.99021 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75476 | 0.9673 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77235 | 0.9673 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87502 | 0.9673 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75477 | 0.97429 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79333 | 0.97429 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77263 | 0.98968 | Yes
Active | 2025W1-N11-WVM288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79285 | 0.9902 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75455 | 0.96712 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77213 | 0.96712 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87482 | 0.96712 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75456 | 0.9741 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79311 | 0.9741 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77241 | 0.9895 | Yes
Active | 2025W1-N11-WVM288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79263 | 0.99002 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75333 | 0.96605 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77088 | 0.96605 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87364 | 0.96605 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75335 | 0.97304 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79183 | 0.97304 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77117 | 0.98846 | Yes
Active | 2025W1-N11-WVM288616 | 288616 | 05NBY6 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79135 | 0.98898 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75311 | 0.96586 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77066 | 0.96586 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87342 | 0.96586 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75312 | 0.97285 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.7916 | 0.97285 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77094 | 0.98827 | Yes
Active | 2025W1-N11-WVM288617 | 288617 | 05NBY7 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79112 | 0.98879 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75336 | 0.96607 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77091 | 0.96607 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87366 | 0.96607 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75337 | 0.97306 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79186 | 0.97306 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77119 | 0.98848 | Yes
Active | 2025W1-N11-WVM288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79137 | 0.989 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75335 | 0.96607 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77091 | 0.96607 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87366 | 0.96607 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75337 | 0.97306 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79186 | 0.97306 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77119 | 0.98848 | Yes
Active | 2025W1-N11-WVM288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79137 | 0.989 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76083 | 0.96058 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77783 | 0.96058 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8704 | 0.96058 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76083 | 0.96596 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79201 | 0.96596 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.778 | 0.97457 | Yes
Active | 2025W1-N11-WVM288640 | 288640 | 05DUBLINX | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79134 | 0.97565 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77028 | 0.97707 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78871 | 0.97707 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8885 | 0.97707 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77028 | 0.98383 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80998 | 0.98383 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78898 | 0.99943 | Yes
Active | 2025W1-N11-WVM288643 | 288643 | 05KIBER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80949 | 0.99998 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77558 | 0.9718 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79102 | 0.9718 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8807 | 0.9718 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7756 | 0.97679 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80248 | 0.97679 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79119 | 0.98243 | Yes
Active | 2025W1-N11-WVM288701 | 288701 | 05MILEPOST | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80176 | 0.98257 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76313 | 0.96026 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78386 | 0.96026 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87837 | 0.96026 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76311 | 0.96686 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80644 | 0.96686 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78411 | 0.9835 | Yes
Active | 2025W1-N11-WVM288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80598 | 0.98398 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7721 | 0.97439 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78875 | 0.97439 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88342 | 0.97439 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77211 | 0.98004 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80414 | 0.98004 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78895 | 0.98726 | Yes
Active | 2025W1-N11-WVM288718 | 288718 | 05GILES | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80348 | 0.98875 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75513 | 0.96755 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77286 | 0.96755 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87551 | 0.96755 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75514 | 0.97452 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79389 | 0.97452 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77314 | 0.99003 | Yes
Active | 2025W1-N11-WVM288721 | 288721 | 05MACY | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7934 | 0.99055 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82541 | 0.97667 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.83542 | 0.97667 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89577 | 0.97667 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82543 | 0.97973 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83219 | 0.97973 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.83536 | 0.98477 | Yes
Active | 2025W1-N11-WVM288724 | 288724 | 05CHENOWETH | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8313 | 0.97903 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75775 | 0.95654 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77786 | 0.95654 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8733 | 0.95654 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75774 | 0.96306 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79966 | 0.96306 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77811 | 0.97939 | Yes
Active | 2025W1-N11-WVM288726 | 288726 | 05GREENCHPL | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7992 | 0.97989 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76499 | 0.96359 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78434 | 0.96359 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87989 | 0.96359 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76498 | 0.97012 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8065 | 0.97012 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78461 | 0.98566 | Yes
Active | 2025W1-N11-WVM288727 | 288727 | 05CURLEYS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80602 | 0.98627 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76305 | 0.96752 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78125 | 0.96752 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8795 | 0.96752 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76306 | 0.97404 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80178 | 0.97404 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78152 | 0.98807 | Yes
Active | 2025W1-N11-WVM288729 | 288729 | 05SOUDER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80126 | 0.98883 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79464 | 0.97358 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80819 | 0.97358 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89142 | 0.97358 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79469 | 0.97803 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81722 | 0.97803 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80838 | 0.98464 | Yes
Active | 2025W1-N11-WVM288776 | 288776 | 05CYPRUS34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81651 | 0.98314 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79582 | 0.97186 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80887 | 0.97186 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88873 | 0.97186 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79587 | 0.97619 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81731 | 0.97619 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80906 | 0.98317 | Yes
Active | 2025W1-N11-WVM288778 | 288778 | 05CYPRUS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81661 | 0.98121 | Yes
Active | 2025W1-N11-WVM288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91865 | 0.99791 | Yes
Active | 2025W1-N11-WVM288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9188 | 0.99838 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7603 | 0.9562 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77756 | 0.9562 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86842 | 0.9562 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76029 | 0.96153 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79267 | 0.96153 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77773 | 0.97163 | Yes
Active | 2025W1-N11-WVM288936 | 288936 | 05CELTIC | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79199 | 0.97326 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81032 | 0.9741 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.82147 | 0.9741 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89057 | 0.9741 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81035 | 0.97764 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.82264 | 0.97764 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82151 | 0.98329 | Yes
Active | 2025W1-N11-WVM289114 | 289114 | 05BIG PLAIN | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8218 | 0.97902 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76464 | 0.95692 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78408 | 0.95692 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87592 | 0.95692 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76461 | 0.9626 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80468 | 0.9626 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78428 | 0.97703 | Yes
Active | 2025W1-N11-WVM289528 | 289528 | 05MALIS | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8041 | 0.97888 | Yes
Active | 2025W1-N11-WVM290024 | 290024 | 05GOMER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.908 | 0.98201 | Yes
Active | 2025W1-N11-WVM290024 | 290024 | 05GOMER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88902 | 0.98184 | Yes
Active | 2025W1-N11-WVM290024 | 290024 | 05GOMER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9079 | 0.98184 | Yes
Active | 2025W1-N11-WVM290024 | 290024 | 05GOMER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88706 | 0.96455 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84179 | 0.98597 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85362 | 0.98597 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91952 | 0.98597 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84192 | 0.9883 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85623 | 0.9883 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85366 | 0.99433 | Yes
Active | 2025W1-N11-WVM290113 | 290113 | 05WESTFALL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8557 | 0.99162 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79464 | 0.97357 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80819 | 0.97357 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89142 | 0.97357 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79469 | 0.97802 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81722 | 0.97802 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80838 | 0.98462 | Yes
Active | 2025W1-N11-WVM290230 | 290230 | 05CYPRUS12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81651 | 0.98313 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75524 | 0.96773 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77284 | 0.96773 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87549 | 0.96773 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75525 | 0.97471 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79384 | 0.97471 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77312 | 0.9901 | Yes
Active | 2025W1-N11-WVM290239 | 290239 | 05HUMBOLDT | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79335 | 0.99062 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80536 | 0.97807 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.82056 | 0.97807 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90341 | 0.97807 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80546 | 0.98303 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.83549 | 0.98303 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82092 | 0.99109 | Yes
Active | 2025W1-N11-WVM290241 | 290241 | 05SIFFORD | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.83499 | 0.99069 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7628 | 0.97123 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78122 | 0.97123 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88189 | 0.97123 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76281 | 0.97805 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80266 | 0.97805 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7815 | 0.99371 | Yes
Active | 2025W1-N11-WVM290254 | 290254 | 05INNOVATION | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80216 | 0.99426 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81438 | 0.97295 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.82881 | 0.97295 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90481 | 0.97295 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.81444 | 0.9776 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84526 | 0.9776 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82946 | 0.98473 | Yes
Active | 2025W1-N11-WVM290313 | 290313 | 05CONESV_XFL | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84467 | 0.98428 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75523 | 0.96772 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77283 | 0.96772 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87548 | 0.96772 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75524 | 0.9747 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79383 | 0.9747 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77311 | 0.99009 | Yes
Active | 2025W1-N11-WVM290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79334 | 0.99061 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75525 | 0.96774 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77284 | 0.96774 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8755 | 0.96774 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75526 | 0.97472 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79385 | 0.97472 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77313 | 0.99011 | Yes
Active | 2025W1-N11-WVM290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79336 | 0.99062 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77274 | 0.96358 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78834 | 0.96358 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87596 | 0.96358 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77276 | 0.96856 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8007 | 0.96856 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78849 | 0.97627 | Yes
Active | 2025W1-N11-WVM290328 | 290328 | 05COSGRAY | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79997 | 0.97681 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77557 | 0.97231 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.79113 | 0.97231 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88119 | 0.97231 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7756 | 0.97734 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80283 | 0.97734 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7913 | 0.98294 | Yes
Active | 2025W1-N11-WVM290364 | 290364 | 05TRABUE2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80211 | 0.98319 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7558 | 0.968 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7736 | 0.968 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87614 | 0.968 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75581 | 0.97496 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79466 | 0.97496 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77388 | 0.99049 | Yes
Active | 2025W1-N11-WVM290377 | 290377 | 05BRIE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79417 | 0.99102 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75704 | 0.95391 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77422 | 0.95391 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86543 | 0.95391 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91859 | 0.95391 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75703 | 0.95927 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.78904 | 0.95927 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77438 | 0.96928 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78836 | 0.97071 | Yes
Active | 2025W1-N11-WVM290413 | 290413 | 05KILEVILLE | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91764 | 0.96569 | Yes
Active | 2025W1-N11-WVM290459 | 290459 | 05MT PERRYSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87226 | 0.99302 | Yes
Active | 2025W1-N11-WVM290459 | 290459 | 05MT PERRYSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.88594 | 0.99302 | Yes
Active | 2025W1-N11-WVM290459 | 290459 | 05MT PERRYSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87237 | 0.99559 | Yes
Active | 2025W1-N11-WVM290459 | 290459 | 05MT PERRYSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89796 | 0.99559 | Yes
Active | 2025W1-N11-WVM290459 | 290459 | 05MT PERRYSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88667 | 1.0011 | Yes
Active | 2025W1-N11-WVM290459 | 290459 | 05MT PERRYSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89748 | 1.0006 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76638 | 0.9684 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78361 | 0.9684 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87808 | 0.9684 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76639 | 0.97401 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79911 | 0.97401 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78381 | 0.98261 | Yes
Active | 2025W1-N11-WVM290499 | 290499 | 05SCHERERSS | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79846 | 0.98399 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76817 | 0.95954 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78562 | 0.95954 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87484 | 0.95954 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76816 | 0.96477 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80146 | 0.96477 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78578 | 0.97485 | Yes
Active | 2025W1-N11-WVM290516 | 290516 | 05CELTIC | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80076 | 0.97703 | Yes
Active | 2025W1-N11-WVM290534 | 290534 | 05LUTZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85017 | 0.98768 | Yes
Active | 2025W1-N11-WVM290534 | 290534 | 05LUTZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.86146 | 0.98768 | Yes
Active | 2025W1-N11-WVM290534 | 290534 | 05LUTZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8503 | 0.98976 | Yes
Active | 2025W1-N11-WVM290534 | 290534 | 05LUTZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86328 | 0.98976 | Yes
Active | 2025W1-N11-WVM290534 | 290534 | 05LUTZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.86148 | 0.99563 | Yes
Active | 2025W1-N11-WVM290534 | 290534 | 05LUTZ | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.86277 | 0.99276 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76571 | 0.96457 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78454 | 0.96457 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88033 | 0.96457 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76571 | 0.97113 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8066 | 0.97113 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78483 | 0.98634 | Yes
Active | 2025W1-N11-WVM290573 | 290573 | 05INNOVATION | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80611 | 0.9869 | Yes
Active | 2025W1-N11-WVM290607 | 290607 | 05SORENSN_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84979 | 0.94849 | Yes
Active | 2025W1-N11-WVM290607 | 290607 | 05SORENSN_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84968 | 0.94334 | Yes
Active | 2025W1-N11-WVM290607 | 290607 | 05SORENSN_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | 0.91894 | 0.94334 | Yes
Active | 2025W1-N11-WVM290607 | 290607 | 05SORENSN_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91791 | 0.95327 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91915 | 0.95725 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91931 | 0.95689 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91905 | 0.95675 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91728 | 0.95593 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91772 | 0.95593 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91774 | 0.95663 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.73785 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87138 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90203 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.90965 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91063 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18232_SRT-A | 0.9185 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91859 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | 0.91866 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6463_16757_SRT-A | 0.91949 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6457_16758_SRT-A | 0.9196 | 0.93005 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9152 | 0.95958 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91641 | 0.95579 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91718 | 0.95579 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91692 | 0.95607 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91795 | 0.95607 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91694 | 0.95422 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91871 | 0.95422 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91611 | 0.95427 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91855 | 0.95427 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91227 | 0.95201 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91585 | 0.95201 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91934 | 0.95829 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91566 | 0.955 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9159 | 0.955 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90977 | 0.9524 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91107 | 0.9524 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90619 | 0.96166 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.73775 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89421 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90345 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91005 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91072 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#730_590_SRT-A | 0.91816 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | 0.9185 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#16618_27957_SRT-A | 0.91902 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#10137_570_SRT-A | 0.9191 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#2891_19577_SRT-A | 0.91974 | 0.9267 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90933 | 0.94985 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91632 | 0.94985 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.87119 | 0.95438 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89389 | 0.95438 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91506 | 0.96001 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91819 | 0.95614 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91947 | 0.95614 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91784 | 0.95651 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#737_7791_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91961 | 0.95876 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90126 | 0.95078 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90337 | 0.95078 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91482 | 0.95517 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91816 | 0.95517 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9157 | 0.95532 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91611 | 0.95532 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91745 | 0.9567 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9185 | 0.9565 | Yes
Active | 2025W1-N11-WVM290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91818 | 0.9564 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91827 | 0.95657 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91841 | 0.95657 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91892 | 0.95731 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.73843 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86307 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90248 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.91059 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91116 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.91806 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18134_SRT-A | 0.9187 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18232_SRT-A | 0.91905 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | 0.91947 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91953 | 0.93066 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91653 | 0.96028 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91755 | 0.95643 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91773 | 0.95643 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91806 | 0.95671 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91851 | 0.95671 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91808 | 0.95485 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91929 | 0.95485 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91741 | 0.95505 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91928 | 0.95505 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91362 | 0.95282 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91661 | 0.95282 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91644 | 0.95563 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9168 | 0.95563 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91029 | 0.95303 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91223 | 0.95303 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90712 | 0.96242 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.73834 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.78886 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9046 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91155 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91188 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#734_8011_SRT-A | 0.91885 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#16635_SRT-A | 0.91891 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#730_590_SRT-A | 0.91926 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.91928 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | 0.91964 | 0.92781 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91085 | 0.95087 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91727 | 0.95087 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91609 | 0.96057 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91929 | 0.95675 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91901 | 0.95717 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.78839 | 0.96075 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9017 | 0.95142 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90451 | 0.95142 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91621 | 0.95601 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91897 | 0.95601 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91626 | 0.95598 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91727 | 0.95598 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91859 | 0.95735 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91965 | 0.95715 | Yes
Active | 2025W1-N11-WVM290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91933 | 0.95705 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91858 | 0.95668 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86326 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.87227 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90296 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9115 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.91837 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91902 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#18232_SRT-A | 0.91937 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | 0.91972 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#709_546_SRT-A | 0.91988 | 0.93086 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91807 | 0.95655 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91884 | 0.95683 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91958 | 0.95498 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91954 | 0.95513 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91688 | 0.95291 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91676 | 0.95574 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91065 | 0.95316 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91765 | 0.95101 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8721 | 0.95503 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90221 | 0.95158 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91923 | 0.95607 | Yes
Active | 2025W1-N11-WVM290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9166 | 0.95609 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75974 | 0.968 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77772 | 0.968 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87829 | 0.968 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75975 | 0.9748 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79885 | 0.9748 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.778 | 0.98998 | Yes
Active | 2025W1-N11-WVM290628 | 290628 | 05BADGER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79836 | 0.99055 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.77219 | 0.96403 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78775 | 0.96403 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87597 | 0.96403 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7722 | 0.96904 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80026 | 0.96904 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.7879 | 0.97646 | Yes
Active | 2025W1-N11-WVM290679 | 290679 | 05BEACON | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79954 | 0.97706 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7672 | 0.97471 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7858 | 0.97471 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88595 | 0.97471 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76721 | 0.9815 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80721 | 0.9815 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78607 | 0.99722 | Yes
Active | 2025W1-N11-WVM290690 | 290690 | 05GREENCHL12 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80671 | 0.99777 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76126 | 0.97038 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77956 | 0.97038 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88058 | 0.97038 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76126 | 0.97723 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.80092 | 0.97723 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77984 | 0.99288 | Yes
Active | 2025W1-N11-WVM290779 | 290779 | 05JORDEN | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.80042 | 0.99342 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75978 | 0.96807 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.7778 | 0.96807 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87839 | 0.96807 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75978 | 0.97488 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79894 | 0.97488 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77808 | 0.99012 | Yes
Active | 2025W1-N11-WVM290809 | 290809 | 05HORIZON | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79844 | 0.99068 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.76719 | 0.97471 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.78579 | 0.97471 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88595 | 0.97471 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.76719 | 0.98149 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.8072 | 0.98149 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78606 | 0.99722 | Yes
Active | 2025W1-N11-WVM290884 | 290884 | 05GREENCHL34 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8067 | 0.99777 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75572 | 0.96814 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77333 | 0.96814 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87595 | 0.96814 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75574 | 0.97512 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79435 | 0.97512 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77361 | 0.9905 | Yes
Active | 2025W1-N11-WVM290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79386 | 0.99102 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.75475 | 0.96729 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.77233 | 0.96729 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87501 | 0.96729 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.75476 | 0.97428 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79332 | 0.97428 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.77262 | 0.98967 | Yes
Active | 2025W1-N11-WVM290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79284 | 0.99019 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79487 | 0.97354 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80843 | 0.97354 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.89169 | 0.97354 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.79493 | 0.97799 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81747 | 0.97799 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80862 | 0.9846 | Yes
Active | 2025W1-N11-WVM290925 | 290925 | 05PARSONS2 | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81675 | 0.98311 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.8004 | 0.96596 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84821 | 0.96596 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.88545 | 0.96596 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80031 | 0.96748 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.81797 | 0.96748 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84812 | 0.97906 | Yes
Active | 2025W1-N11-WVM290984 | 290984 | 05BOKESCRK | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.81656 | 0.97551 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.85029 | 0.98386 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.85934 | 0.98386 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90775 | 0.98386 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85029 | 0.98622 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.85041 | 0.98622 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.85917 | 0.99057 | Yes
Active | 2025W1-N11-WVM291017 | 291017 | 09FAYETT | 345 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84948 | 0.98318 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.88369 | 0.98098 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90743 | 0.98098 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91867 | 0.98098 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.87172 | 0.98132 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.88363 | 0.98132 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90723 | 0.98648 | Yes
Active | 2025W1-N11-WVM291032 | 291032 | 09KTLRSVL | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.87012 | 0.97313 | Yes
Active | 2025W1-N11-WVM313054 | 313054 | 6PLYMOUTH | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.88039 | 1.0042 | Yes
Active | 2025W1-N11-WVM313054 | 313054 | 6PLYMOUTH | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.88039 | 0.99623 | Yes
Active | 2025W1-N11-WVM314203 | 314203 | 6MACKEYS | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.88119 | 1.0104 | Yes
Active | 2025W1-N11-WVM314203 | 314203 | 6MACKEYS | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.88119 | 0.99678 | Yes
Active | 2025W1-N11-WVM314594 | 314594 | 6PLYMOUTH TP | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.8804 | 1.0042 | Yes
Active | 2025W1-N11-WVM314594 | 314594 | 6PLYMOUTH TP | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.8804 | 0.99624 | Yes
Active | 2025W1-N11-WVM314616 | 314616 | 6TRWBRDG | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2126_SRT-A | 0.86644 | 1.0026 | Yes
Active | 2025W1-N11-WVM314616 | 314616 | 6TRWBRDG | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.88026 | 1.003 | Yes
Active | 2025W1-N11-WVM314616 | 314616 | 6TRWBRDG | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2126_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.8664 | 0.99351 | Yes
Active | 2025W1-N11-WVM314616 | 314616 | 6TRWBRDG | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.88025 | 0.99614 | Yes
Active | 2025W1-N11-WVM315725 | 315725 | AD1-074 MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2126_SRT-A | 0.86864 | 1.0045 | Yes
Active | 2025W1-N11-WVM315725 | 315725 | AD1-074 MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.88247 | 1.0048 | Yes
Active | 2025W1-N11-WVM315725 | 315725 | AD1-074 MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2126_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.8686 | 0.99575 | Yes
Active | 2025W1-N11-WVM315725 | 315725 | AD1-074 MAIN | 230 | 345 | 0.93 | 1.05 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.88246 | 0.99838 | Yes
Active | 2025W1-N11-WVM940610 | 940610 | AE2-048 TAP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89493 | 0.99611 | Yes
Active | 2025W1-N11-WVM940610 | 940610 | AE2-048 TAP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90392 | 0.99611 | Yes
Active | 2025W1-N11-WVM940610 | 940610 | AE2-048 TAP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89506 | 1 | Yes
Active | 2025W1-N11-WVM940610 | 940610 | AE2-048 TAP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9129 | 1 | Yes
Active | 2025W1-N11-WVM940610 | 940610 | AE2-048 TAP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90429 | 1.0024 | Yes
Active | 2025W1-N11-WVM940610 | 940610 | AE2-048 TAP | 345 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91286 | 1.0025 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.7863 | 0.95147 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.80138 | 0.95147 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.86114 | 0.95147 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91939 | 0.95147 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89011 | 0.95433 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8913 | 0.95433 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90102 | 0.95433 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.78629 | 0.9528 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.79372 | 0.9528 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.80122 | 0.96023 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.79266 | 0.9541 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91851 | 0.95689 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89006 | 0.96416 | Yes
Active | 2025W1-N11-WVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89125 | 0.95302 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.82857 | 0.99014 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.84232 | 0.99014 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91694 | 0.99014 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.82868 | 0.99342 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.84934 | 0.99342 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.84239 | 0.9998 | Yes
Active | 2025W1-N11-WVM960800 | 960800 | AF2-371 TAP | 138 | 205 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.84881 | 0.99854 | Yes

## Volt Drop
PJM N-1-1 Voltage Drop Result (Winter 2030 Case)
FG # Status | FG# | Bus # | Name | KV | Area | Vdrop(%) | Contingency 1 | Contingency 2 | BaseVolt | ContVolt | % Vdrop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2025W1-N11-WVD207959 | 207959 | EPAL TR1 | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 1.0062 | 0.89912 | 10.707 | Yes
Active | 2025W1-N11-WVD207959 | 207959 | EPAL TR1 | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 1.0062 | 0.89912 | 10.707 | Yes
Active | 2025W1-N11-WVD207960 | 207960 | EPAL TR2 | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 1.0062 | 0.89894 | 10.724 | Yes
Active | 2025W1-N11-WVD207960 | 207960 | EPAL TR2 | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 1.0062 | 0.89894 | 10.724 | Yes
Active | 2025W1-N11-WVD207963 | 207963 | SLYK | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.99305 | 0.84787 | 14.518 | Yes
Active | 2025W1-N11-WVD207963 | 207963 | SLYK | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.99305 | 0.84787 | 14.518 | Yes
Active | 2025W1-N11-WVD207966 | 207966 | BWAY | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.99288 | 0.84767 | 14.521 | Yes
Active | 2025W1-N11-WVD207966 | 207966 | BWAY | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.99288 | 0.84767 | 14.521 | Yes
Active | 2025W1-N11-WVD207967 | 207967 | LOFT | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.98939 | 0.84411 | 14.528 | Yes
Active | 2025W1-N11-WVD207967 | 207967 | LOFT | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.98939 | 0.84411 | 14.528 | Yes
Active | 2025W1-N11-WVD207969 | 207969 | TRES | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.99352 | 0.849 | 14.452 | Yes
Active | 2025W1-N11-WVD207969 | 207969 | TRES | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.99352 | 0.849 | 14.452 | Yes
Active | 2025W1-N11-WVD208072 | 208072 | SIEG | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 1.0058 | 0.9235 | 8.226 | Yes
Active | 2025W1-N11-WVD208072 | 208072 | SIEG | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 1.0058 | 0.9235 | 8.226 | Yes
Active | 2025W1-N11-WVD210406 | 210406 | APPE TP | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99779 | 0.88243 | 11.536 | Yes
Active | 2025W1-N11-WVD210406 | 210406 | APPE TP | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97821 | 0.89502 | 8.319 | Yes
Active | 2025W1-N11-WVD210406 | 210406 | APPE TP | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99367 | 0.84936 | 14.431 | Yes
Active | 2025W1-N11-WVD210406 | 210406 | APPE TP | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99632 | 0.86592 | 13.04 | Yes
Active | 2025W1-N11-WVD210407 | 210407 | APPE | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99757 | 0.88217 | 11.54 | Yes
Active | 2025W1-N11-WVD210407 | 210407 | APPE | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97799 | 0.89477 | 8.322 | Yes
Active | 2025W1-N11-WVD210407 | 210407 | APPE | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99345 | 0.84908 | 14.437 | Yes
Active | 2025W1-N11-WVD210407 | 210407 | APPE | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99611 | 0.86566 | 13.045 | Yes
Active | 2025W1-N11-WVD210432 | 210432 | BART TP1 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99837 | 0.87039 | 12.798 | Yes
Active | 2025W1-N11-WVD210432 | 210432 | BART TP1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99882 | 0.87254 | 12.629 | Yes
Active | 2025W1-N11-WVD210432 | 210432 | BART TP1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97638 | 0.89401 | 8.237 | Yes
Active | 2025W1-N11-WVD210432 | 210432 | BART TP1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.9962 | 0.84541 | 15.079 | Yes
Active | 2025W1-N11-WVD210432 | 210432 | BART TP1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99748 | 0.85538 | 14.21 | Yes
Active | 2025W1-N11-WVD210433 | 210433 | BART 1 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.9977 | 0.86952 | 12.818 | Yes
Active | 2025W1-N11-WVD210433 | 210433 | BART 1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99815 | 0.87167 | 12.648 | Yes
Active | 2025W1-N11-WVD210433 | 210433 | BART 1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97568 | 0.89318 | 8.25 | Yes
Active | 2025W1-N11-WVD210433 | 210433 | BART 1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99553 | 0.84449 | 15.104 | Yes
Active | 2025W1-N11-WVD210433 | 210433 | BART 1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99681 | 0.85449 | 14.232 | Yes
Active | 2025W1-N11-WVD210434 | 210434 | BART TP2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99879 | 0.87095 | 12.784 | Yes
Active | 2025W1-N11-WVD210434 | 210434 | BART TP2 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99925 | 0.87309 | 12.616 | Yes
Active | 2025W1-N11-WVD210434 | 210434 | BART TP2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97682 | 0.89453 | 8.229 | Yes
Active | 2025W1-N11-WVD210434 | 210434 | BART TP2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99663 | 0.846 | 15.062 | Yes
Active | 2025W1-N11-WVD210434 | 210434 | BART TP2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99791 | 0.85595 | 14.196 | Yes
Active | 2025W1-N11-WVD210436 | 210436 | BART 2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99875 | 0.8709 | 12.786 | Yes
Active | 2025W1-N11-WVD210436 | 210436 | BART 2 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99921 | 0.87304 | 12.617 | Yes
Active | 2025W1-N11-WVD210436 | 210436 | BART 2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97678 | 0.89448 | 8.229 | Yes
Active | 2025W1-N11-WVD210436 | 210436 | BART 2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99659 | 0.84595 | 15.064 | Yes
Active | 2025W1-N11-WVD210436 | 210436 | BART 2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99787 | 0.85589 | 14.197 | Yes
Active | 2025W1-N11-WVD210596 | 210596 | EFMO TP1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0013 | 0.90616 | 9.516 | Yes
Active | 2025W1-N11-WVD210596 | 210596 | EFMO TP1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.98409 | 0.89466 | 8.943 | Yes
Active | 2025W1-N11-WVD210596 | 210596 | EFMO TP1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99339 | 0.84895 | 14.445 | Yes
Active | 2025W1-N11-WVD210596 | 210596 | EFMO TP1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0003 | 0.8922 | 10.807 | Yes
Active | 2025W1-N11-WVD210597 | 210597 | EFMO | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.9992 | 0.9023 | 9.69 | Yes
Active | 2025W1-N11-WVD210597 | 210597 | EFMO | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.9822 | 0.90137 | 8.083 | Yes
Active | 2025W1-N11-WVD210597 | 210597 | EFMO | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99725 | 0.88217 | 11.507 | Yes
Active | 2025W1-N11-WVD210597 | 210597 | EFMO | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99413 | 0.85774 | 13.639 | Yes
Active | 2025W1-N11-WVD210599 | 210599 | EFMO TP2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99973 | 0.90295 | 9.678 | Yes
Active | 2025W1-N11-WVD210599 | 210599 | EFMO TP2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.98275 | 0.90203 | 8.072 | Yes
Active | 2025W1-N11-WVD210599 | 210599 | EFMO TP2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99778 | 0.88286 | 11.492 | Yes
Active | 2025W1-N11-WVD210599 | 210599 | EFMO TP2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99466 | 0.85845 | 13.622 | Yes
Active | 2025W1-N11-WVD210600 | 210600 | EFMO DC | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99972 | 0.90293 | 9.679 | Yes
Active | 2025W1-N11-WVD210600 | 210600 | EFMO DC | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.98273 | 0.90201 | 8.072 | Yes
Active | 2025W1-N11-WVD210600 | 210600 | EFMO DC | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99777 | 0.88284 | 11.493 | Yes
Active | 2025W1-N11-WVD210600 | 210600 | EFMO DC | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99465 | 0.85843 | 13.622 | Yes
Active | 2025W1-N11-WVD210693 | 210693 | GILB 1CB | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0027 | 0.91528 | 8.739 | Yes
Active | 2025W1-N11-WVD210693 | 210693 | GILB 1CB | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.98643 | 0.89467 | 9.176 | Yes
Active | 2025W1-N11-WVD210693 | 210693 | GILB 1CB | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.9934 | 0.84896 | 14.445 | Yes
Active | 2025W1-N11-WVD210693 | 210693 | GILB 1CB | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0018 | 0.90239 | 9.937 | Yes
Active | 2025W1-N11-WVD210694 | 210694 | GILB 2CB | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0008 | 0.91186 | 8.898 | Yes
Active | 2025W1-N11-WVD210694 | 210694 | GILB 2CB | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100133_SRT-A | 0.98477 | 0.90204 | 8.273 | Yes
Active | 2025W1-N11-WVD210694 | 210694 | GILB 2CB | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99906 | 0.8933 | 10.575 | Yes
Active | 2025W1-N11-WVD210694 | 210694 | GILB 2CB | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99467 | 0.85846 | 13.622 | Yes
Active | 2025W1-N11-WVD210695 | 210695 | GILB 2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0008 | 0.91191 | 8.893 | Yes
Active | 2025W1-N11-WVD210695 | 210695 | GILB 2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99906 | 0.89337 | 10.57 | Yes
Active | 2025W1-N11-WVD210696 | 210696 | GILB 1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0027 | 0.91533 | 8.734 | Yes
Active | 2025W1-N11-WVD210696 | 210696 | GILB 1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0018 | 0.90245 | 9.932 | Yes
Active | 2025W1-N11-WVD210748 | 210748 | JKSN | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99658 | 0.87462 | 12.196 | Yes
Active | 2025W1-N11-WVD210748 | 210748 | JKSN | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99711 | 0.87675 | 12.036 | Yes
Active | 2025W1-N11-WVD210748 | 210748 | JKSN | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.977 | 0.89549 | 8.151 | Yes
Active | 2025W1-N11-WVD210748 | 210748 | JKSN | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99405 | 0.84987 | 14.418 | Yes
Active | 2025W1-N11-WVD210748 | 210748 | JKSN | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99553 | 0.85969 | 13.585 | Yes
Active | 2025W1-N11-WVD210896 | 210896 | MCMI 2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99809 | 0.88869 | 10.94 | Yes
Active | 2025W1-N11-WVD210896 | 210896 | MCMI 2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99585 | 0.86619 | 12.966 | Yes
Active | 2025W1-N11-WVD210896 | 210896 | MCMI 2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99493 | 0.85885 | 13.608 | Yes
Active | 2025W1-N11-WVD210897 | 210897 | MCMI 1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99896 | 0.89112 | 10.784 | Yes
Active | 2025W1-N11-WVD210897 | 210897 | MCMI 1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.9802 | 0.89461 | 8.559 | Yes
Active | 2025W1-N11-WVD210897 | 210897 | MCMI 1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99334 | 0.8489 | 14.444 | Yes
Active | 2025W1-N11-WVD210897 | 210897 | MCMI 1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99764 | 0.8755 | 12.214 | Yes
Active | 2025W1-N11-WVD210937 | 210937 | MONR | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0061 | 0.86699 | 13.907 | Yes
Active | 2025W1-N11-WVD210937 | 210937 | MONR | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0064 | 0.86915 | 13.721 | Yes
Active | 2025W1-N11-WVD210937 | 210937 | MONR | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97689 | 0.89375 | 8.313 | Yes
Active | 2025W1-N11-WVD210937 | 210937 | MONR | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.0047 | 0.84183 | 16.288 | Yes
Active | 2025W1-N11-WVD210937 | 210937 | MONR | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0056 | 0.85191 | 15.365 | Yes
Active | 2025W1-N11-WVD210989 | 210989 | NSTR 1 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0024 | 0.86791 | 13.452 | Yes
Active | 2025W1-N11-WVD210989 | 210989 | NSTR 1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0028 | 0.87006 | 13.272 | Yes
Active | 2025W1-N11-WVD210989 | 210989 | NSTR 1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97763 | 0.89463 | 8.3 | Yes
Active | 2025W1-N11-WVD210989 | 210989 | NSTR 1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.0007 | 0.8428 | 15.792 | Yes
Active | 2025W1-N11-WVD210989 | 210989 | NSTR 1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0017 | 0.85285 | 14.89 | Yes
Active | 2025W1-N11-WVD210990 | 210990 | NSTR 2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0022 | 0.86767 | 13.451 | Yes
Active | 2025W1-N11-WVD210990 | 210990 | NSTR 2 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0026 | 0.86983 | 13.272 | Yes
Active | 2025W1-N11-WVD210990 | 210990 | NSTR 2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97743 | 0.8944 | 8.303 | Yes
Active | 2025W1-N11-WVD210990 | 210990 | NSTR 2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.0005 | 0.84255 | 15.792 | Yes
Active | 2025W1-N11-WVD210990 | 210990 | NSTR 2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0015 | 0.85261 | 14.89 | Yes
Active | 2025W1-N11-WVD210991 | 210991 | NSTR CB1 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0024 | 0.86791 | 13.451 | Yes
Active | 2025W1-N11-WVD210991 | 210991 | NSTR CB1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0028 | 0.87007 | 13.272 | Yes
Active | 2025W1-N11-WVD210991 | 210991 | NSTR CB1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97762 | 0.89462 | 8.3 | Yes
Active | 2025W1-N11-WVD210991 | 210991 | NSTR CB1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.0007 | 0.8428 | 15.791 | Yes
Active | 2025W1-N11-WVD210991 | 210991 | NSTR CB1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0017 | 0.85286 | 14.89 | Yes
Active | 2025W1-N11-WVD210992 | 210992 | NSTR CB2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0022 | 0.86768 | 13.451 | Yes
Active | 2025W1-N11-WVD210992 | 210992 | NSTR CB2 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0026 | 0.86983 | 13.272 | Yes
Active | 2025W1-N11-WVD210992 | 210992 | NSTR CB2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97742 | 0.89439 | 8.303 | Yes
Active | 2025W1-N11-WVD210992 | 210992 | NSTR CB2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.0005 | 0.84256 | 15.792 | Yes
Active | 2025W1-N11-WVD210992 | 210992 | NSTR CB2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0015 | 0.85261 | 14.89 | Yes
Active | 2025W1-N11-WVD211231 | 211231 | STRO 2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0047 | 0.86705 | 13.76 | Yes
Active | 2025W1-N11-WVD211231 | 211231 | STRO 2 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.005 | 0.86921 | 13.576 | Yes
Active | 2025W1-N11-WVD211231 | 211231 | STRO 2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97693 | 0.89381 | 8.312 | Yes
Active | 2025W1-N11-WVD211231 | 211231 | STRO 2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.0032 | 0.84189 | 16.128 | Yes
Active | 2025W1-N11-WVD211231 | 211231 | STRO 2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.0041 | 0.85197 | 15.212 | Yes
Active | 2025W1-N11-WVD211232 | 211232 | STRO 1 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 1.0045 | 0.86692 | 13.76 | Yes
Active | 2025W1-N11-WVD211232 | 211232 | STRO 1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 1.0048 | 0.86908 | 13.576 | Yes
Active | 2025W1-N11-WVD211232 | 211232 | STRO 1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97683 | 0.89369 | 8.314 | Yes
Active | 2025W1-N11-WVD211232 | 211232 | STRO 1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 1.003 | 0.84176 | 16.129 | Yes
Active | 2025W1-N11-WVD211232 | 211232 | STRO 1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 1.004 | 0.85185 | 15.212 | Yes
Active | 2025W1-N11-WVD211248 | 211248 | TANN 1 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99748 | 0.87168 | 12.58 | Yes
Active | 2025W1-N11-WVD211248 | 211248 | TANN 1 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99796 | 0.87382 | 12.414 | Yes
Active | 2025W1-N11-WVD211248 | 211248 | TANN 1 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97639 | 0.89429 | 8.209 | Yes
Active | 2025W1-N11-WVD211248 | 211248 | TANN 1 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99518 | 0.84677 | 14.84 | Yes
Active | 2025W1-N11-WVD211248 | 211248 | TANN 1 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99653 | 0.85669 | 13.984 | Yes
Active | 2025W1-N11-WVD211249 | 211249 | TANN 2 | 138 | 229 | 8 | PL_02_P12_103162_SRT-A | PL_22_P12_000231_SRT-A | 0.99773 | 0.87201 | 12.572 | Yes
Active | 2025W1-N11-WVD211249 | 211249 | TANN 2 | 138 | 229 | 8 | PL_02_P12_103165_SRT-A | PL_22_P12_000231_SRT-A | 0.99821 | 0.87414 | 12.407 | Yes
Active | 2025W1-N11-WVD211249 | 211249 | TANN 2 | 138 | 229 | 8 | PL_22_P12_000231_SRT-A | PL_22_P12_100132_SRT-A | 0.97663 | 0.8946 | 8.204 | Yes
Active | 2025W1-N11-WVD211249 | 211249 | TANN 2 | 138 | 229 | 8 | PL_22_P12_100132_SRT-A | PL_22_P12_000231_SRT-A | 0.99543 | 0.84712 | 14.831 | Yes
Active | 2025W1-N11-WVD211249 | 211249 | TANN 2 | 138 | 229 | 8 | PL_22_P12_100133_SRT-A | PL_22_P12_000231_SRT-A | 0.99678 | 0.85702 | 13.976 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96807 | 0.80193 | 16.614 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96665 | 0.79837 | 16.829 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96659 | 0.79962 | 16.696 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96471 | 0.79672 | 16.799 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95329 | 0.758 | 19.529 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95329 | 0.76079 | 19.25 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95329 | 0.76937 | 18.393 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95329 | 0.7801 | 17.319 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95329 | 0.78613 | 16.717 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97163 | 0.77926 | 19.237 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9677 | 0.80336 | 16.434 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96808 | 0.80339 | 16.47 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96797 | 0.80168 | 16.629 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.94489 | 0.83443 | 11.047 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94489 | 0.83449 | 11.04 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.94489 | 0.83527 | 10.962 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96488 | 0.79669 | 16.82 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96523 | 0.79506 | 17.017 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96198 | 0.78577 | 17.621 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96198 | 0.79212 | 16.986 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97001 | 0.77419 | 19.583 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9526 | 0.75315 | 19.945 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9526 | 0.75532 | 19.728 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9526 | 0.78301 | 16.959 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9526 | 0.78986 | 16.274 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96161 | 0.8489 | 11.271 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96035 | 0.76459 | 19.576 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97153 | 0.79636 | 17.517 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96707 | 0.79958 | 16.75 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95306 | 0.75432 | 19.874 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95306 | 0.75906 | 19.399 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9692 | 0.78679 | 18.241 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95606 | 0.7799 | 17.616 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95606 | 0.78527 | 17.079 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97035 | 0.8703 | 10.005 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.96095 | 0.83106 | 12.989 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95263 | 0.80414 | 14.849 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95263 | 0.83018 | 12.244 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95263 | 0.83361 | 11.902 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95131 | 0.80653 | 14.478 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95131 | 0.83111 | 12.02 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95131 | 0.83435 | 11.696 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.95357 | 0.79731 | 15.626 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.95357 | 0.80638 | 14.719 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95357 | 0.8295 | 12.407 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96246 | 0.79572 | 16.674 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96841 | 0.80393 | 16.448 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.966 | 0.79728 | 16.872 | Yes
Active | 2025W1-N11-WVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96572 | 0.79668 | 16.905 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97228 | 0.80613 | 16.615 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97218 | 0.80387 | 16.831 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97121 | 0.8049 | 16.631 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97261 | 0.79711 | 17.55 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95255 | 0.74455 | 20.801 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95255 | 0.76301 | 18.954 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95255 | 0.76519 | 18.736 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95255 | 0.77579 | 17.677 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95255 | 0.79084 | 16.171 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97596 | 0.77189 | 20.407 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9713 | 0.79981 | 17.149 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97173 | 0.80013 | 17.16 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97248 | 0.80632 | 16.616 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9691 | 0.80014 | 16.896 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9703 | 0.79894 | 17.136 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9676 | 0.78929 | 17.832 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9676 | 0.79924 | 16.836 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97589 | 0.77069 | 20.52 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95629 | 0.74334 | 21.295 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95629 | 0.7609 | 19.539 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95629 | 0.77698 | 17.931 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95629 | 0.80023 | 15.606 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96836 | 0.86234 | 10.603 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96576 | 0.75907 | 20.669 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97551 | 0.79981 | 17.569 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97128 | 0.80322 | 16.806 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96599 | 0.76213 | 20.386 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96599 | 0.7648 | 20.119 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97811 | 0.79622 | 18.189 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96461 | 0.78574 | 17.887 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96461 | 0.79474 | 16.987 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97047 | 0.79574 | 17.473 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97256 | 0.80138 | 17.118 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9718 | 0.80323 | 16.857 | Yes
Active | 2025W1-N11-WVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97161 | 0.80231 | 16.93 | Yes
Active | 2025W1-N11-WVD238600 | 238600 | 02CAIRNS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97172 | 0.86964 | 10.208 | Yes
Active | 2025W1-N11-WVD238600 | 238600 | 02CAIRNS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97339 | 0.86769 | 10.569 | Yes
Active | 2025W1-N11-WVD238600 | 238600 | 02CAIRNS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97339 | 0.8677 | 10.569 | Yes
Active | 2025W1-N11-WVD238600 | 238600 | 02CAIRNS | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97624 | 0.87606 | 10.018 | Yes
Active | 2025W1-N11-WVD238600 | 238600 | 02CAIRNS | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97342 | 0.8703 | 10.312 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97799 | 0.86955 | 10.844 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97811 | 0.86768 | 11.044 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9774 | 0.86757 | 10.983 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97828 | 0.86275 | 11.553 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96975 | 0.82798 | 14.177 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96975 | 0.83432 | 13.542 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96975 | 0.84148 | 12.826 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96975 | 0.85058 | 11.917 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96975 | 0.85987 | 10.988 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96975 | 0.86335 | 10.639 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96975 | 0.86514 | 10.461 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97974 | 0.84992 | 12.982 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97756 | 0.8647 | 11.286 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97777 | 0.8649 | 11.287 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97677 | 0.86224 | 11.453 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97385 | 0.85983 | 11.402 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97695 | 0.86324 | 11.37 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97548 | 0.85627 | 11.92 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97548 | 0.86418 | 11.13 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97935 | 0.84244 | 13.691 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96949 | 0.82362 | 14.587 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96949 | 0.82745 | 14.204 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96949 | 0.85433 | 11.516 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96949 | 0.86702 | 10.247 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97418 | 0.83454 | 13.964 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97999 | 0.8638 | 11.619 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97746 | 0.86775 | 10.971 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96987 | 0.8299 | 13.997 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96987 | 0.83181 | 13.806 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97887 | 0.85602 | 12.285 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97427 | 0.85532 | 11.895 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97427 | 0.86251 | 11.176 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97727 | 0.86201 | 11.526 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97821 | 0.86573 | 11.248 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97793 | 0.86722 | 11.071 | Yes
Active | 2025W1-N11-WVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97784 | 0.86663 | 11.122 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97281 | 0.80963 | 16.318 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97133 | 0.80609 | 16.524 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97133 | 0.80729 | 16.404 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96918 | 0.80486 | 16.432 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95826 | 0.766 | 19.227 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95826 | 0.76812 | 19.014 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95826 | 0.7773 | 18.097 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95826 | 0.78792 | 17.035 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95826 | 0.79384 | 16.442 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97629 | 0.78721 | 18.908 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9725 | 0.81181 | 16.068 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97286 | 0.81181 | 16.105 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97269 | 0.80935 | 16.335 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.95096 | 0.84095 | 11.001 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95096 | 0.84202 | 10.894 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.95096 | 0.84665 | 10.431 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96966 | 0.8044 | 16.527 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96997 | 0.80279 | 16.718 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96671 | 0.79353 | 17.318 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96671 | 0.79973 | 16.698 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97465 | 0.782 | 19.264 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95749 | 0.76035 | 19.714 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95749 | 0.7633 | 19.419 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95749 | 0.79092 | 16.657 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95749 | 0.7974 | 16.009 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96626 | 0.85573 | 11.053 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96508 | 0.77254 | 19.255 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9762 | 0.80411 | 17.21 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97183 | 0.8073 | 16.454 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95752 | 0.76155 | 19.597 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95752 | 0.76641 | 19.111 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9737 | 0.7942 | 17.949 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96074 | 0.78761 | 17.313 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96074 | 0.79284 | 16.79 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.96601 | 0.8425 | 12.351 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95729 | 0.80806 | 14.923 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95729 | 0.83546 | 12.183 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95729 | 0.84014 | 11.715 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95608 | 0.81058 | 14.549 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95608 | 0.83652 | 11.956 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95608 | 0.84104 | 11.504 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.95798 | 0.80099 | 15.698 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.95798 | 0.81043 | 14.755 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95798 | 0.83703 | 12.094 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96702 | 0.80391 | 16.311 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97313 | 0.8123 | 16.083 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97068 | 0.80497 | 16.571 | Yes
Active | 2025W1-N11-WVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97041 | 0.80439 | 16.601 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.84685 | 14.605 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.84503 | 14.8 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99201 | 0.84518 | 14.683 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.83917 | 15.425 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97623 | 0.78998 | 18.625 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97623 | 0.80273 | 17.35 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97623 | 0.80837 | 16.786 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97623 | 0.81892 | 15.731 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97623 | 0.83453 | 14.17 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97623 | 0.83525 | 14.098 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97623 | 0.83858 | 13.765 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99565 | 0.81902 | 17.663 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99241 | 0.84171 | 15.07 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99273 | 0.84197 | 15.076 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.84426 | 14.871 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.83928 | 15.024 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99157 | 0.84014 | 15.143 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98945 | 0.83139 | 15.805 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98945 | 0.84147 | 14.798 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.81262 | 18.249 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97995 | 0.7882 | 19.175 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97995 | 0.79852 | 18.143 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97995 | 0.82442 | 15.553 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97995 | 0.84391 | 13.604 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98766 | 0.80353 | 18.414 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99584 | 0.84112 | 15.472 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.84434 | 14.776 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98386 | 0.8003 | 18.356 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98386 | 0.80217 | 18.169 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99555 | 0.83291 | 16.264 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98739 | 0.82914 | 15.824 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98739 | 0.83835 | 14.904 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.83817 | 15.376 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.84304 | 15.034 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99274 | 0.84443 | 14.831 | Yes
Active | 2025W1-N11-WVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.84365 | 14.895 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.85341 | 13.935 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.85161 | 14.129 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99192 | 0.85165 | 14.026 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99325 | 0.84594 | 14.731 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97711 | 0.79873 | 17.838 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97711 | 0.80986 | 16.725 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97711 | 0.81632 | 16.079 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97711 | 0.8266 | 15.052 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97711 | 0.84087 | 13.625 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97711 | 0.84251 | 13.461 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97711 | 0.84551 | 13.16 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9953 | 0.82732 | 16.797 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.8484 | 14.391 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99261 | 0.84864 | 14.397 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99265 | 0.84993 | 14.272 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98923 | 0.84538 | 14.385 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9915 | 0.84677 | 14.473 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.83833 | 15.117 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9895 | 0.84816 | 14.134 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.82027 | 17.448 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98061 | 0.79681 | 18.38 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98061 | 0.80557 | 17.503 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98061 | 0.83255 | 14.806 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98061 | 0.85072 | 12.988 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98778 | 0.8114 | 17.638 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99555 | 0.8477 | 14.785 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99201 | 0.85103 | 14.098 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98352 | 0.80751 | 17.601 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98352 | 0.80928 | 17.425 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.83917 | 15.573 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98761 | 0.83635 | 15.126 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98761 | 0.84533 | 14.227 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.845 | 14.686 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99321 | 0.84966 | 14.355 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99263 | 0.85103 | 14.159 | Yes
Active | 2025W1-N11-WVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9925 | 0.85028 | 14.222 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95268 | 0.7769 | 17.578 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95158 | 0.77343 | 17.816 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95118 | 0.77474 | 17.644 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95069 | 0.77074 | 17.995 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95178 | 0.85131 | 10.047 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93724 | 0.73189 | 20.535 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93724 | 0.73746 | 19.978 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.93724 | 0.74368 | 19.356 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93724 | 0.7547 | 18.254 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93724 | 0.76141 | 17.583 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95652 | 0.75321 | 20.33 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95233 | 0.77607 | 17.626 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95279 | 0.7762 | 17.66 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95263 | 0.77678 | 17.585 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.92536 | 0.79947 | 12.59 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.92536 | 0.8107 | 11.467 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.92536 | 0.81232 | 11.304 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.92536 | 0.8241 | 10.126 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94936 | 0.77164 | 17.772 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94988 | 0.77001 | 17.987 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94677 | 0.76069 | 18.607 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94677 | 0.76761 | 17.916 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95504 | 0.74874 | 20.63 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93683 | 0.72926 | 20.757 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93683 | 0.73033 | 20.65 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.93683 | 0.75713 | 17.97 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93683 | 0.7658 | 17.103 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94667 | 0.82689 | 11.978 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94511 | 0.73881 | 20.63 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95633 | 0.77118 | 18.515 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95161 | 0.77448 | 17.713 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93908 | 0.73142 | 20.766 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93908 | 0.73568 | 20.339 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9548 | 0.76293 | 19.187 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94118 | 0.75516 | 18.602 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94118 | 0.76107 | 18.011 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95511 | 0.84863 | 10.648 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95178 | 0.85131 | 10.047 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94478 | 0.79501 | 14.977 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93667 | 0.79125 | 14.541 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93667 | 0.81151 | 12.516 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93667 | 0.81234 | 12.433 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93497 | 0.79316 | 14.181 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93497 | 0.81171 | 12.326 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93497 | 0.81278 | 12.218 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93934 | 0.78535 | 15.399 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93934 | 0.79302 | 14.632 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93934 | 0.80569 | 13.365 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94808 | 0.76951 | 17.857 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95333 | 0.77695 | 17.637 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95092 | 0.77246 | 17.846 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95279 | 0.85173 | 10.106 | Yes
Active | 2025W1-N11-WVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95063 | 0.77175 | 17.887 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9939 | 0.89709 | 9.681 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99404 | 0.89498 | 9.906 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.89491 | 9.859 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.89033 | 10.382 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98539 | 0.8575 | 12.789 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98539 | 0.85998 | 12.54 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98539 | 0.86885 | 11.654 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98539 | 0.87771 | 10.768 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98539 | 0.88384 | 10.154 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98539 | 0.88879 | 9.659 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98539 | 0.89009 | 9.53 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99542 | 0.8794 | 11.602 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99356 | 0.89213 | 10.143 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99373 | 0.89231 | 10.142 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.88735 | 10.527 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98933 | 0.8859 | 10.344 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99302 | 0.89056 | 10.247 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.88408 | 10.774 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99182 | 0.89085 | 10.096 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.87229 | 12.273 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98733 | 0.85519 | 13.214 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98733 | 0.85577 | 13.157 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98733 | 0.88376 | 10.357 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98733 | 0.89407 | 9.326 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.86462 | 12.586 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99555 | 0.89087 | 10.469 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99347 | 0.89552 | 9.795 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98496 | 0.858 | 12.696 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98496 | 0.86049 | 12.447 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.8829 | 11.08 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99087 | 0.88361 | 10.727 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99087 | 0.88971 | 10.116 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.88967 | 10.367 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.89308 | 10.101 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.89456 | 9.933 | Yes
Active | 2025W1-N11-WVD238745 | 238745 | 02GALION | 345 | 202 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.89402 | 9.981 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98191 | 0.88188 | 10.003 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98203 | 0.87995 | 10.207 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98139 | 0.87981 | 10.159 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.87536 | 10.682 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97315 | 0.84173 | 13.141 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97315 | 0.84675 | 12.64 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97315 | 0.8542 | 11.895 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97315 | 0.86266 | 11.049 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97315 | 0.87045 | 10.27 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98345 | 0.86372 | 11.973 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98155 | 0.8772 | 10.435 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98173 | 0.87738 | 10.435 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98033 | 0.87332 | 10.702 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97756 | 0.87155 | 10.601 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98094 | 0.87562 | 10.532 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97964 | 0.86905 | 11.06 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97964 | 0.87622 | 10.343 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98311 | 0.85644 | 12.667 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97465 | 0.83922 | 13.543 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97465 | 0.84145 | 13.32 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97465 | 0.86807 | 10.658 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97856 | 0.84918 | 12.938 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98365 | 0.87606 | 10.759 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98145 | 0.88024 | 10.121 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97437 | 0.84407 | 13.031 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97437 | 0.84625 | 12.812 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98248 | 0.86853 | 11.395 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97866 | 0.86841 | 11.025 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97866 | 0.87489 | 10.377 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9813 | 0.87468 | 10.662 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98212 | 0.87816 | 10.396 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98186 | 0.87952 | 10.234 | Yes
Active | 2025W1-N11-WVD238746 | 238746 | 02GALION | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98179 | 0.87897 | 10.282 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99143 | 0.85608 | 13.535 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.85429 | 13.73 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.85429 | 13.634 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.84874 | 14.317 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97643 | 0.8028 | 17.363 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97643 | 0.81318 | 16.326 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97643 | 0.81991 | 15.653 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97643 | 0.82999 | 14.644 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97643 | 0.84356 | 13.287 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97643 | 0.84557 | 13.087 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97643 | 0.8484 | 12.803 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99387 | 0.83092 | 16.295 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99101 | 0.85114 | 13.987 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9913 | 0.85138 | 13.992 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99121 | 0.85214 | 13.907 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98785 | 0.84785 | 13.999 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.8495 | 14.071 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.84125 | 14.704 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98829 | 0.85087 | 13.742 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.82368 | 16.964 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97976 | 0.80081 | 17.895 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97976 | 0.80883 | 17.092 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97976 | 0.83604 | 14.372 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97976 | 0.85348 | 12.628 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98662 | 0.81497 | 17.165 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.85039 | 14.374 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99072 | 0.85378 | 13.694 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98225 | 0.81084 | 17.141 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98225 | 0.81259 | 16.966 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.84183 | 15.153 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98649 | 0.83941 | 14.708 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98649 | 0.8482 | 13.829 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99058 | 0.84783 | 14.275 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99187 | 0.85237 | 13.95 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99132 | 0.85372 | 13.759 | Yes
Active | 2025W1-N11-WVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9912 | 0.853 | 13.82 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98523 | 0.83084 | 15.439 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98527 | 0.82893 | 15.634 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98426 | 0.8293 | 15.496 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98572 | 0.82317 | 16.255 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96827 | 0.77241 | 19.586 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96827 | 0.78787 | 18.041 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96827 | 0.7922 | 17.607 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96827 | 0.80226 | 16.601 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96827 | 0.81858 | 14.969 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96827 | 0.81961 | 14.866 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96827 | 0.82244 | 14.584 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98826 | 0.79996 | 18.83 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98473 | 0.82595 | 15.878 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98508 | 0.82622 | 15.887 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98529 | 0.82939 | 15.59 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98206 | 0.82398 | 15.808 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98379 | 0.82407 | 15.972 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98158 | 0.81506 | 16.652 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98158 | 0.82474 | 15.684 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98778 | 0.79568 | 19.21 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97185 | 0.77093 | 20.092 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97185 | 0.7833 | 18.855 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97185 | 0.806 | 16.585 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97185 | 0.82722 | 14.462 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97994 | 0.78742 | 19.252 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98818 | 0.82511 | 16.307 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98436 | 0.82816 | 15.62 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97765 | 0.7848 | 19.285 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97765 | 0.78739 | 19.025 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98886 | 0.81778 | 17.107 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97937 | 0.81246 | 16.691 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97937 | 0.82121 | 15.815 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98416 | 0.82216 | 16.2 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98576 | 0.82731 | 15.845 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98493 | 0.82827 | 15.666 | Yes
Active | 2025W1-N11-WVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98477 | 0.82744 | 15.733 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97438 | 0.85549 | 11.889 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97438 | 0.86009 | 11.429 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97438 | 0.8671 | 10.728 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98325 | 0.87582 | 10.743 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98297 | 0.86871 | 11.426 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97567 | 0.85309 | 12.257 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97567 | 0.85428 | 12.138 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97904 | 0.8623 | 11.675 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97543 | 0.85687 | 11.856 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97543 | 0.85965 | 11.578 | Yes
Active | 2025W1-N11-WVD238891 | 238891 | 02LESIDE | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98243 | 0.87962 | 10.28 | Yes
Active | 2025W1-N11-WVD238906 | 238906 | 02LNGVEW | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97713 | 0.87528 | 10.185 | Yes
Active | 2025W1-N11-WVD238906 | 238906 | 02LNGVEW | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97713 | 0.87548 | 10.165 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95446 | 0.77858 | 17.588 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95417 | 0.77517 | 17.899 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95321 | 0.77669 | 17.653 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9556 | 0.77077 | 18.484 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9385 | 0.72803 | 21.047 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9385 | 0.73937 | 19.913 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9385 | 0.74133 | 19.717 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9385 | 0.75343 | 18.507 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9385 | 0.76189 | 17.661 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95832 | 0.75196 | 20.636 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95427 | 0.77349 | 18.078 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95483 | 0.77382 | 18.101 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9545 | 0.77872 | 17.578 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91999 | 0.77863 | 14.137 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91999 | 0.81466 | 10.533 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91999 | 0.81496 | 10.503 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95132 | 0.77308 | 17.825 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9521 | 0.77133 | 18.077 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94979 | 0.76165 | 18.814 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94979 | 0.76994 | 17.985 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95721 | 0.74823 | 20.899 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9398 | 0.72634 | 21.345 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9398 | 0.73376 | 20.604 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9398 | 0.7563 | 18.35 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9398 | 0.76877 | 17.103 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95008 | 0.83353 | 11.655 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94821 | 0.73715 | 21.106 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95804 | 0.77234 | 18.57 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95338 | 0.77591 | 17.747 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94502 | 0.73471 | 21.03 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94502 | 0.73834 | 20.667 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95806 | 0.76618 | 19.188 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94538 | 0.75634 | 18.904 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94538 | 0.76355 | 18.183 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95685 | 0.85254 | 10.431 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.95456 | 0.79704 | 15.752 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.9518 | 0.79708 | 15.472 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94611 | 0.77426 | 17.185 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94108 | 0.81376 | 12.731 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94108 | 0.82751 | 11.357 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94108 | 0.82768 | 11.34 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94026 | 0.8143 | 12.595 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94026 | 0.82831 | 11.194 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94026 | 0.82979 | 11.047 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94451 | 0.81121 | 13.33 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.94451 | 0.82444 | 12.007 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.94451 | 0.82955 | 11.496 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95254 | 0.76894 | 18.36 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95571 | 0.77502 | 18.069 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95361 | 0.77444 | 17.917 | Yes
Active | 2025W1-N11-WVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95331 | 0.77348 | 17.984 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99319 | 0.85254 | 14.066 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.85074 | 14.26 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.85079 | 14.155 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.84504 | 14.866 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97733 | 0.79741 | 17.992 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97733 | 0.80877 | 16.856 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97733 | 0.81516 | 16.217 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97733 | 0.82549 | 15.184 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97733 | 0.83998 | 13.734 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97733 | 0.84152 | 13.581 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97733 | 0.84458 | 13.275 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99577 | 0.82617 | 16.96 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.84751 | 14.524 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.84776 | 14.529 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.84923 | 14.391 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98971 | 0.84459 | 14.511 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.84589 | 14.604 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98991 | 0.83738 | 15.252 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98991 | 0.84729 | 14.262 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99522 | 0.81916 | 17.606 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98088 | 0.7955 | 18.538 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98088 | 0.8045 | 17.638 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98088 | 0.83143 | 14.945 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98088 | 0.84984 | 13.104 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98816 | 0.81024 | 17.792 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.84683 | 14.92 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.85013 | 14.231 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98392 | 0.80642 | 17.75 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98392 | 0.80818 | 17.574 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.83829 | 15.71 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98798 | 0.83536 | 15.263 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98798 | 0.84441 | 14.357 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.84409 | 14.821 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99366 | 0.84879 | 14.487 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.85016 | 14.291 | Yes
Active | 2025W1-N11-WVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99294 | 0.8494 | 14.353 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97109 | 0.80504 | 16.605 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97092 | 0.80272 | 16.82 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96995 | 0.80368 | 16.627 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97128 | 0.79657 | 17.471 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95192 | 0.74521 | 20.671 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95192 | 0.76302 | 18.889 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95192 | 0.76441 | 18.751 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95192 | 0.77558 | 17.634 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95192 | 0.78985 | 16.206 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97477 | 0.77181 | 20.295 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97031 | 0.79957 | 17.073 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97073 | 0.79987 | 17.087 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97127 | 0.80521 | 16.606 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96792 | 0.79911 | 16.881 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96906 | 0.7979 | 17.116 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96632 | 0.78829 | 17.802 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96632 | 0.79796 | 16.836 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97461 | 0.77038 | 20.424 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95528 | 0.74386 | 21.142 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95528 | 0.75986 | 19.542 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95528 | 0.7768 | 17.848 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95528 | 0.79876 | 15.652 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96704 | 0.86055 | 10.649 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96455 | 0.75899 | 20.556 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97432 | 0.79876 | 17.556 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97009 | 0.80217 | 16.792 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96434 | 0.76109 | 20.325 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96434 | 0.76389 | 20.045 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97663 | 0.79479 | 18.184 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96315 | 0.78463 | 17.852 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96315 | 0.79334 | 16.981 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96914 | 0.79523 | 17.39 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97151 | 0.80105 | 17.046 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9705 | 0.80203 | 16.848 | Yes
Active | 2025W1-N11-WVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97031 | 0.80113 | 16.917 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.84802 | 14.43 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99247 | 0.84622 | 14.624 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99144 | 0.84632 | 14.512 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99284 | 0.84042 | 15.243 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97586 | 0.79169 | 18.416 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97586 | 0.80389 | 17.197 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97586 | 0.80988 | 16.598 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97586 | 0.82035 | 15.55 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97586 | 0.83556 | 14.03 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97586 | 0.83663 | 13.923 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97586 | 0.83986 | 13.599 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99501 | 0.82074 | 17.426 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.84293 | 14.891 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.84319 | 14.898 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99238 | 0.84521 | 14.717 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98891 | 0.84033 | 14.858 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.84134 | 14.968 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.83267 | 15.625 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98892 | 0.84273 | 14.62 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99445 | 0.81404 | 18.041 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97955 | 0.78987 | 18.968 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97955 | 0.79968 | 17.987 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97955 | 0.82609 | 15.346 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97955 | 0.84521 | 13.435 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98714 | 0.805 | 18.214 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.84231 | 15.292 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99153 | 0.84554 | 14.599 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98309 | 0.80151 | 18.158 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98309 | 0.80331 | 17.978 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99477 | 0.83391 | 16.086 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98691 | 0.8305 | 15.641 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98691 | 0.83969 | 14.721 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.83944 | 15.194 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.84425 | 14.855 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.84562 | 14.655 | Yes
Active | 2025W1-N11-WVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99204 | 0.84485 | 14.719 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96541 | 0.85514 | 11.028 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96541 | 0.85968 | 10.573 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97335 | 0.86759 | 10.576 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96691 | 0.85302 | 11.389 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96691 | 0.85339 | 11.352 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96995 | 0.86182 | 10.814 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96677 | 0.85602 | 11.076 | Yes
Active | 2025W1-N11-WVD239028 | 239028 | 02ONTARO | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96677 | 0.85947 | 10.73 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.85259 | 14.061 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.8508 | 14.256 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.85085 | 14.151 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.8451 | 14.861 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97734 | 0.79748 | 17.986 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97734 | 0.80883 | 16.851 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97734 | 0.81523 | 16.212 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97734 | 0.82555 | 15.179 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97734 | 0.84004 | 13.73 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97734 | 0.84158 | 13.576 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97734 | 0.84464 | 13.27 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99578 | 0.82624 | 16.954 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.84757 | 14.519 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99307 | 0.84782 | 14.525 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99315 | 0.84928 | 14.387 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98972 | 0.84465 | 14.507 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.84595 | 14.6 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.83744 | 15.248 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98992 | 0.84735 | 14.257 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.81923 | 17.6 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9809 | 0.79558 | 18.532 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9809 | 0.80457 | 17.633 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9809 | 0.8315 | 14.94 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9809 | 0.8499 | 13.1 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98818 | 0.81031 | 17.787 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.84689 | 14.915 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99245 | 0.85019 | 14.226 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98393 | 0.80648 | 17.745 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98393 | 0.80824 | 17.568 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.83835 | 15.705 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.988 | 0.83542 | 15.258 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.988 | 0.84448 | 14.352 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.84415 | 14.816 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99367 | 0.84885 | 14.482 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.85022 | 14.286 | Yes
Active | 2025W1-N11-WVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99295 | 0.84946 | 14.349 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98189 | 0.89276 | 8.913 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98211 | 0.81227 | 16.984 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98218 | 0.81014 | 17.205 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98114 | 0.81147 | 16.967 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98295 | 0.80171 | 18.124 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98166 | 0.88888 | 9.278 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96028 | 0.74423 | 21.605 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96028 | 0.76466 | 19.562 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96028 | 0.77225 | 18.803 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96028 | 0.77865 | 18.163 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96028 | 0.79561 | 16.467 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98606 | 0.7726 | 21.347 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98067 | 0.80364 | 17.703 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98113 | 0.80404 | 17.709 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98365 | 0.902 | 8.165 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98219 | 0.81284 | 16.935 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97882 | 0.80623 | 17.259 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97882 | 0.8941 | 8.473 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98243 | 0.90078 | 8.166 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9801 | 0.80475 | 17.535 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97734 | 0.79466 | 18.269 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97734 | 0.80531 | 17.204 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98659 | 0.77431 | 21.228 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96515 | 0.74375 | 22.14 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96515 | 0.76875 | 19.64 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96515 | 0.77792 | 18.722 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96515 | 0.80663 | 15.852 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97837 | 0.87154 | 10.683 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97555 | 0.76138 | 21.416 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98527 | 0.80552 | 17.975 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98108 | 0.80914 | 17.193 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9792 | 0.76995 | 20.925 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9792 | 0.77253 | 20.667 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99018 | 0.80503 | 18.515 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99018 | 0.90358 | 8.66 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97473 | 0.79125 | 18.348 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97473 | 0.80094 | 17.379 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9848 | 0.88541 | 9.939 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98166 | 0.88888 | 9.278 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98312 | 0.89641 | 8.671 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98306 | 0.89693 | 8.614 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9807 | 0.80015 | 18.055 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9807 | 0.89404 | 8.666 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98211 | 0.8055 | 17.661 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98187 | 0.80961 | 17.225 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98367 | 0.89202 | 9.165 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98291 | 0.89921 | 8.371 | Yes
Active | 2025W1-N11-WVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9817 | 0.80859 | 17.31 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97553 | 0.80964 | 16.589 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97551 | 0.80745 | 16.806 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97455 | 0.80857 | 16.598 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97597 | 0.79994 | 17.603 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95519 | 0.74588 | 20.931 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95519 | 0.76514 | 19.005 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95519 | 0.76817 | 18.702 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95519 | 0.77822 | 17.697 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95519 | 0.7942 | 16.099 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97921 | 0.7742 | 20.501 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97429 | 0.8023 | 17.198 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97472 | 0.80265 | 17.207 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97574 | 0.80985 | 16.589 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97235 | 0.80359 | 16.875 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97361 | 0.8024 | 17.121 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97097 | 0.79267 | 17.83 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97097 | 0.80297 | 16.8 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97921 | 0.77322 | 20.599 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95934 | 0.74483 | 21.451 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95934 | 0.76413 | 19.521 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95934 | 0.7794 | 17.994 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95934 | 0.80415 | 15.519 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97176 | 0.86647 | 10.528 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96903 | 0.7613 | 20.773 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97875 | 0.80331 | 17.545 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97454 | 0.80669 | 16.785 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96968 | 0.76536 | 20.432 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96968 | 0.76792 | 20.177 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98165 | 0.80008 | 18.157 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96816 | 0.78922 | 17.894 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96816 | 0.79857 | 16.959 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97383 | 0.79852 | 17.531 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97561 | 0.80398 | 17.163 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97517 | 0.80687 | 16.83 | Yes
Active | 2025W1-N11-WVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97499 | 0.80592 | 16.907 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9767 | 0.86843 | 10.827 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9767 | 0.87262 | 10.408 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98439 | 0.88054 | 10.384 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97802 | 0.86631 | 11.171 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97802 | 0.86659 | 11.142 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98097 | 0.87482 | 10.615 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97781 | 0.86915 | 10.866 | Yes
Active | 2025W1-N11-WVD239195 | 239195 | 02MILIRN | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97781 | 0.87239 | 10.542 | Yes
Active | 2025W1-N11-WVD239196 | 239196 | 02ARM+BU | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97245 | 0.87118 | 10.127 | Yes
Active | 2025W1-N11-WVD239196 | 239196 | 02ARM+BU | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97414 | 0.86921 | 10.493 | Yes
Active | 2025W1-N11-WVD239196 | 239196 | 02ARM+BU | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97414 | 0.86925 | 10.489 | Yes
Active | 2025W1-N11-WVD239196 | 239196 | 02ARM+BU | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97419 | 0.87182 | 10.237 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97809 | 0.81537 | 16.272 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97809 | 0.81326 | 16.483 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97712 | 0.81417 | 16.294 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97856 | 0.80623 | 17.232 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95873 | 0.75309 | 20.563 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95873 | 0.77249 | 18.624 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95873 | 0.77347 | 18.526 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95873 | 0.78474 | 17.399 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95873 | 0.8008 | 15.793 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98159 | 0.78118 | 20.041 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97706 | 0.80871 | 16.835 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97748 | 0.80904 | 16.843 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97824 | 0.81511 | 16.313 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9749 | 0.80909 | 16.581 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9763 | 0.80826 | 16.804 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97379 | 0.79873 | 17.506 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97379 | 0.80885 | 16.494 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98147 | 0.7793 | 20.217 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9627 | 0.75192 | 21.078 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9627 | 0.76929 | 19.342 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9627 | 0.78662 | 17.608 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9627 | 0.81039 | 15.231 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9745 | 0.87122 | 10.328 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97195 | 0.76839 | 20.356 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98123 | 0.8092 | 17.203 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97713 | 0.8125 | 16.464 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97182 | 0.77059 | 20.122 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97182 | 0.77315 | 19.867 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98354 | 0.80484 | 17.87 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97115 | 0.79551 | 17.564 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97115 | 0.80469 | 16.646 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97658 | 0.80493 | 17.165 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9783 | 0.8103 | 16.8 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97775 | 0.81266 | 16.509 | Yes
Active | 2025W1-N11-WVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97758 | 0.81174 | 16.584 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97756 | 0.81463 | 16.293 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97756 | 0.81248 | 16.507 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97659 | 0.81347 | 16.313 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97801 | 0.80521 | 17.28 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95786 | 0.75192 | 20.594 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95786 | 0.77104 | 18.682 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95786 | 0.7728 | 18.507 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95786 | 0.78373 | 17.413 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95786 | 0.79973 | 15.813 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9811 | 0.78027 | 20.082 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97642 | 0.8076 | 16.882 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97684 | 0.80794 | 16.89 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97768 | 0.81438 | 16.331 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97431 | 0.80832 | 16.598 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97571 | 0.80745 | 16.826 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97316 | 0.79786 | 17.53 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97316 | 0.8081 | 16.506 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98104 | 0.77854 | 20.25 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9619 | 0.75077 | 21.114 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9619 | 0.76873 | 19.317 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9619 | 0.78551 | 17.639 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9619 | 0.80948 | 15.242 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97392 | 0.87057 | 10.335 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97128 | 0.76705 | 20.423 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98071 | 0.80836 | 17.235 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97659 | 0.81174 | 16.485 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97138 | 0.77004 | 20.133 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97138 | 0.7725 | 19.888 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98322 | 0.80443 | 17.879 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97047 | 0.79459 | 17.588 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97047 | 0.80389 | 16.658 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97597 | 0.80385 | 17.212 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97769 | 0.80923 | 16.846 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97722 | 0.8119 | 16.532 | Yes
Active | 2025W1-N11-WVD239264 | 239264 | 02DBP | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97705 | 0.81097 | 16.607 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96767 | 0.80386 | 16.381 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96642 | 0.80056 | 16.586 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9662 | 0.8016 | 16.46 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96482 | 0.79903 | 16.579 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95342 | 0.75922 | 19.42 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95342 | 0.76329 | 19.014 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95342 | 0.77121 | 18.222 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95342 | 0.78194 | 17.149 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95342 | 0.78893 | 16.449 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97122 | 0.78026 | 19.096 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96756 | 0.80546 | 16.211 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96794 | 0.80549 | 16.244 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9676 | 0.80363 | 16.396 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94808 | 0.83684 | 11.123 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.94808 | 0.84685 | 10.122 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96453 | 0.79852 | 16.601 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96498 | 0.79703 | 16.795 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96177 | 0.78773 | 17.404 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96177 | 0.79436 | 16.741 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96975 | 0.77558 | 19.418 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95269 | 0.75562 | 19.708 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95269 | 0.75634 | 19.635 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95269 | 0.78426 | 16.843 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95269 | 0.79277 | 15.992 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96156 | 0.85131 | 11.025 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96024 | 0.76604 | 19.42 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97106 | 0.79815 | 17.29 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9667 | 0.80147 | 16.523 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95389 | 0.75685 | 19.704 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95389 | 0.7614 | 19.249 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96916 | 0.78904 | 18.013 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95643 | 0.78237 | 17.407 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95643 | 0.78802 | 16.841 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.96158 | 0.84696 | 11.462 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95149 | 0.80464 | 14.685 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95149 | 0.83655 | 11.494 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95149 | 0.84606 | 10.543 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9496 | 0.80619 | 14.341 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9496 | 0.83674 | 11.286 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9496 | 0.84614 | 10.345 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.95337 | 0.79759 | 15.578 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.95337 | 0.80602 | 14.734 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95337 | 0.83122 | 12.215 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96268 | 0.79805 | 16.463 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96825 | 0.80605 | 16.22 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96574 | 0.79943 | 16.631 | Yes
Active | 2025W1-N11-WVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96548 | 0.79882 | 16.666 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.85294 | 13.976 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99285 | 0.85116 | 14.17 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.85119 | 14.067 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99321 | 0.84548 | 14.773 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97697 | 0.79812 | 17.885 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97697 | 0.8093 | 16.767 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97697 | 0.81577 | 16.121 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97697 | 0.82606 | 15.092 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97697 | 0.84039 | 13.659 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97697 | 0.84201 | 13.496 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97697 | 0.84504 | 13.194 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99525 | 0.82679 | 16.846 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99226 | 0.84794 | 14.432 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.84818 | 14.438 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.84953 | 14.309 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.84495 | 14.424 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99145 | 0.84631 | 14.514 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98944 | 0.83785 | 15.159 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98944 | 0.84771 | 14.173 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.81973 | 17.497 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98049 | 0.7962 | 18.429 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98049 | 0.80503 | 17.547 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98049 | 0.83203 | 14.846 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98049 | 0.85027 | 13.022 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9877 | 0.81084 | 17.686 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99551 | 0.84724 | 14.827 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.85056 | 14.139 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98343 | 0.80696 | 17.647 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.80872 | 17.471 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99485 | 0.83869 | 15.616 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98753 | 0.83585 | 15.168 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98753 | 0.84487 | 14.266 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99181 | 0.84453 | 14.728 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.84921 | 14.396 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.85057 | 14.2 | Yes
Active | 2025W1-N11-WVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99245 | 0.84982 | 14.262 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96522 | 0.8546 | 11.063 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96522 | 0.85915 | 10.607 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97318 | 0.86709 | 10.609 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96671 | 0.85247 | 11.424 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96671 | 0.85286 | 11.385 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96976 | 0.86129 | 10.848 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96657 | 0.85548 | 11.108 | Yes
Active | 2025W1-N11-WVD240533 | 240533 | 02OSTUMBO | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96657 | 0.85893 | 10.764 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97084 | 0.80324 | 16.761 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97076 | 0.80086 | 16.99 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96974 | 0.80196 | 16.778 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97141 | 0.79381 | 17.76 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95103 | 0.74144 | 20.959 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95103 | 0.75979 | 19.125 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95103 | 0.76256 | 18.848 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95103 | 0.77278 | 17.825 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95103 | 0.78758 | 16.345 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97457 | 0.76893 | 20.564 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96975 | 0.7962 | 17.355 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9702 | 0.79655 | 17.366 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97105 | 0.80348 | 16.758 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96766 | 0.79727 | 17.039 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96885 | 0.796 | 17.286 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96619 | 0.78622 | 17.997 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96619 | 0.79633 | 16.986 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97452 | 0.76778 | 20.674 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95492 | 0.74033 | 21.459 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95492 | 0.75849 | 19.643 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95492 | 0.77403 | 18.089 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95492 | 0.79724 | 15.769 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96704 | 0.8601 | 10.694 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96439 | 0.75593 | 20.846 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9741 | 0.79689 | 17.722 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96983 | 0.80032 | 16.952 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96487 | 0.75969 | 20.518 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96487 | 0.76223 | 20.264 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97684 | 0.79357 | 18.326 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96318 | 0.78256 | 18.061 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96318 | 0.79171 | 17.147 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96916 | 0.79235 | 17.68 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97109 | 0.79785 | 17.323 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97039 | 0.80026 | 17.013 | Yes
Active | 2025W1-N11-WVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9702 | 0.79931 | 17.089 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9667 | 0.79733 | 16.937 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96656 | 0.79474 | 17.182 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96547 | 0.79582 | 16.965 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96742 | 0.78826 | 17.916 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94763 | 0.73791 | 20.972 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.94763 | 0.75515 | 19.248 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.94763 | 0.75744 | 19.019 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.94763 | 0.76805 | 17.958 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.94763 | 0.7814 | 16.623 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97049 | 0.76448 | 20.601 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96581 | 0.7907 | 17.511 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96628 | 0.79104 | 17.524 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96691 | 0.7976 | 16.93 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96353 | 0.79148 | 17.205 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96463 | 0.79009 | 17.454 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96196 | 0.78025 | 18.171 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96196 | 0.79011 | 17.185 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97032 | 0.76303 | 20.729 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95114 | 0.73672 | 21.442 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95114 | 0.75327 | 19.787 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95114 | 0.76945 | 18.169 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95114 | 0.79065 | 16.049 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96286 | 0.85401 | 10.885 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96031 | 0.75126 | 20.905 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97001 | 0.79098 | 17.904 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96568 | 0.79446 | 17.121 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96045 | 0.75443 | 20.603 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96045 | 0.75701 | 20.345 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97245 | 0.78744 | 18.502 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95869 | 0.77631 | 18.238 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95869 | 0.78518 | 17.351 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96502 | 0.78674 | 17.828 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96716 | 0.79232 | 17.484 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96614 | 0.7941 | 17.204 | Yes
Active | 2025W1-N11-WVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96593 | 0.79315 | 17.278 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95668 | 0.78254 | 17.415 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95641 | 0.77934 | 17.707 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95533 | 0.78063 | 17.471 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95775 | 0.77439 | 18.335 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93982 | 0.72964 | 21.018 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93982 | 0.74368 | 19.614 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.93982 | 0.74394 | 19.588 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93982 | 0.75635 | 18.347 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93982 | 0.76598 | 17.384 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96056 | 0.75407 | 20.648 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95632 | 0.77702 | 17.93 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95685 | 0.77735 | 17.95 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9568 | 0.78277 | 17.403 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95354 | 0.77695 | 17.659 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9544 | 0.77529 | 17.911 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9519 | 0.76547 | 18.643 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9519 | 0.77433 | 17.757 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95983 | 0.75123 | 20.86 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94189 | 0.72813 | 21.376 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.94189 | 0.7387 | 20.318 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.94189 | 0.75861 | 18.328 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.94189 | 0.77369 | 16.82 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95253 | 0.83816 | 11.438 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95042 | 0.73987 | 21.055 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96018 | 0.77623 | 18.395 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95562 | 0.77981 | 17.581 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9486 | 0.73972 | 20.888 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9486 | 0.74286 | 20.574 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96115 | 0.77118 | 18.997 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94783 | 0.7606 | 18.723 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94783 | 0.7684 | 17.944 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9591 | 0.85612 | 10.298 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.95759 | 0.82842 | 12.917 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.95531 | 0.82846 | 12.685 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94514 | 0.83423 | 11.091 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94514 | 0.83678 | 10.836 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94452 | 0.83491 | 10.961 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94452 | 0.83759 | 10.693 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94861 | 0.83377 | 11.485 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.94861 | 0.84555 | 10.307 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95489 | 0.77267 | 18.222 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95773 | 0.77857 | 17.916 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95588 | 0.77862 | 17.726 | Yes
Active | 2025W1-N11-WVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95562 | 0.77767 | 17.794 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94367 | 0.76479 | 17.888 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94276 | 0.76143 | 18.133 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94221 | 0.76274 | 17.947 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9424 | 0.75848 | 18.392 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94264 | 0.84003 | 10.261 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.92778 | 0.71937 | 20.841 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.92778 | 0.7261 | 20.169 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.92778 | 0.73131 | 19.647 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.92778 | 0.74234 | 18.544 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.92778 | 0.74937 | 17.842 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94761 | 0.74087 | 20.674 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94342 | 0.76317 | 18.025 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94391 | 0.76334 | 18.058 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94364 | 0.76473 | 17.891 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.9143 | 0.78202 | 13.228 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9143 | 0.7986 | 11.57 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9143 | 0.79977 | 11.453 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.9143 | 0.81159 | 10.271 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94032 | 0.75957 | 18.075 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94092 | 0.75796 | 18.296 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93793 | 0.74874 | 18.919 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93793 | 0.75583 | 18.21 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94618 | 0.73664 | 20.954 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92773 | 0.71698 | 21.075 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.92773 | 0.71941 | 20.832 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.92773 | 0.74481 | 18.292 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.92773 | 0.75421 | 17.352 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93791 | 0.81574 | 12.216 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93625 | 0.72667 | 20.958 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94739 | 0.75907 | 18.833 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94258 | 0.76236 | 18.021 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93072 | 0.72045 | 21.028 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93072 | 0.72451 | 20.621 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94618 | 0.7514 | 19.478 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93249 | 0.74337 | 18.912 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93249 | 0.74945 | 18.304 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94615 | 0.8375 | 10.865 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94264 | 0.84003 | 10.261 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.94204 | 0.72756 | 21.448 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.93826 | 0.72759 | 21.067 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9356 | 0.77765 | 15.796 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9275 | 0.7839 | 14.36 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9275 | 0.79896 | 12.855 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9275 | 0.80211 | 12.539 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.92597 | 0.78591 | 14.006 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92597 | 0.79923 | 12.674 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92597 | 0.80267 | 12.33 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93051 | 0.77871 | 15.181 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93051 | 0.78579 | 14.473 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93051 | 0.79393 | 13.658 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93963 | 0.75715 | 18.249 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94453 | 0.76417 | 18.036 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9421 | 0.76052 | 18.157 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9439 | 0.84087 | 10.303 | Yes
Active | 2025W1-N11-WVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9418 | 0.75978 | 18.202 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94354 | 0.76462 | 17.892 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94261 | 0.76125 | 18.136 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94207 | 0.76256 | 17.951 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94222 | 0.75831 | 18.391 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94251 | 0.83985 | 10.266 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.92765 | 0.71927 | 20.838 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.92765 | 0.72592 | 20.173 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.92765 | 0.73118 | 19.646 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.92765 | 0.74221 | 18.544 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.92765 | 0.7492 | 17.845 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94747 | 0.74073 | 20.674 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94328 | 0.76304 | 18.024 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94377 | 0.7632 | 18.057 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9435 | 0.76455 | 17.895 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91422 | 0.78208 | 13.215 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91422 | 0.79838 | 11.584 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91422 | 0.79958 | 11.464 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91422 | 0.81142 | 10.28 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94018 | 0.7594 | 18.078 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94078 | 0.75779 | 18.299 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93778 | 0.74857 | 18.921 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93778 | 0.75564 | 18.214 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94604 | 0.7365 | 20.954 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92757 | 0.71687 | 21.071 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.92757 | 0.71921 | 20.836 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.92757 | 0.74467 | 18.29 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.92757 | 0.75401 | 17.356 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93775 | 0.81551 | 12.224 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93609 | 0.72653 | 20.956 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94726 | 0.7589 | 18.836 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94244 | 0.76219 | 18.025 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93053 | 0.72025 | 21.027 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93053 | 0.72432 | 20.62 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94603 | 0.7512 | 19.482 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94603 | 0.84597 | 10.006 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93232 | 0.74319 | 18.912 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93232 | 0.74926 | 18.306 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94601 | 0.8373 | 10.871 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94251 | 0.83985 | 10.266 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.94189 | 0.72671 | 21.518 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.93809 | 0.72674 | 21.135 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93546 | 0.77771 | 15.775 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.92736 | 0.78346 | 14.39 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92736 | 0.79877 | 12.859 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92736 | 0.80181 | 12.555 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.92582 | 0.78546 | 14.036 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92582 | 0.79904 | 12.678 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92582 | 0.80237 | 12.345 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93035 | 0.77823 | 15.212 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93035 | 0.78533 | 14.502 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93035 | 0.79371 | 13.665 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93946 | 0.75699 | 18.247 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94438 | 0.76403 | 18.035 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94195 | 0.76034 | 18.161 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94376 | 0.84067 | 10.309 | Yes
Active | 2025W1-N11-WVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94165 | 0.7596 | 18.205 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97036 | 0.79987 | 17.049 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97039 | 0.79532 | 17.507 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96932 | 0.79788 | 17.144 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9734 | 0.78828 | 18.512 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95579 | 0.74533 | 21.045 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95579 | 0.75832 | 19.747 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95579 | 0.75839 | 19.74 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95579 | 0.77242 | 18.337 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95579 | 0.77962 | 17.617 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9741 | 0.77228 | 20.181 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96935 | 0.78888 | 18.047 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97004 | 0.78943 | 18.061 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97041 | 0.80021 | 17.019 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96757 | 0.79407 | 17.351 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96821 | 0.79163 | 17.658 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96676 | 0.78093 | 18.583 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96676 | 0.7902 | 17.656 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9729 | 0.7677 | 20.52 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9579 | 0.74427 | 21.363 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9579 | 0.75333 | 20.457 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9579 | 0.77687 | 18.103 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9579 | 0.78817 | 16.972 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96729 | 0.8583 | 10.898 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96538 | 0.75452 | 21.086 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97386 | 0.79292 | 18.093 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9693 | 0.79694 | 17.236 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96327 | 0.75408 | 20.919 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96327 | 0.75774 | 20.553 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97401 | 0.78716 | 18.685 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96283 | 0.77439 | 18.844 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96283 | 0.78244 | 18.039 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96975 | 0.78566 | 18.408 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97131 | 0.79117 | 18.014 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96994 | 0.79483 | 17.511 | Yes
Active | 2025W1-N11-WVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96963 | 0.79355 | 17.608 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99215 | 0.85482 | 13.733 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.85303 | 13.928 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99133 | 0.85305 | 13.828 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99264 | 0.84742 | 14.522 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97683 | 0.80085 | 17.598 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97683 | 0.81159 | 16.524 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97683 | 0.8182 | 15.864 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97683 | 0.82837 | 14.846 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97683 | 0.84229 | 13.454 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97683 | 0.84412 | 13.272 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97683 | 0.84704 | 12.98 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99464 | 0.8292 | 16.544 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99172 | 0.84984 | 14.187 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99201 | 0.85009 | 14.193 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.85111 | 14.088 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9886 | 0.8467 | 14.19 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99092 | 0.84822 | 14.27 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98895 | 0.83987 | 14.909 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98895 | 0.84959 | 13.936 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.82205 | 17.204 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98024 | 0.79889 | 18.135 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98024 | 0.80728 | 17.296 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98024 | 0.83438 | 14.586 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98024 | 0.85218 | 12.806 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.81326 | 17.399 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.84912 | 14.578 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.85248 | 13.894 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98294 | 0.80925 | 17.369 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98294 | 0.81101 | 17.193 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.84058 | 15.361 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98711 | 0.83796 | 14.915 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98711 | 0.84685 | 14.026 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.8465 | 14.479 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.8511 | 14.151 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99203 | 0.85246 | 13.958 | Yes
Active | 2025W1-N11-WVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.85172 | 14.019 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98232 | 0.86876 | 11.356 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98074 | 0.86662 | 11.412 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98102 | 0.86604 | 11.498 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97827 | 0.87423 | 10.404 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97052 | 0.8291 | 14.142 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97052 | 0.83432 | 13.62 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97052 | 0.84348 | 12.704 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97052 | 0.85097 | 11.955 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97052 | 0.85238 | 11.814 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97052 | 0.8545 | 11.602 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97052 | 0.86069 | 10.982 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98457 | 0.85325 | 13.132 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98472 | 0.88323 | 10.15 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98482 | 0.88287 | 10.195 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98212 | 0.86831 | 11.381 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98009 | 0.86462 | 11.548 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97997 | 0.86363 | 11.633 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97723 | 0.85619 | 12.105 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97723 | 0.85974 | 11.749 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98289 | 0.84751 | 13.538 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97055 | 0.82246 | 14.809 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97055 | 0.8331 | 13.745 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97055 | 0.85591 | 11.464 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97055 | 0.85693 | 11.362 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97599 | 0.8411 | 13.489 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9847 | 0.86485 | 11.985 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.86705 | 11.461 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96641 | 0.82381 | 14.26 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96641 | 0.82909 | 13.731 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98074 | 0.85293 | 12.782 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97115 | 0.85067 | 12.047 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97115 | 0.85353 | 11.762 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97716 | 0.87388 | 10.328 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98426 | 0.88239 | 10.186 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98016 | 0.86508 | 11.508 | Yes
Active | 2025W1-N11-WVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97993 | 0.86498 | 11.495 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97007 | 0.80565 | 16.442 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96927 | 0.80279 | 16.649 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96865 | 0.80363 | 16.501 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96865 | 0.79995 | 16.87 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95426 | 0.75603 | 19.823 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95426 | 0.76565 | 18.862 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95426 | 0.76998 | 18.428 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95426 | 0.7813 | 17.297 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95426 | 0.7908 | 16.346 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97368 | 0.77871 | 19.497 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97001 | 0.8051 | 16.491 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9704 | 0.80522 | 16.517 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97012 | 0.80561 | 16.451 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96694 | 0.80013 | 16.681 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96766 | 0.79878 | 16.888 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96461 | 0.78937 | 17.525 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96461 | 0.79712 | 16.749 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97278 | 0.77537 | 19.742 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95504 | 0.75371 | 20.133 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95504 | 0.7592 | 19.584 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95504 | 0.78307 | 17.197 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95504 | 0.7965 | 15.854 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96484 | 0.856 | 10.884 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96311 | 0.76524 | 19.787 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97338 | 0.79972 | 17.365 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96909 | 0.8031 | 16.599 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95932 | 0.76043 | 19.889 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95932 | 0.76426 | 19.506 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97323 | 0.79271 | 18.052 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96015 | 0.78473 | 17.542 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96015 | 0.79151 | 16.864 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9562 | 0.8302 | 12.6 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9562 | 0.84852 | 10.768 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95493 | 0.83216 | 12.277 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95493 | 0.84897 | 10.596 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.95795 | 0.82524 | 13.27 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.95795 | 0.8319 | 12.605 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9665 | 0.79884 | 16.766 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97086 | 0.80599 | 16.487 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96867 | 0.80179 | 16.688 | Yes
Active | 2025W1-N11-WVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96843 | 0.80108 | 16.735 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94903 | 0.77099 | 17.805 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9484 | 0.76767 | 18.074 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94767 | 0.76901 | 17.866 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94884 | 0.76428 | 18.456 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94784 | 0.84649 | 10.135 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93311 | 0.72354 | 20.957 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93311 | 0.73216 | 20.094 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.93311 | 0.73608 | 19.703 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93311 | 0.74747 | 18.563 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93311 | 0.75518 | 17.793 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95295 | 0.74596 | 20.698 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94892 | 0.76818 | 18.074 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94943 | 0.7684 | 18.103 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94903 | 0.771 | 17.803 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91788 | 0.78191 | 13.596 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91788 | 0.80584 | 11.203 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91788 | 0.8064 | 11.148 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91788 | 0.81767 | 10.02 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94576 | 0.76565 | 18.011 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94645 | 0.76402 | 18.244 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94375 | 0.75464 | 18.911 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94375 | 0.76221 | 18.154 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95165 | 0.74196 | 20.969 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93358 | 0.72143 | 21.215 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93358 | 0.72591 | 20.767 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.93358 | 0.75007 | 18.351 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93358 | 0.76083 | 17.276 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94384 | 0.82358 | 12.025 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9421 | 0.73162 | 21.048 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9527 | 0.76506 | 18.765 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94794 | 0.76846 | 17.948 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93753 | 0.72692 | 21.061 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93753 | 0.7308 | 20.673 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95201 | 0.75801 | 19.4 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93875 | 0.74935 | 18.94 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93875 | 0.75588 | 18.287 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95147 | 0.84429 | 10.719 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94784 | 0.84649 | 10.135 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.94803 | 0.75291 | 19.512 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.94461 | 0.75294 | 19.167 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94103 | 0.77754 | 16.349 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93343 | 0.79907 | 13.436 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93343 | 0.80555 | 12.788 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93343 | 0.81215 | 12.128 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9322 | 0.80122 | 13.098 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9322 | 0.80594 | 12.626 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9322 | 0.81284 | 11.936 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93675 | 0.79468 | 14.207 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93675 | 0.80106 | 13.569 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93675 | 0.80154 | 13.521 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94595 | 0.76275 | 18.32 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95015 | 0.76938 | 18.077 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94778 | 0.76682 | 18.096 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94942 | 0.84791 | 10.15 | Yes
Active | 2025W1-N11-WVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94748 | 0.76599 | 18.149 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96351 | 0.88258 | 8.093 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96145 | 0.87194 | 8.951 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96083 | 0.79524 | 16.558 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96102 | 0.79417 | 16.685 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96 | 0.79491 | 16.509 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96118 | 0.78633 | 17.485 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96138 | 0.86822 | 9.316 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93345 | 0.71658 | 21.686 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.93345 | 0.74339 | 19.006 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93345 | 0.75605 | 17.739 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93345 | 0.76109 | 17.235 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93345 | 0.78053 | 15.291 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96472 | 0.74202 | 22.27 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9635 | 0.88286 | 8.064 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95983 | 0.78862 | 17.121 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96017 | 0.78894 | 17.123 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96246 | 0.87958 | 8.287 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96282 | 0.88266 | 8.016 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96287 | 0.88268 | 8.019 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96085 | 0.79616 | 16.47 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95808 | 0.78989 | 16.819 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95808 | 0.87404 | 8.405 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95976 | 0.87617 | 8.359 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96313 | 0.88215 | 8.098 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95902 | 0.78856 | 17.046 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95633 | 0.77919 | 17.714 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95633 | 0.79279 | 16.354 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96572 | 0.75227 | 21.345 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93911 | 0.71638 | 22.273 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.93911 | 0.74761 | 19.149 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93911 | 0.75966 | 17.944 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93911 | 0.79511 | 14.4 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95688 | 0.84964 | 10.724 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96535 | 0.74028 | 22.506 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96317 | 0.80845 | 15.472 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95994 | 0.79229 | 16.765 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96347 | 0.76121 | 20.225 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96347 | 0.76194 | 20.153 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97169 | 0.79287 | 17.883 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97169 | 0.88706 | 8.464 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9546 | 0.77702 | 17.758 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9546 | 0.78996 | 16.464 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96298 | 0.86343 | 9.955 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9627 | 0.88163 | 8.107 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96138 | 0.86822 | 9.316 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96259 | 0.87575 | 8.684 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96258 | 0.87623 | 8.635 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95959 | 0.7852 | 17.438 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95959 | 0.87424 | 8.535 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96092 | 0.79019 | 17.072 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96075 | 0.79363 | 16.713 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96237 | 0.87015 | 9.222 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96168 | 0.87657 | 8.511 | Yes
Active | 2025W1-N11-WVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96063 | 0.79276 | 16.787 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95763 | 0.87591 | 8.172 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95726 | 0.80954 | 14.772 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95714 | 0.80852 | 14.862 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95632 | 0.80876 | 14.756 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95704 | 0.80186 | 15.517 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.958 | 0.87372 | 8.428 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93047 | 0.71344 | 21.703 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93047 | 0.7602 | 17.027 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93047 | 0.7698 | 16.067 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93047 | 0.79666 | 13.38 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.93047 | 0.79933 | 13.114 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95998 | 0.74415 | 21.583 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95618 | 0.80434 | 15.184 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95618 | 0.87449 | 8.169 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95646 | 0.80457 | 15.189 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95726 | 0.81008 | 14.718 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9546 | 0.80445 | 15.015 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9546 | 0.86361 | 9.099 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95538 | 0.80362 | 15.176 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95538 | 0.87143 | 8.395 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95279 | 0.78559 | 16.719 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95279 | 0.79544 | 15.735 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96217 | 0.75658 | 20.559 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92721 | 0.71337 | 21.384 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.92721 | 0.74927 | 17.794 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.92721 | 0.75339 | 17.383 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.92721 | 0.7877 | 13.951 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95051 | 0.85385 | 9.666 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95448 | 0.85264 | 10.185 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96035 | 0.82363 | 13.672 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95651 | 0.80704 | 14.948 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96053 | 0.75494 | 20.56 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96053 | 0.77097 | 18.956 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96995 | 0.80594 | 16.4 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96995 | 0.88042 | 8.953 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95118 | 0.78271 | 16.847 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95118 | 0.79358 | 15.76 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95898 | 0.86851 | 9.047 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.958 | 0.87372 | 8.428 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95572 | 0.80105 | 15.467 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95572 | 0.86353 | 9.219 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95709 | 0.8056 | 15.15 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95689 | 0.80797 | 14.892 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95829 | 0.87425 | 8.404 | Yes
Active | 2025W1-N11-WVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95679 | 0.80727 | 14.952 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92828 | 8.072 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92767 | 8.133 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92322 | 8.578 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0054 | 0.89277 | 11.263 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0054 | 0.89816 | 10.724 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0054 | 0.90179 | 10.36 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0054 | 0.91077 | 9.463 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0054 | 0.9192 | 8.62 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0054 | 0.92008 | 8.532 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0054 | 0.92112 | 8.428 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.91855 | 9.045 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92475 | 8.425 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92493 | 8.407 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92047 | 8.853 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92461 | 8.439 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.91815 | 9.085 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92299 | 8.601 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.9086 | 10.04 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.89251 | 11.605 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0086 | 0.89719 | 11.136 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0086 | 0.92088 | 8.768 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0086 | 0.92523 | 8.332 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.89677 | 11.223 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.9224 | 8.66 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.89921 | 10.979 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.90261 | 10.639 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.91947 | 8.953 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.91766 | 9.134 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92231 | 8.669 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92264 | 8.636 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92566 | 8.334 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92783 | 8.117 | Yes
Active | 2025W1-N11-WVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92738 | 8.162 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99686 | 0.88654 | 11.032 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99686 | 0.90172 | 9.514 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99686 | 0.91162 | 8.524 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0068 | 0.91788 | 8.894 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.91505 | 9.038 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.90233 | 9.331 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99564 | 0.90241 | 9.323 | Yes
Active | 2025W1-N11-WVD242933 | 242933 | 05RPMONE | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98695 | 0.8949 | 9.205 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98421 | 0.89234 | 9.186 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98381 | 0.89123 | 9.258 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9832 | 0.89044 | 9.276 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98402 | 0.89049 | 9.353 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97368 | 0.84417 | 12.95 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97368 | 0.84934 | 12.434 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97368 | 0.86705 | 10.663 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97368 | 0.87147 | 10.221 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97368 | 0.88513 | 8.855 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97368 | 0.88627 | 8.74 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97368 | 0.88846 | 8.522 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98559 | 0.86899 | 11.66 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98447 | 0.89327 | 9.12 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.89328 | 9.132 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98379 | 0.89068 | 9.311 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98163 | 0.88672 | 9.491 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98282 | 0.88804 | 9.478 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9811 | 0.88229 | 9.881 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9811 | 0.88256 | 9.853 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98498 | 0.866 | 11.898 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97387 | 0.83273 | 14.114 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97387 | 0.84892 | 12.495 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97387 | 0.8748 | 9.907 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97387 | 0.88603 | 8.785 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98008 | 0.88126 | 9.882 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98579 | 0.89279 | 9.3 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98378 | 0.89082 | 9.296 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96011 | 0.83585 | 12.426 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96011 | 0.84656 | 11.355 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97939 | 0.86979 | 10.959 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98026 | 0.88099 | 9.927 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98026 | 0.88175 | 9.851 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98326 | 0.89012 | 9.314 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98478 | 0.89364 | 9.115 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98354 | 0.89057 | 9.297 | Yes
Active | 2025W1-N11-WVD242935 | 242935 | 05E LIMA | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98346 | 0.89019 | 9.327 | Yes
Active | 2025W1-N11-WVD242936 | 242936 | 05FOSTOR | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99626 | 0.9132 | 8.306 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9842 | 0.90171 | 8.25 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98419 | 0.82986 | 15.433 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98407 | 0.82816 | 15.59 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98316 | 0.82885 | 15.432 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98431 | 0.82129 | 16.302 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98433 | 0.89887 | 8.546 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96166 | 0.75481 | 20.684 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96166 | 0.78477 | 17.689 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96166 | 0.79233 | 16.933 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96166 | 0.80847 | 15.319 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96166 | 0.81541 | 14.625 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98738 | 0.7842 | 20.318 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98306 | 0.82381 | 15.925 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98342 | 0.82409 | 15.932 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98419 | 0.83017 | 15.402 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9811 | 0.8241 | 15.7 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9811 | 0.89796 | 8.314 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98215 | 0.82311 | 15.904 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97951 | 0.81411 | 16.539 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97951 | 0.81707 | 16.244 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98841 | 0.78813 | 20.028 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96344 | 0.75446 | 20.898 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96344 | 0.77406 | 18.938 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96344 | 0.78951 | 17.393 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96344 | 0.81884 | 14.46 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9787 | 0.87973 | 9.896 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9755 | 0.80552 | 16.998 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98704 | 0.83003 | 15.701 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98332 | 0.82712 | 15.62 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97836 | 0.77567 | 20.269 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97836 | 0.78567 | 19.269 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.82136 | 17.062 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99197 | 0.90653 | 8.545 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97742 | 0.81149 | 16.593 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97742 | 0.81351 | 16.391 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98631 | 0.89458 | 9.173 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98433 | 0.89887 | 8.546 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98536 | 0.9053 | 8.006 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9825 | 0.8201 | 16.24 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9825 | 0.89803 | 8.447 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.82525 | 15.891 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98376 | 0.82758 | 15.618 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98528 | 0.90029 | 8.5 | Yes
Active | 2025W1-N11-WVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98362 | 0.82675 | 15.687 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.92245 | 8.382 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92185 | 8.434 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.91728 | 8.902 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0013 | 0.88612 | 11.519 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0013 | 0.89163 | 10.968 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0013 | 0.89535 | 10.596 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0013 | 0.90453 | 9.679 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0013 | 0.91315 | 8.816 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0013 | 0.91404 | 8.728 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0013 | 0.91511 | 8.621 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0065 | 0.91246 | 9.399 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.91884 | 8.733 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.91903 | 8.717 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.9145 | 9.116 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.9187 | 8.731 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.9121 | 9.366 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.9171 | 8.865 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.90234 | 10.387 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.88586 | 11.866 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0045 | 0.89078 | 11.373 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0045 | 0.91482 | 8.97 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0045 | 0.91938 | 8.514 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.89024 | 11.549 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.91645 | 9.008 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.89285 | 11.288 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.89622 | 10.952 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.91347 | 9.298 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.91158 | 9.416 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.91641 | 8.933 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.91668 | 8.949 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.91978 | 8.649 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.922 | 8.425 | Yes
Active | 2025W1-N11-WVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92154 | 8.47 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99388 | 0.8592 | 13.468 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.85607 | 13.873 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.85652 | 13.766 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99536 | 0.84821 | 14.716 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98136 | 0.80089 | 18.047 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98136 | 0.81183 | 16.953 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98136 | 0.81756 | 16.38 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98136 | 0.82871 | 15.265 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98136 | 0.84305 | 13.831 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98136 | 0.84449 | 13.688 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98136 | 0.84561 | 13.575 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99659 | 0.83504 | 16.154 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99388 | 0.84992 | 14.396 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.85029 | 14.386 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.84493 | 14.945 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98657 | 0.8413 | 14.527 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.84911 | 14.428 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.83953 | 15.254 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99207 | 0.85095 | 14.112 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99585 | 0.82509 | 17.076 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.80019 | 18.543 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98562 | 0.81553 | 17.009 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98562 | 0.83887 | 14.674 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98562 | 0.85413 | 13.148 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99416 | 0.91255 | 8.16 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.80909 | 18.249 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99672 | 0.84844 | 14.828 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99323 | 0.85699 | 13.624 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99063 | 0.81751 | 17.312 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.81819 | 17.243 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.84591 | 15.107 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9906 | 0.83902 | 15.158 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9906 | 0.84945 | 14.116 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.84691 | 14.718 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.85159 | 14.313 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.85556 | 13.907 | Yes
Active | 2025W1-N11-WVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99453 | 0.8547 | 13.983 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99272 | 0.90231 | 9.04 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99272 | 0.9064 | 8.631 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99824 | 0.91544 | 8.28 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99356 | 0.89638 | 9.718 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99356 | 0.90524 | 8.832 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98814 | 0.9005 | 8.764 | Yes
Active | 2025W1-N11-WVD242942 | 242942 | 05SBERWI | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98814 | 0.90487 | 8.326 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98002 | 0.87969 | 10.033 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97957 | 0.87862 | 10.095 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97896 | 0.87766 | 10.129 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97967 | 0.87972 | 9.995 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96793 | 0.83057 | 13.736 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96793 | 0.83308 | 13.485 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96793 | 0.85679 | 11.115 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96793 | 0.85721 | 11.073 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96793 | 0.86865 | 9.929 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96793 | 0.87167 | 9.627 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96793 | 0.87453 | 9.341 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98165 | 0.85457 | 12.708 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98108 | 0.88367 | 9.74 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9812 | 0.88362 | 9.758 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97975 | 0.87862 | 10.113 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97757 | 0.87435 | 10.322 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97847 | 0.87508 | 10.34 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97647 | 0.86884 | 10.764 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97647 | 0.86934 | 10.714 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98105 | 0.85171 | 12.934 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96838 | 0.81926 | 14.912 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96838 | 0.83264 | 13.574 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96838 | 0.86001 | 10.837 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96838 | 0.87215 | 9.623 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97509 | 0.86494 | 11.015 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98182 | 0.87972 | 10.21 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97953 | 0.87799 | 10.154 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96033 | 0.82286 | 13.747 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96033 | 0.83345 | 12.688 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9776 | 0.85975 | 11.785 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97477 | 0.86703 | 10.775 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97477 | 0.86712 | 10.765 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97881 | 0.87928 | 9.953 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98124 | 0.88385 | 9.739 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97918 | 0.87774 | 10.145 | Yes
Active | 2025W1-N11-WVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97907 | 0.87735 | 10.173 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92602 | 8.298 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0064 | 0.89682 | 10.957 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0064 | 0.9018 | 10.459 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0064 | 0.90437 | 10.201 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0064 | 0.91434 | 9.205 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0064 | 0.9216 | 8.478 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0064 | 0.92293 | 8.346 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0064 | 0.92437 | 8.202 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92162 | 8.738 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92757 | 8.143 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92775 | 8.125 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92335 | 8.565 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92781 | 8.119 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92145 | 8.755 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92588 | 8.312 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.9122 | 9.68 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0089 | 0.89649 | 11.239 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0089 | 0.8998 | 10.909 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0089 | 0.92391 | 8.498 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0089 | 0.92772 | 8.117 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.90047 | 10.853 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92533 | 8.367 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.90198 | 10.702 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.90535 | 10.365 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92201 | 8.699 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92055 | 8.845 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92492 | 8.408 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92546 | 8.354 | Yes
Active | 2025W1-N11-WVD242947 | 242947 | 05WATERFORD | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92846 | 8.054 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98885 | 0.90647 | 8.238 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98609 | 0.81585 | 17.025 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98765 | 0.82082 | 16.684 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98671 | 0.82175 | 16.496 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98858 | 0.81188 | 17.67 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98678 | 0.89813 | 8.865 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96694 | 0.75763 | 20.932 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96694 | 0.76967 | 19.728 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96694 | 0.78151 | 18.543 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96694 | 0.7894 | 17.754 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96694 | 0.80554 | 16.14 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96694 | 0.81135 | 15.56 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96694 | 0.88302 | 8.393 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99056 | 0.79397 | 19.659 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98619 | 0.8135 | 17.269 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9866 | 0.81394 | 17.267 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98584 | 0.82348 | 16.236 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98443 | 0.81531 | 16.912 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98443 | 0.90411 | 8.032 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9856 | 0.81351 | 17.209 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9835 | 0.803 | 18.049 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9835 | 0.81657 | 16.693 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98963 | 0.7861 | 20.353 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97337 | 0.75723 | 21.614 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97337 | 0.78079 | 19.258 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97337 | 0.79798 | 17.539 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97337 | 0.81931 | 15.405 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98677 | 0.88677 | 10 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98394 | 0.76718 | 21.676 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99059 | 0.81083 | 17.977 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98419 | 0.81093 | 17.326 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9841 | 0.78219 | 20.191 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9841 | 0.78244 | 20.166 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.81215 | 18.02 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99236 | 0.91036 | 8.2 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98134 | 0.80178 | 17.956 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98134 | 0.81429 | 16.704 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98916 | 0.89536 | 9.379 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98678 | 0.89813 | 8.865 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98908 | 0.90764 | 8.144 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98906 | 0.90812 | 8.093 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98659 | 0.81033 | 17.626 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98659 | 0.90555 | 8.104 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9875 | 0.81544 | 17.206 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98739 | 0.82028 | 16.711 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9891 | 0.90169 | 8.74 | Yes
Active | 2025W1-N11-WVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98725 | 0.81927 | 16.797 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.8874 | 12.001 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.88659 | 12.131 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88661 | 12.08 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.87997 | 12.806 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.83982 | 16.237 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0022 | 0.84827 | 15.391 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0022 | 0.85147 | 15.071 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0022 | 0.86491 | 13.727 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0022 | 0.87633 | 12.585 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0022 | 0.87856 | 12.362 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0022 | 0.87943 | 12.275 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0092 | 0.86772 | 14.146 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88201 | 12.536 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.88228 | 12.525 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88154 | 12.555 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99879 | 0.86764 | 13.116 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.881 | 12.593 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.87138 | 13.454 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0059 | 0.88117 | 12.475 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.85796 | 15.075 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.83742 | 16.589 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0033 | 0.84363 | 15.968 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0033 | 0.87303 | 13.028 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0033 | 0.88613 | 11.719 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.84569 | 15.966 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0093 | 0.88 | 12.931 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.88497 | 12.19 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0036 | 0.84736 | 15.621 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.84892 | 15.465 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.87406 | 13.42 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.87144 | 13.406 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.88028 | 12.521 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.87897 | 12.825 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.88336 | 12.453 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.88605 | 12.17 | Yes
Active | 2025W1-N11-WVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.88533 | 12.236 | Yes
Active | 2025W1-N11-WVD242956 | 242956 | 05BALLHL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99506 | 0.91159 | 8.346 | Yes
Active | 2025W1-N11-WVD242956 | 242956 | 05BALLHL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99506 | 0.91401 | 8.105 | Yes
Active | 2025W1-N11-WVD242956 | 242956 | 05BALLHL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99635 | 0.91296 | 8.339 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.88613 | 12.055 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88538 | 12.168 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.88543 | 12.116 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87904 | 12.803 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.84043 | 16.196 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0024 | 0.84575 | 15.665 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0024 | 0.85324 | 14.916 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0024 | 0.86553 | 13.687 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0024 | 0.87523 | 12.716 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0024 | 0.87908 | 12.332 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0024 | 0.8801 | 12.229 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0086 | 0.86601 | 14.261 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.88128 | 12.524 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.88154 | 12.516 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.881 | 12.519 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99852 | 0.86792 | 13.06 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.87993 | 12.608 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.87036 | 13.439 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0048 | 0.87944 | 12.532 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.85688 | 15.127 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.8374 | 16.534 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0027 | 0.83965 | 16.31 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0027 | 0.87239 | 13.036 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0027 | 0.8853 | 11.744 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.84581 | 15.781 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.87922 | 12.944 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.88369 | 12.241 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.84434 | 15.704 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.84675 | 15.462 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87175 | 13.53 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.87033 | 13.39 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0042 | 0.87849 | 12.575 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.87809 | 12.811 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88257 | 12.451 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.88482 | 12.207 | Yes
Active | 2025W1-N11-WVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.88411 | 12.271 | Yes
Active | 2025W1-N11-WVD242974 | 242974 | 05BUCKLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.005 | 0.91855 | 8.644 | Yes
Active | 2025W1-N11-WVD242974 | 242974 | 05BUCKLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.005 | 0.92349 | 8.15 | Yes
Active | 2025W1-N11-WVD242974 | 242974 | 05BUCKLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0052 | 0.91134 | 9.391 | Yes
Active | 2025W1-N11-WVD242974 | 242974 | 05BUCKLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.92247 | 8.277 | Yes
Active | 2025W1-N11-WVD242974 | 242974 | 05BUCKLR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99922 | 0.91634 | 8.288 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.9145 | 8.076 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99334 | 0.88956 | 10.378 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99334 | 0.89 | 10.333 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99334 | 0.90111 | 9.222 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99334 | 0.90683 | 8.651 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99334 | 0.90961 | 8.372 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99613 | 0.90551 | 9.062 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.91334 | 8.095 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98933 | 0.90567 | 8.366 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.91454 | 8.015 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99383 | 0.90881 | 8.502 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99383 | 0.91356 | 8.027 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99591 | 0.89888 | 9.703 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99298 | 0.88241 | 11.057 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.8871 | 10.588 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99298 | 0.91111 | 8.186 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.89444 | 9.839 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99629 | 0.91466 | 8.163 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99092 | 0.88774 | 10.318 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99092 | 0.89142 | 9.95 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.90635 | 8.804 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.90884 | 8.464 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99348 | 0.913 | 8.048 | Yes
Active | 2025W1-N11-WVD242976 | 242976 | 05BUCYRC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.91403 | 8.078 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99309 | 0.90866 | 8.444 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99309 | 0.913 | 8.01 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99553 | 0.90765 | 8.788 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.90859 | 8.694 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99673 | 0.91147 | 8.526 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99689 | 0.9091 | 8.778 | Yes
Active | 2025W1-N11-WVD242977 | 242977 | 05CALDWE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99689 | 0.91567 | 8.122 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.87922 | 12.579 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.87698 | 12.893 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.87688 | 12.852 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.869 | 13.719 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99536 | 0.82536 | 17 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99536 | 0.83473 | 16.062 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99536 | 0.84023 | 15.512 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99536 | 0.85095 | 14.44 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99536 | 0.86275 | 13.26 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99536 | 0.86414 | 13.122 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99536 | 0.86593 | 12.942 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0072 | 0.85967 | 14.751 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.8709 | 13.429 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.87125 | 13.414 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.87416 | 13.023 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.85809 | 13.856 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.87269 | 13.233 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.85786 | 14.456 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.86809 | 13.434 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.84749 | 15.854 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.82458 | 17.389 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99846 | 0.83701 | 16.146 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99846 | 0.86309 | 13.537 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99846 | 0.87377 | 12.469 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.83219 | 17.088 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.86977 | 13.779 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.87696 | 12.747 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0028 | 0.83927 | 16.352 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.84097 | 16.182 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.86609 | 14.1 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.86013 | 14.237 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.86931 | 13.319 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86783 | 13.743 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.87249 | 13.333 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.87633 | 12.941 | Yes
Active | 2025W1-N11-WVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.87557 | 13.009 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0016 | 0.9141 | 8.752 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.91642 | 8.521 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.92483 | 8.035 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0022 | 0.90811 | 9.409 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.91486 | 8.734 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99857 | 0.9125 | 8.608 | Yes
Active | 2025W1-N11-WVD242984 | 242984 | 05CHATFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99857 | 0.91646 | 8.211 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86963 | 13.568 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.86822 | 13.802 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.8683 | 13.736 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.85958 | 14.702 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99417 | 0.81447 | 17.971 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99417 | 0.82405 | 17.012 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99417 | 0.82955 | 16.463 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99417 | 0.84112 | 15.305 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99417 | 0.85238 | 14.179 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99417 | 0.85429 | 13.988 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99417 | 0.85663 | 13.755 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0079 | 0.8495 | 15.844 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86154 | 14.376 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86192 | 14.363 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.86625 | 13.876 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99791 | 0.85177 | 14.614 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.86437 | 14.076 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.84721 | 15.465 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.85773 | 14.413 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.83752 | 16.892 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99708 | 0.81359 | 18.349 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99708 | 0.82595 | 17.113 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99708 | 0.85303 | 14.405 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99708 | 0.86412 | 13.296 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.8214 | 18.122 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.86086 | 14.742 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.86697 | 13.76 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.82829 | 17.389 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.83032 | 17.186 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.85684 | 15.079 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.85007 | 15.183 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.85946 | 14.243 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.85829 | 14.712 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.86327 | 14.284 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.8675 | 13.851 | Yes
Active | 2025W1-N11-WVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.86669 | 13.923 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.9233 | 8.145 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.9219 | 8.242 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.91728 | 8.726 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99664 | 0.89363 | 10.301 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99664 | 0.89443 | 10.222 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99664 | 0.89744 | 9.921 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99664 | 0.90912 | 8.753 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99664 | 0.91033 | 8.631 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99664 | 0.9111 | 8.555 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99664 | 0.9138 | 8.284 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.006 | 0.91521 | 9.078 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91912 | 8.5 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.9193 | 8.496 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.91591 | 8.617 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99802 | 0.9076 | 9.042 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99802 | 0.9115 | 8.652 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.90728 | 9.626 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99613 | 0.89166 | 10.447 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.893 | 10.313 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.89657 | 10.434 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.91927 | 8.701 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.8948 | 10.566 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.89663 | 10.383 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.9125 | 9.216 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.91168 | 8.967 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0013 | 0.91577 | 8.558 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.91668 | 8.722 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.92006 | 8.453 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.92243 | 8.206 | Yes
Active | 2025W1-N11-WVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.9221 | 8.235 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.90654 | 9.052 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.90547 | 9.122 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99614 | 0.9046 | 9.154 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99685 | 0.90512 | 9.174 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98834 | 0.85936 | 12.898 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98834 | 0.8656 | 12.275 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98834 | 0.88201 | 10.633 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98834 | 0.88728 | 10.107 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98834 | 0.89953 | 8.881 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98834 | 0.90164 | 8.67 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98834 | 0.90376 | 8.458 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99833 | 0.88423 | 11.409 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.90803 | 8.942 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99756 | 0.90802 | 8.954 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.90464 | 9.201 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.90045 | 9.403 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99579 | 0.90225 | 9.354 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.89674 | 9.745 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99419 | 0.89676 | 9.744 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99769 | 0.88065 | 11.704 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98825 | 0.84792 | 14.033 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98825 | 0.86481 | 12.344 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98825 | 0.8908 | 9.745 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98825 | 0.90128 | 8.697 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.89444 | 9.87 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99853 | 0.90664 | 9.189 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99667 | 0.90503 | 9.163 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97515 | 0.85221 | 12.293 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97515 | 0.86254 | 11.261 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99266 | 0.88421 | 10.845 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9932 | 0.89538 | 9.782 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.89585 | 9.735 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99617 | 0.90477 | 9.14 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99769 | 0.90834 | 8.935 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99643 | 0.90479 | 9.164 | Yes
Active | 2025W1-N11-WVD242989 | 242989 | 05E LIMA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99635 | 0.90442 | 9.193 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99327 | 0.90067 | 9.259 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99286 | 0.89971 | 9.315 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.89847 | 9.368 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99327 | 0.90085 | 9.242 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98477 | 0.85169 | 13.308 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98477 | 0.85964 | 12.514 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98477 | 0.87429 | 11.048 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98477 | 0.88174 | 10.303 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98477 | 0.8953 | 8.948 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98477 | 0.89641 | 8.836 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98477 | 0.89869 | 8.608 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9946 | 0.87798 | 11.662 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.9042 | 9.005 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99436 | 0.90414 | 9.021 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99294 | 0.89923 | 9.372 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9908 | 0.89503 | 9.577 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99187 | 0.89642 | 9.546 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9901 | 0.89041 | 9.97 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.89081 | 9.93 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.87431 | 11.951 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98487 | 0.83998 | 14.489 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98487 | 0.8592 | 12.568 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98487 | 0.88564 | 9.923 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98487 | 0.89597 | 8.89 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98887 | 0.88922 | 9.965 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.90113 | 9.372 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99285 | 0.89914 | 9.371 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97017 | 0.84465 | 12.552 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97017 | 0.85561 | 11.456 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.87782 | 11.17 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9888 | 0.88876 | 10.004 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9888 | 0.88966 | 9.914 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.90053 | 9.204 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.90435 | 9.006 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99253 | 0.8989 | 9.363 | Yes
Active | 2025W1-N11-WVD242991 | 242991 | 05E SIDE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.89856 | 9.388 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9829 | 0.8858 | 9.71 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9829 | 0.89222 | 9.069 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9829 | 0.9014 | 8.15 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98856 | 0.90532 | 8.324 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98813 | 0.902 | 8.612 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98296 | 0.87701 | 10.595 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98296 | 0.89158 | 9.138 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97425 | 0.88338 | 9.086 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97425 | 0.89119 | 8.306 | Yes
Active | 2025W1-N11-WVD242993 | 242993 | 05E.LEIPSIC2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9849 | 0.90401 | 8.088 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.8963 | 9.596 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9919 | 0.89529 | 9.661 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.8942 | 9.702 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99219 | 0.89579 | 9.64 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98229 | 0.84643 | 13.586 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98229 | 0.85261 | 12.968 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98229 | 0.87145 | 11.084 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98229 | 0.87551 | 10.678 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98229 | 0.88808 | 9.421 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98229 | 0.89055 | 9.174 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98229 | 0.89291 | 8.938 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99366 | 0.87273 | 12.093 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.89913 | 9.395 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.8991 | 9.41 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.89471 | 9.724 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98972 | 0.89037 | 9.935 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.89185 | 9.904 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98913 | 0.88598 | 10.316 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98913 | 0.88622 | 10.291 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99299 | 0.86905 | 12.394 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98246 | 0.83479 | 14.768 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98246 | 0.85193 | 13.054 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98246 | 0.87927 | 10.32 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98246 | 0.89053 | 9.194 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98795 | 0.88314 | 10.482 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99391 | 0.89644 | 9.747 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99183 | 0.89469 | 9.714 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96994 | 0.83913 | 13.08 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96994 | 0.84977 | 12.017 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.87389 | 11.441 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98791 | 0.88456 | 10.335 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98791 | 0.88485 | 10.306 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99145 | 0.89541 | 9.604 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99329 | 0.89937 | 9.392 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99158 | 0.8945 | 9.708 | Yes
Active | 2025W1-N11-WVD242995 | 242995 | 05EASTOW | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99149 | 0.89412 | 9.737 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.88124 | 12.286 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.87866 | 12.603 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.87862 | 12.57 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.87101 | 13.388 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99714 | 0.82618 | 17.096 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99714 | 0.83617 | 16.097 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99714 | 0.84165 | 15.549 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99714 | 0.85236 | 14.478 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99714 | 0.86639 | 13.075 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99714 | 0.86641 | 13.073 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99714 | 0.86802 | 12.912 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99714 | 0.91207 | 8.507 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.86044 | 14.507 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.87286 | 13.136 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.8732 | 13.115 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.8721 | 13.132 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99178 | 0.85302 | 13.876 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.87307 | 13.095 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.86134 | 14.134 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.87213 | 13.055 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.84867 | 15.624 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99973 | 0.82535 | 17.438 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99973 | 0.83903 | 16.07 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99973 | 0.86409 | 13.564 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99973 | 0.8766 | 12.313 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.83339 | 16.95 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.87117 | 13.459 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.87906 | 12.467 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.84123 | 16.139 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.84227 | 16.035 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86802 | 13.759 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.86223 | 14.025 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.87202 | 13.046 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.86986 | 13.442 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.87442 | 13.022 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.87809 | 12.65 | Yes
Active | 2025W1-N11-WVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.87732 | 12.722 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.88323 | 12.147 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.88052 | 12.489 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.88042 | 12.458 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.87291 | 13.271 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99702 | 0.8289 | 16.812 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99702 | 0.8386 | 15.841 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99702 | 0.84411 | 15.29 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99702 | 0.85459 | 14.243 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99702 | 0.86791 | 12.911 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99702 | 0.86831 | 12.871 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99702 | 0.86985 | 12.716 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99702 | 0.9151 | 8.192 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0063 | 0.86302 | 14.328 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.87477 | 13.012 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.8751 | 12.994 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.87521 | 12.87 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99368 | 0.85684 | 13.684 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.87531 | 12.938 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.863 | 14.005 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.87344 | 12.961 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.85103 | 15.454 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99986 | 0.82812 | 17.175 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99986 | 0.84127 | 15.859 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99986 | 0.86655 | 13.331 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99986 | 0.87818 | 12.168 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.83595 | 16.743 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87318 | 13.343 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.88113 | 12.316 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.84348 | 15.967 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.84477 | 15.838 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.8699 | 13.647 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.86425 | 13.87 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.8737 | 12.925 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.87178 | 13.316 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.8763 | 12.905 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87994 | 12.535 | Yes
Active | 2025W1-N11-WVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.87919 | 12.605 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1 | 0.90522 | 9.482 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1 | 0.91033 | 8.971 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0049 | 0.92394 | 8.092 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.92005 | 8.45 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0003 | 0.89721 | 10.309 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90937 | 9.093 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99312 | 0.90242 | 9.07 | Yes
Active | 2025W1-N11-WVD243004 | 243004 | 05FINDLC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99312 | 0.90909 | 8.403 | Yes
Active | 2025W1-N11-WVD243006 | 243006 | 05FOSTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0062 | 0.91977 | 8.642 | Yes
Active | 2025W1-N11-WVD243006 | 243006 | 05FOSTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0062 | 0.92469 | 8.15 | Yes
Active | 2025W1-N11-WVD243006 | 243006 | 05FOSTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0065 | 0.91257 | 9.39 | Yes
Active | 2025W1-N11-WVD243006 | 243006 | 05FOSTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.92372 | 8.276 | Yes
Active | 2025W1-N11-WVD243006 | 243006 | 05FOSTOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.91755 | 8.285 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.87264 | 13.218 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.87126 | 13.415 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.87143 | 13.358 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.86332 | 14.235 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99818 | 0.8163 | 18.188 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99818 | 0.82702 | 17.117 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99818 | 0.8325 | 16.568 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99818 | 0.84405 | 15.414 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99818 | 0.85901 | 13.917 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99818 | 0.85985 | 13.833 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99818 | 0.86089 | 13.729 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99818 | 0.90886 | 8.932 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0064 | 0.85077 | 15.561 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.86519 | 13.97 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.86555 | 13.949 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.86413 | 14.059 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.84577 | 14.63 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.86483 | 13.978 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.85396 | 14.971 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0037 | 0.86587 | 13.78 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.83956 | 16.636 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.81501 | 18.53 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0003 | 0.83012 | 17.018 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0003 | 0.85481 | 14.549 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0003 | 0.86987 | 13.044 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.8235 | 18.008 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.86323 | 14.33 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.87002 | 13.435 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0032 | 0.8324 | 17.078 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.83276 | 17.041 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.86039 | 14.617 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.85405 | 14.905 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.8649 | 13.819 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.86207 | 14.289 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.86684 | 13.852 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.8707 | 13.46 | Yes
Active | 2025W1-N11-WVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.86986 | 13.539 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.8909 | 11.521 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.89001 | 11.63 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.88999 | 11.588 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.88436 | 12.181 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0032 | 0.84853 | 15.471 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0032 | 0.85007 | 15.317 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0032 | 0.86284 | 14.04 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0032 | 0.87279 | 13.045 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0032 | 0.87983 | 12.341 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0032 | 0.88596 | 11.728 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0032 | 0.8871 | 11.614 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.008 | 0.87089 | 13.708 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.88676 | 11.908 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.88698 | 11.904 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.88581 | 11.958 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99808 | 0.87361 | 12.447 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.88488 | 12.037 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.87588 | 12.796 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0038 | 0.88367 | 12.017 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.86257 | 14.499 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0027 | 0.84243 | 16.03 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.84499 | 15.774 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0027 | 0.87831 | 12.442 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0027 | 0.8904 | 11.233 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.8539 | 14.827 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.88471 | 12.324 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.88861 | 11.694 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99939 | 0.8482 | 15.119 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99939 | 0.8517 | 14.769 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.87528 | 13.038 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.87577 | 12.749 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.88271 | 12.055 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.88352 | 12.182 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.88791 | 11.846 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.88943 | 11.669 | Yes
Active | 2025W1-N11-WVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.88878 | 11.728 | Yes
Active | 2025W1-N11-WVD243014 | 243014 | 05GRABILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99741 | 0.8923 | 10.512 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.90051 | 9.508 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9952 | 0.89952 | 9.568 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.89836 | 9.615 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99555 | 0.90044 | 9.51 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98606 | 0.85069 | 13.537 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98606 | 0.85771 | 12.835 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98606 | 0.87518 | 11.088 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98606 | 0.88034 | 10.572 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98606 | 0.89323 | 9.283 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98606 | 0.89521 | 9.084 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98606 | 0.89759 | 8.847 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.87721 | 11.977 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99655 | 0.90387 | 9.268 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99666 | 0.90382 | 9.284 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.89903 | 9.625 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.89476 | 9.833 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.89613 | 9.807 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9924 | 0.89032 | 10.208 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.89033 | 10.207 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99626 | 0.87356 | 12.27 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98623 | 0.83901 | 14.722 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98623 | 0.85715 | 12.909 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98623 | 0.88416 | 10.208 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98623 | 0.89506 | 9.117 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99116 | 0.88788 | 10.328 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99723 | 0.90077 | 9.646 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.89893 | 9.624 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9729 | 0.8435 | 12.94 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9729 | 0.8543 | 11.86 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.87809 | 11.376 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99109 | 0.88861 | 10.249 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.88913 | 10.196 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.90009 | 9.472 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99672 | 0.90405 | 9.267 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99487 | 0.89871 | 9.616 | Yes
Active | 2025W1-N11-WVD243016 | 243016 | 05HANTHR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.89835 | 9.643 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0058 | 0.89636 | 10.947 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0058 | 0.90827 | 9.757 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0058 | 0.91195 | 9.388 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0058 | 0.92578 | 8.006 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0107 | 0.92308 | 8.76 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.91989 | 9.073 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.90224 | 10.264 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.90861 | 9.627 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98805 | 0.90459 | 8.346 | Yes
Active | 2025W1-N11-WVD243017 | 243017 | 05HAVILAND1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99901 | 0.90546 | 9.354 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99976 | 0.83843 | 16.134 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.84003 | 16.107 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.84073 | 15.958 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.83097 | 17.082 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.91661 | 8.363 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98649 | 0.78033 | 20.616 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98649 | 0.79131 | 19.517 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98649 | 0.79918 | 18.731 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98649 | 0.81073 | 17.576 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98649 | 0.82653 | 15.996 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98649 | 0.82809 | 15.84 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98649 | 0.83043 | 15.606 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98649 | 0.90213 | 8.436 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98649 | 0.9044 | 8.209 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0034 | 0.8154 | 18.804 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99989 | 0.83281 | 16.708 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.83324 | 16.699 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.83979 | 16.066 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99483 | 0.82843 | 16.64 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99939 | 0.83303 | 16.636 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.82122 | 17.63 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99752 | 0.83473 | 16.279 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.80544 | 19.71 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99013 | 0.77852 | 21.161 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99013 | 0.79677 | 19.336 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99013 | 0.8198 | 17.034 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99013 | 0.8385 | 15.163 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90537 | 9.49 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.78711 | 21.032 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.83075 | 17.278 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99855 | 0.83461 | 16.394 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.79876 | 19.823 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.79886 | 19.813 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.82941 | 17.479 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.82069 | 17.533 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99602 | 0.83303 | 16.3 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.91414 | 8.786 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.91661 | 8.363 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.82946 | 17.07 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.83474 | 16.623 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.83945 | 16.142 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.9201 | 8.219 | Yes
Active | 2025W1-N11-WVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.83846 | 16.229 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99572 | 0.90342 | 9.23 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99572 | 0.90953 | 8.619 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99572 | 0.91244 | 8.327 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.9155 | 8.45 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.90312 | 9.453 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99764 | 0.90476 | 9.288 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99936 | 0.90749 | 9.188 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9996 | 0.90618 | 9.342 | Yes
Active | 2025W1-N11-WVD243020 | 243020 | 05HILLVI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9996 | 0.91236 | 8.724 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.85001 | 15.185 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.84954 | 15.33 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.84995 | 15.206 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.83954 | 16.391 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.92211 | 8.014 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98669 | 0.79366 | 19.304 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98669 | 0.80294 | 18.375 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98669 | 0.80852 | 17.818 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98669 | 0.82111 | 16.558 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98669 | 0.82928 | 15.742 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98669 | 0.83291 | 15.378 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98669 | 0.83687 | 14.982 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.82925 | 17.622 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.84149 | 15.986 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.84194 | 15.98 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.85121 | 15.107 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.84094 | 15.746 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.84754 | 15.418 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99601 | 0.8243 | 17.171 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99601 | 0.83481 | 16.12 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.81798 | 18.53 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99008 | 0.79306 | 19.703 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99008 | 0.80451 | 18.557 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99008 | 0.83271 | 15.737 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99008 | 0.84309 | 14.699 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.91438 | 8.985 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99768 | 0.80075 | 19.693 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.84247 | 16.332 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.84673 | 15.407 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.997 | 0.80681 | 19.02 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.997 | 0.80968 | 18.732 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.83775 | 16.714 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99634 | 0.82898 | 16.736 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99634 | 0.83829 | 15.805 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.92168 | 8.294 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.92211 | 8.014 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.83797 | 16.364 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.8435 | 15.909 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.84865 | 15.382 | Yes
Active | 2025W1-N11-WVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.84777 | 15.457 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.92327 | 8.109 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.89699 | 10.34 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0004 | 0.89791 | 10.248 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0004 | 0.90767 | 9.272 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0004 | 0.9138 | 8.659 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0004 | 0.91741 | 8.297 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0051 | 0.91465 | 9.044 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.92209 | 8.125 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99821 | 0.9141 | 8.411 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.92335 | 8.039 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.91756 | 8.536 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0029 | 0.92269 | 8.023 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.90766 | 9.72 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0013 | 0.89216 | 10.912 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89504 | 10.624 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0013 | 0.91941 | 8.187 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.90274 | 9.943 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.92336 | 8.196 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99921 | 0.89633 | 10.288 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99921 | 0.89955 | 9.966 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.9157 | 8.794 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.91765 | 8.497 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.92218 | 8.044 | Yes
Active | 2025W1-N11-WVD243024 | 243024 | 05HOWARD1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.92279 | 8.113 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.8569 | 14.861 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.85625 | 15.04 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.85661 | 14.93 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.84687 | 16.034 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99252 | 0.79962 | 19.29 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99252 | 0.80947 | 18.306 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99252 | 0.81597 | 17.655 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99252 | 0.82755 | 16.498 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99252 | 0.83974 | 15.278 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99252 | 0.84095 | 15.157 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99252 | 0.84464 | 14.788 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99252 | 0.91085 | 8.167 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0087 | 0.83591 | 17.28 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.84879 | 15.669 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.84922 | 15.658 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.85581 | 15.008 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99975 | 0.8428 | 15.695 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.85111 | 15.413 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.83442 | 16.759 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.84643 | 15.557 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.82395 | 18.331 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.79885 | 19.762 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99647 | 0.81334 | 18.313 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99647 | 0.83962 | 15.684 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99647 | 0.8524 | 14.407 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.91988 | 8.745 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.80683 | 19.593 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0091 | 0.84859 | 16.046 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.85378 | 15.081 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.81551 | 18.682 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.81672 | 18.561 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.84499 | 16.37 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.83664 | 16.495 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.84741 | 15.418 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.84539 | 16.033 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.85071 | 15.577 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.85555 | 15.085 | Yes
Active | 2025W1-N11-WVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.85463 | 15.166 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99577 | 0.89933 | 9.644 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.89835 | 9.702 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.89715 | 9.751 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.8995 | 9.623 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9858 | 0.84893 | 13.688 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9858 | 0.8558 | 13 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9858 | 0.8742 | 11.16 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9858 | 0.87869 | 10.711 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9858 | 0.89151 | 9.429 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9858 | 0.89367 | 9.214 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9858 | 0.89612 | 8.968 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9972 | 0.87571 | 12.149 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99683 | 0.90306 | 9.378 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99695 | 0.903 | 9.394 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99547 | 0.89794 | 9.753 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99328 | 0.89364 | 9.964 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99434 | 0.8949 | 9.943 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.889 | 10.349 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99249 | 0.88909 | 10.341 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.87208 | 12.439 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98606 | 0.83725 | 14.88 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98606 | 0.85527 | 13.079 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98606 | 0.88254 | 10.352 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98606 | 0.89363 | 9.242 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.88632 | 10.49 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.89957 | 9.788 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99533 | 0.89772 | 9.761 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97313 | 0.84172 | 13.141 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97313 | 0.85255 | 12.057 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.87712 | 11.509 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99111 | 0.88727 | 10.384 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.88772 | 10.339 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99498 | 0.89913 | 9.584 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.90322 | 9.377 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.89751 | 9.751 | Yes
Active | 2025W1-N11-WVD243030 | 243030 | 05LIMAOR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.89714 | 9.778 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.90282 | 9.729 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99988 | 0.90171 | 9.817 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99941 | 0.90119 | 9.822 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99978 | 0.89942 | 10.036 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99771 | 0.86056 | 13.715 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99771 | 0.86616 | 13.154 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99771 | 0.88669 | 11.102 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99771 | 0.88832 | 10.939 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99771 | 0.89198 | 10.572 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99771 | 0.90176 | 9.595 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99771 | 0.90351 | 9.419 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.88177 | 11.982 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.9022 | 9.791 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90227 | 9.798 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99936 | 0.89938 | 9.998 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9952 | 0.89233 | 10.287 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99891 | 0.89787 | 10.104 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99731 | 0.89124 | 10.607 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99731 | 0.89383 | 10.348 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.87665 | 12.446 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99586 | 0.84887 | 14.699 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99586 | 0.86291 | 13.295 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99586 | 0.8909 | 10.496 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99586 | 0.9014 | 9.446 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99554 | 0.8818 | 11.374 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.90053 | 10.11 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99968 | 0.90109 | 9.859 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98734 | 0.85604 | 13.13 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98734 | 0.86408 | 12.327 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.997 | 0.88278 | 11.422 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.89064 | 10.582 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99646 | 0.89264 | 10.382 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99906 | 0.89894 | 10.013 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.90279 | 9.767 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99965 | 0.90107 | 9.858 | Yes
Active | 2025W1-N11-WVD243031 | 243031 | 05LYNN Z | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99957 | 0.90061 | 9.896 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0011 | 0.90681 | 9.428 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0011 | 0.91191 | 8.918 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0059 | 0.92542 | 8.045 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.92156 | 8.4 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0013 | 0.89884 | 10.251 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.91095 | 9.04 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9942 | 0.90403 | 9.018 | Yes
Active | 2025W1-N11-WVD243033 | 243033 | 05THORNWD SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9942 | 0.91066 | 8.355 | Yes
Active | 2025W1-N11-WVD243034 | 243034 | 05MARQUI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0189 | 0.93542 | 8.351 | Yes
Active | 2025W1-N11-WVD243034 | 243034 | 05MARQUI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0189 | 0.93477 | 8.417 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.92369 | 8.307 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99948 | 0.90136 | 9.812 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99948 | 0.90155 | 9.792 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99948 | 0.90495 | 9.453 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99948 | 0.91628 | 8.32 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99948 | 0.91746 | 8.202 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99948 | 0.91771 | 8.177 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0081 | 0.922 | 8.611 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.92547 | 8.091 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.92564 | 8.087 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.92233 | 8.217 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.91506 | 8.568 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.91892 | 8.181 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.91448 | 9.135 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99894 | 0.89904 | 9.99 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99894 | 0.90091 | 9.803 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90411 | 9.928 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.92558 | 8.28 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0029 | 0.90218 | 10.07 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.90356 | 9.932 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91885 | 8.799 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.91837 | 8.545 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0038 | 0.92245 | 8.137 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92313 | 8.305 | Yes
Active | 2025W1-N11-WVD243038 | 243038 | 05MEIG1Z | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.92636 | 8.046 | Yes
Active | 2025W1-N11-WVD243039 | 243039 | 05MELMOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0045 | 0.9189 | 8.563 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88535 | 12.175 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.88417 | 12.339 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88421 | 12.292 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.87725 | 13.046 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.83521 | 16.662 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0018 | 0.84587 | 15.597 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0018 | 0.84669 | 15.515 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0018 | 0.86095 | 14.089 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0018 | 0.87381 | 12.802 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0018 | 0.87496 | 12.688 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0018 | 0.87582 | 12.601 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0087 | 0.865 | 14.367 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87923 | 12.785 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.87953 | 12.77 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.87797 | 12.879 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99663 | 0.86218 | 13.445 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.87835 | 12.836 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.8685 | 13.729 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0058 | 0.87878 | 12.701 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.85481 | 15.343 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.83321 | 16.999 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0032 | 0.8419 | 16.13 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0032 | 0.86993 | 13.328 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0032 | 0.88344 | 11.977 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.84164 | 16.371 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0088 | 0.87725 | 13.156 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.88294 | 12.369 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.004 | 0.84521 | 15.876 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.84648 | 15.749 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.87214 | 13.591 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.86856 | 13.68 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0054 | 0.87787 | 12.749 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.87619 | 13.08 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.88066 | 12.69 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88363 | 12.38 | Yes
Active | 2025W1-N11-WVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88288 | 12.45 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.89702 | 10.846 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.89598 | 10.95 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.89585 | 10.922 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.89126 | 11.395 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0043 | 0.8561 | 14.823 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0043 | 0.8586 | 14.573 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0043 | 0.87523 | 12.91 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0043 | 0.88187 | 12.245 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0043 | 0.88573 | 11.86 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0043 | 0.89469 | 10.964 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0043 | 0.89598 | 10.834 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0072 | 0.87709 | 13.016 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.89383 | 11.131 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.894 | 11.131 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.89208 | 11.246 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.88118 | 11.665 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.89126 | 11.316 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.883 | 11.986 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0029 | 0.88919 | 11.368 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.86977 | 13.711 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0028 | 0.84655 | 15.621 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.85446 | 14.831 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0028 | 0.88577 | 11.699 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0028 | 0.89694 | 10.583 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.86448 | 13.62 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.89181 | 11.535 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.89492 | 11.004 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99741 | 0.85366 | 14.376 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99741 | 0.85853 | 13.889 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.87991 | 12.414 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.88278 | 11.943 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.88819 | 11.401 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.89054 | 11.387 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.8948 | 11.083 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.89539 | 10.99 | Yes
Active | 2025W1-N11-WVD243048 | 243048 | 05N WALD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.8948 | 11.041 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.91062 | 9.36 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.90928 | 9.517 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.90909 | 9.498 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.90427 | 10.024 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99983 | 0.87134 | 12.849 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99983 | 0.87662 | 12.321 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99983 | 0.88197 | 11.786 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99983 | 0.89169 | 10.813 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99983 | 0.89934 | 10.049 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99983 | 0.9031 | 9.673 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99983 | 0.90379 | 9.604 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.89445 | 11.076 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.90601 | 9.816 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.9062 | 9.807 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.90317 | 10.034 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99554 | 0.89099 | 10.454 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.90476 | 9.903 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.89737 | 10.564 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.90471 | 9.83 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.886 | 11.892 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.86958 | 13.146 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.001 | 0.87205 | 12.899 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.001 | 0.89906 | 10.198 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.001 | 0.90886 | 9.218 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.87741 | 12.505 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.9043 | 10.111 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90888 | 9.503 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.87565 | 12.456 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.87783 | 12.238 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.89796 | 10.627 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.89747 | 10.52 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.90406 | 9.862 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.90356 | 10.046 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.90702 | 9.747 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.90885 | 9.551 | Yes
Active | 2025W1-N11-WVD243050 | 243050 | 05NBELVL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.90829 | 9.602 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9838 | 0.90349 | 8.032 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98117 | 0.86537 | 11.58 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98117 | 0.87311 | 10.805 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98117 | 0.8754 | 10.577 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98117 | 0.89244 | 8.873 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9859 | 0.88611 | 9.979 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98451 | 0.90424 | 8.027 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98262 | 0.90049 | 8.213 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98364 | 0.90208 | 8.155 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9821 | 0.89551 | 8.659 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9821 | 0.89748 | 8.463 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98498 | 0.88252 | 10.246 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98082 | 0.85428 | 12.654 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98082 | 0.87305 | 10.777 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98082 | 0.89641 | 8.441 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98109 | 0.8996 | 8.149 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98456 | 0.90444 | 8.012 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96311 | 0.85944 | 10.367 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96311 | 0.87021 | 9.29 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98074 | 0.88111 | 9.963 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98099 | 0.89431 | 8.668 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98099 | 0.89665 | 8.435 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98419 | 0.90412 | 8.006 | Yes
Active | 2025W1-N11-WVD243051 | 243051 | 05NDELPH | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98411 | 0.90385 | 8.026 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99536 | 0.89989 | 9.547 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99536 | 0.90614 | 8.922 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99536 | 0.90917 | 8.619 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99536 | 0.91511 | 8.025 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99981 | 0.91242 | 8.739 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.89957 | 9.782 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99739 | 0.90179 | 9.56 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99914 | 0.90409 | 9.506 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99936 | 0.90325 | 9.611 | Yes
Active | 2025W1-N11-WVD243056 | 243056 | 05NEWCOM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99936 | 0.90913 | 9.022 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99443 | 0.89359 | 10.084 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99443 | 0.8993 | 9.513 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99443 | 0.91099 | 8.344 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.91356 | 8.66 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99978 | 0.90984 | 8.994 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99457 | 0.88483 | 10.974 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.89843 | 9.614 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98604 | 0.89021 | 9.583 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98604 | 0.89772 | 8.831 | Yes
Active | 2025W1-N11-WVD243057 | 243057 | 05NEW LIBR1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.91262 | 8.407 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.91172 | 8.198 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.82332 | 16.853 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99274 | 0.82287 | 16.986 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.8239 | 16.797 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99367 | 0.81367 | 18.001 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.90269 | 8.878 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97562 | 0.76131 | 21.431 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97562 | 0.77317 | 20.245 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97562 | 0.78241 | 19.321 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97562 | 0.79245 | 18.317 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97562 | 0.80841 | 16.721 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97562 | 0.81095 | 16.467 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97562 | 0.81375 | 16.187 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97562 | 0.8896 | 8.602 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97562 | 0.88961 | 8.601 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99548 | 0.79571 | 19.977 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.81532 | 17.603 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99174 | 0.81577 | 17.597 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.82229 | 17.001 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98679 | 0.81319 | 17.359 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98679 | 0.90473 | 8.206 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99092 | 0.81568 | 17.524 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98907 | 0.8047 | 18.437 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98907 | 0.81856 | 17.052 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99474 | 0.78781 | 20.692 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98021 | 0.76 | 22.021 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98021 | 0.7807 | 19.95 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98021 | 0.80013 | 18.008 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98021 | 0.82134 | 15.887 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99139 | 0.89054 | 10.085 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.76949 | 21.952 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99542 | 0.81336 | 18.206 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99073 | 0.81978 | 17.095 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.78217 | 20.665 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98882 | 0.78239 | 20.644 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99689 | 0.81338 | 18.351 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99689 | 0.91556 | 8.133 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98695 | 0.8032 | 18.375 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98695 | 0.81584 | 17.111 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99465 | 0.89711 | 9.754 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.90269 | 8.878 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9939 | 0.9128 | 8.11 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99388 | 0.9133 | 8.058 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.81204 | 17.972 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99176 | 0.9109 | 8.086 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.81734 | 17.526 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.82232 | 17.016 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99403 | 0.90691 | 8.712 | Yes
Active | 2025W1-N11-WVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99234 | 0.82127 | 17.107 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0037 | 0.90485 | 9.886 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0037 | 0.91016 | 9.354 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0037 | 0.92208 | 8.163 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92431 | 8.469 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.92043 | 8.823 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0039 | 0.89642 | 10.75 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90921 | 9.47 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99611 | 0.90167 | 9.444 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.90876 | 8.734 | Yes
Active | 2025W1-N11-WVD243059 | 243059 | 05N.FINDLAY1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.92336 | 8.247 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.91301 | 9.083 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91203 | 9.206 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.9118 | 9.186 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.90739 | 9.673 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99946 | 0.87653 | 12.293 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99946 | 0.87959 | 11.987 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99946 | 0.88736 | 11.209 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99946 | 0.89607 | 10.338 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99946 | 0.90213 | 9.733 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99946 | 0.90707 | 9.239 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99946 | 0.90774 | 9.171 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.005 | 0.8977 | 10.729 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.90916 | 9.46 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90933 | 9.454 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.90703 | 9.608 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99686 | 0.89688 | 9.998 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.90778 | 9.556 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.90069 | 10.175 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.90747 | 9.497 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.88965 | 11.502 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0005 | 0.87435 | 12.614 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.87443 | 12.607 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0005 | 0.90265 | 9.785 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0005 | 0.91189 | 8.86 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.88214 | 11.957 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.90743 | 9.776 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.91129 | 9.219 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99904 | 0.87837 | 12.067 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99904 | 0.88088 | 11.815 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.90022 | 10.345 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.9008 | 10.13 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0021 | 0.90686 | 9.525 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.90674 | 9.681 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91009 | 9.404 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.9116 | 9.238 | Yes
Active | 2025W1-N11-WVD243061 | 243061 | 05NLEXTN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.91108 | 9.285 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9997 | 0.91236 | 8.734 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99943 | 0.91173 | 8.77 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99974 | 0.90706 | 9.268 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99286 | 0.87527 | 11.758 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99286 | 0.88146 | 11.14 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99286 | 0.88561 | 10.725 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99286 | 0.89386 | 9.9 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99286 | 0.90344 | 8.942 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99286 | 0.90389 | 8.897 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99286 | 0.90409 | 8.877 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99995 | 0.90238 | 9.757 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99949 | 0.90862 | 9.087 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99955 | 0.90882 | 9.073 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.90041 | 9.559 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99928 | 0.90864 | 9.065 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.90084 | 9.762 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99846 | 0.90651 | 9.195 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9995 | 0.8915 | 10.8 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9965 | 0.87499 | 12.151 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9965 | 0.88127 | 11.524 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9965 | 0.90487 | 9.163 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9965 | 0.9097 | 8.68 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99865 | 0.87988 | 11.877 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90651 | 9.379 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99875 | 0.88322 | 11.553 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99875 | 0.88629 | 11.245 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.90354 | 9.653 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99858 | 0.90122 | 9.737 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99858 | 0.90652 | 9.207 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99947 | 0.90643 | 9.304 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99968 | 0.90959 | 9.009 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99964 | 0.9119 | 8.774 | Yes
Active | 2025W1-N11-WVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99963 | 0.91142 | 8.82 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.85461 | 14.586 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.85467 | 14.669 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.85507 | 14.567 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.84625 | 15.559 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99099 | 0.79874 | 19.225 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99099 | 0.8097 | 18.128 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99099 | 0.81506 | 17.593 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99099 | 0.82751 | 16.347 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99099 | 0.8427 | 14.828 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99099 | 0.84366 | 14.733 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99099 | 0.84499 | 14.6 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99099 | 0.90668 | 8.431 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.83235 | 17.078 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.84816 | 15.231 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.84855 | 15.217 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.85165 | 14.889 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.83779 | 15.463 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.84826 | 15.18 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.83644 | 16.202 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99846 | 0.8488 | 14.967 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.82179 | 18.056 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99312 | 0.7966 | 19.652 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99312 | 0.81174 | 18.137 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99312 | 0.83676 | 15.635 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99312 | 0.85309 | 14.002 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.91531 | 8.54 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99843 | 0.80507 | 19.336 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.84624 | 15.702 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99962 | 0.85143 | 14.82 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99785 | 0.81418 | 18.367 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99785 | 0.81462 | 18.323 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.8435 | 15.989 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.83648 | 16.104 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99752 | 0.84771 | 14.981 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.8449 | 15.571 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.84992 | 15.135 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.85408 | 14.709 | Yes
Active | 2025W1-N11-WVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.85318 | 14.79 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99351 | 0.89868 | 9.483 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.89766 | 9.548 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.89661 | 9.588 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.89801 | 9.542 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98377 | 0.84934 | 13.443 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98377 | 0.85556 | 12.821 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98377 | 0.87391 | 10.986 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98377 | 0.8782 | 10.558 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98377 | 0.8907 | 9.307 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98377 | 0.89311 | 9.066 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98377 | 0.89541 | 8.836 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99488 | 0.87539 | 11.949 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99426 | 0.90126 | 9.299 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.90123 | 9.314 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.89703 | 9.614 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.89273 | 9.824 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.89427 | 9.789 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.88847 | 10.196 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99043 | 0.88869 | 10.175 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.87172 | 12.249 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9839 | 0.83775 | 14.615 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9839 | 0.85485 | 12.905 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9839 | 0.88192 | 10.198 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9839 | 0.89303 | 9.087 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98928 | 0.88574 | 10.355 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99512 | 0.89881 | 9.631 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.89709 | 9.599 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97123 | 0.84208 | 12.915 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97123 | 0.85263 | 11.861 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98945 | 0.8763 | 11.316 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98926 | 0.88709 | 10.217 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98926 | 0.8874 | 10.187 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.89764 | 9.506 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99447 | 0.90151 | 9.295 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99284 | 0.8969 | 9.594 | Yes
Active | 2025W1-N11-WVD243066 | 243066 | 05NW LIM | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.89652 | 9.623 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91925 | 8.134 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.91823 | 8.207 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.91745 | 8.238 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.91761 | 8.28 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99385 | 0.87696 | 11.688 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99385 | 0.88304 | 11.081 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99385 | 0.89725 | 9.66 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99385 | 0.90253 | 9.132 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99385 | 0.91214 | 8.17 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.89961 | 10.201 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.92015 | 8.07 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.92015 | 8.08 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91688 | 8.325 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99822 | 0.91311 | 8.511 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99955 | 0.91525 | 8.429 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99825 | 0.91026 | 8.799 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99825 | 0.91063 | 8.762 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.89589 | 10.521 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99382 | 0.86665 | 12.717 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.88217 | 11.165 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99382 | 0.90606 | 8.776 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99729 | 0.90708 | 9.021 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.91884 | 8.294 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.9179 | 8.237 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98306 | 0.87184 | 11.121 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98306 | 0.88093 | 10.212 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99707 | 0.89913 | 9.794 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99745 | 0.90949 | 8.796 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.90957 | 8.788 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99986 | 0.91731 | 8.255 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.92046 | 8.061 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91764 | 8.245 | Yes
Active | 2025W1-N11-WVD243067 | 243067 | 05NWOODC | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.9173 | 8.272 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0093 | 0.88217 | 12.709 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0099 | 0.87991 | 12.997 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0095 | 0.87993 | 12.956 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0101 | 0.87201 | 13.81 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.82615 | 17.58 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.002 | 0.83634 | 16.561 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.002 | 0.84196 | 16 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.002 | 0.85296 | 14.9 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.002 | 0.86722 | 13.474 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.002 | 0.86724 | 13.472 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.002 | 0.86907 | 13.289 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 1.002 | 0.91487 | 8.709 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0108 | 0.86104 | 14.974 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.87389 | 13.548 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0095 | 0.87424 | 13.527 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.87309 | 13.552 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99666 | 0.85414 | 14.252 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0091 | 0.87418 | 13.497 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.86204 | 14.569 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0077 | 0.87325 | 13.448 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0101 | 0.84918 | 16.096 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.82528 | 17.93 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0046 | 0.83947 | 16.512 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0046 | 0.86477 | 13.981 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0046 | 0.87782 | 12.676 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.83349 | 17.444 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.011 | 0.87227 | 13.877 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0089 | 0.87984 | 12.901 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0076 | 0.84169 | 16.594 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.84259 | 16.504 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0109 | 0.86908 | 14.179 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.86296 | 14.453 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0075 | 0.87313 | 13.436 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.87081 | 13.862 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0098 | 0.8755 | 13.432 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0098 | 0.87933 | 13.044 | Yes
Active | 2025W1-N11-WVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0097 | 0.87852 | 13.119 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.88103 | 12.548 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87879 | 12.807 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87889 | 12.769 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.8711 | 13.593 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0011 | 0.82466 | 17.648 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0011 | 0.83523 | 16.591 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0011 | 0.84065 | 16.049 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0011 | 0.85179 | 14.935 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0011 | 0.86652 | 13.462 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0011 | 0.86735 | 13.378 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0011 | 0.86826 | 13.288 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 1.0011 | 0.9094 | 9.174 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0075 | 0.85909 | 14.841 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.87294 | 13.357 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87329 | 13.332 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.86943 | 13.655 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.84892 | 14.231 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87237 | 13.389 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86203 | 14.361 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0056 | 0.87356 | 13.208 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.84782 | 15.936 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.82372 | 17.944 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0031 | 0.83852 | 16.463 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0031 | 0.86297 | 14.018 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0031 | 0.87738 | 12.578 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.83218 | 17.335 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.87101 | 13.664 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.87869 | 12.755 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.8407 | 16.448 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.84119 | 16.4 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.86814 | 13.95 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.86209 | 14.312 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.87261 | 13.26 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.8699 | 13.665 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.87453 | 13.229 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.87825 | 12.853 | Yes
Active | 2025W1-N11-WVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.87744 | 12.931 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.88738 | 11.765 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.88437 | 12.151 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.88417 | 12.126 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87693 | 12.916 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99661 | 0.83455 | 16.206 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99661 | 0.84376 | 15.284 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99661 | 0.84922 | 14.739 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99661 | 0.85926 | 13.734 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99661 | 0.87156 | 12.504 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99661 | 0.87241 | 12.42 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99661 | 0.87379 | 12.281 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0068 | 0.86806 | 13.875 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87877 | 12.654 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.87908 | 12.638 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.88089 | 12.321 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.86344 | 13.237 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.87968 | 12.544 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.86689 | 13.625 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.87668 | 12.646 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.85592 | 15.002 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99975 | 0.83384 | 16.591 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99975 | 0.84607 | 15.369 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99975 | 0.8714 | 12.835 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99975 | 0.8817 | 11.806 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.8413 | 16.232 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.87729 | 12.991 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.88544 | 11.913 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.84826 | 15.52 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.84991 | 15.356 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87389 | 13.297 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.86856 | 13.462 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0032 | 0.8774 | 12.578 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87585 | 12.95 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.88024 | 12.556 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.88377 | 12.196 | Yes
Active | 2025W1-N11-WVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.88306 | 12.263 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.88148 | 12.65 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.87922 | 12.927 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0081 | 0.87927 | 12.887 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.8714 | 13.73 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.82532 | 17.612 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0014 | 0.83565 | 16.578 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0014 | 0.84119 | 16.024 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0014 | 0.85225 | 14.918 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0014 | 0.8667 | 13.473 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0014 | 0.86701 | 13.442 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0014 | 0.8685 | 13.293 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 1.0014 | 0.91256 | 8.887 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0093 | 0.86003 | 14.927 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.87326 | 13.478 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.87361 | 13.456 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.87147 | 13.594 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.85192 | 14.248 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0078 | 0.87323 | 13.459 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.86177 | 14.494 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0067 | 0.87311 | 13.359 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0088 | 0.8484 | 16.038 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.82442 | 17.94 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0038 | 0.83883 | 16.499 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0038 | 0.86382 | 14 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0038 | 0.8774 | 12.643 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.83272 | 17.407 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0095 | 0.87153 | 13.798 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.87915 | 12.848 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0065 | 0.84104 | 16.542 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.84178 | 16.469 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.86846 | 14.095 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.86236 | 14.403 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0064 | 0.87267 | 13.372 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0081 | 0.8702 | 13.79 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.87487 | 13.358 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.87866 | 12.974 | Yes
Active | 2025W1-N11-WVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.87785 | 13.05 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.83833 | 15.087 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98996 | 0.83663 | 15.333 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98929 | 0.83711 | 15.218 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.82818 | 16.228 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97577 | 0.7764 | 19.936 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97577 | 0.78786 | 18.791 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97577 | 0.79549 | 18.028 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97577 | 0.80602 | 16.974 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97577 | 0.82272 | 15.304 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97577 | 0.82464 | 15.113 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97577 | 0.82596 | 14.98 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97577 | 0.88977 | 8.599 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99184 | 0.81204 | 17.981 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98906 | 0.83009 | 15.897 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98932 | 0.83049 | 15.884 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98971 | 0.83094 | 15.877 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98131 | 0.82077 | 16.053 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98862 | 0.82973 | 15.889 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98718 | 0.81916 | 16.802 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98718 | 0.83253 | 15.466 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.80214 | 18.91 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98018 | 0.77559 | 20.458 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98018 | 0.79439 | 18.579 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98018 | 0.81621 | 16.396 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98018 | 0.83567 | 14.451 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98906 | 0.89897 | 9.009 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98678 | 0.78489 | 20.189 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.82752 | 16.441 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9885 | 0.83551 | 15.299 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98632 | 0.79595 | 19.037 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98632 | 0.79626 | 19.005 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.82617 | 16.652 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98573 | 0.81822 | 16.752 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98573 | 0.83052 | 15.522 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.89897 | 9.232 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.8268 | 16.24 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9899 | 0.83189 | 15.801 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98978 | 0.83608 | 15.37 | Yes
Active | 2025W1-N11-WVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98968 | 0.83514 | 15.455 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.86479 | 13.799 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.86409 | 13.944 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.86435 | 13.87 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.85595 | 14.794 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99499 | 0.8086 | 18.639 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99499 | 0.81943 | 17.556 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99499 | 0.8249 | 17.008 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99499 | 0.83682 | 15.816 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99499 | 0.85193 | 14.306 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99499 | 0.85279 | 14.219 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99499 | 0.85396 | 14.103 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99499 | 0.90782 | 8.717 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0048 | 0.84287 | 16.195 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.85784 | 14.503 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.85821 | 14.485 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.85881 | 14.408 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.84235 | 14.977 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.85766 | 14.488 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.84637 | 15.495 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0013 | 0.85853 | 14.279 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.83184 | 17.239 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99715 | 0.80697 | 19.019 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99715 | 0.82221 | 17.494 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99715 | 0.84707 | 15.009 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99715 | 0.86267 | 13.448 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.92291 | 8.022 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.81547 | 18.579 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.85588 | 14.91 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.86194 | 14.023 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.82456 | 17.623 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.8249 | 17.589 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.85307 | 15.197 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.84646 | 15.415 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.85753 | 14.308 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.85466 | 14.831 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.85954 | 14.394 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.86352 | 13.987 | Yes
Active | 2025W1-N11-WVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.86266 | 14.067 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98415 | 0.8725 | 11.165 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98415 | 0.87884 | 10.531 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98415 | 0.89132 | 9.283 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98415 | 0.89744 | 8.671 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99172 | 0.89443 | 9.729 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98855 | 0.90777 | 8.078 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.90961 | 8.012 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.90497 | 8.351 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98848 | 0.90498 | 8.349 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99121 | 0.89102 | 10.019 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98412 | 0.86248 | 12.164 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98412 | 0.87814 | 10.598 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98412 | 0.90082 | 8.33 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98757 | 0.9027 | 8.487 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97345 | 0.86794 | 10.551 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97345 | 0.8769 | 9.655 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98721 | 0.89375 | 9.345 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98771 | 0.90392 | 8.379 | Yes
Active | 2025W1-N11-WVD243080 | 243080 | 05RILEYC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98771 | 0.90429 | 8.342 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99405 | 0.90149 | 9.256 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.90045 | 9.324 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99307 | 0.89947 | 9.36 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99394 | 0.90042 | 9.352 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9849 | 0.85315 | 13.174 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9849 | 0.85954 | 12.536 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9849 | 0.8767 | 10.819 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9849 | 0.88169 | 10.321 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9849 | 0.89413 | 9.077 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9849 | 0.89637 | 8.853 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9849 | 0.89855 | 8.635 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99536 | 0.87874 | 11.662 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.90346 | 9.115 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.90345 | 9.129 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99368 | 0.89969 | 9.399 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99149 | 0.89544 | 9.605 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.89714 | 9.561 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9911 | 0.89151 | 9.96 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9911 | 0.89162 | 9.948 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.87507 | 11.964 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98491 | 0.84162 | 14.329 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98491 | 0.85878 | 12.614 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98491 | 0.88534 | 9.957 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98491 | 0.89614 | 8.877 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.88904 | 10.097 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.90162 | 9.397 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99364 | 0.89994 | 9.37 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97178 | 0.84595 | 12.583 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97178 | 0.85638 | 11.54 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.87899 | 11.075 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99005 | 0.89018 | 9.988 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.89056 | 9.949 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99324 | 0.90006 | 9.318 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99485 | 0.90375 | 9.11 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.89973 | 9.368 | Yes
Active | 2025W1-N11-WVD243082 | 243082 | 05ROCKHILL1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99333 | 0.89936 | 9.397 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.90917 | 8.54 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99423 | 0.90816 | 8.608 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.90732 | 8.64 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.90778 | 8.66 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98669 | 0.86447 | 12.222 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98669 | 0.87075 | 11.594 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98669 | 0.88563 | 10.107 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98669 | 0.89123 | 9.546 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98669 | 0.90265 | 8.404 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98669 | 0.90481 | 8.189 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99573 | 0.8882 | 10.753 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.91051 | 8.441 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.91049 | 8.453 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99417 | 0.90723 | 8.693 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99215 | 0.90329 | 8.885 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9934 | 0.90511 | 8.83 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.89994 | 9.2 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99194 | 0.89995 | 9.199 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99514 | 0.88469 | 11.046 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98662 | 0.85359 | 13.303 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98662 | 0.87 | 11.662 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98662 | 0.8947 | 9.193 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98662 | 0.90447 | 8.215 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.89765 | 9.33 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99592 | 0.90918 | 8.674 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.90776 | 8.646 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97447 | 0.85833 | 11.614 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97447 | 0.86813 | 10.634 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99052 | 0.88792 | 10.26 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99104 | 0.8987 | 9.234 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.89913 | 9.191 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99376 | 0.90746 | 8.63 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99515 | 0.9108 | 8.435 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.90752 | 8.648 | Yes
Active | 2025W1-N11-WVD243083 | 243083 | 05CAMPSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99392 | 0.90717 | 8.675 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0054 | 0.91604 | 8.936 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0054 | 0.91838 | 8.702 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0054 | 0.92089 | 8.452 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.92973 | 8.085 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.91473 | 9.012 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.91771 | 8.714 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.9201 | 8.845 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0079 | 0.91786 | 9.004 | Yes
Active | 2025W1-N11-WVD243084 | 243084 | 05RUTLAND1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.91825 | 8.965 | Yes
Active | 2025W1-N11-WVD243086 | 243086 | 05S HICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0026 | 0.91445 | 8.811 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.92137 | 8.283 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.82919 | 17.218 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.83109 | 17.157 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.83217 | 16.954 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.82131 | 18.239 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91103 | 9.022 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98361 | 0.76906 | 21.455 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98361 | 0.78062 | 20.298 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98361 | 0.79038 | 19.323 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98361 | 0.80011 | 18.349 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98361 | 0.81491 | 16.87 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98361 | 0.81644 | 16.717 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98361 | 0.82108 | 16.253 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98361 | 0.89757 | 8.604 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98361 | 0.9005 | 8.311 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.80491 | 20.075 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.82293 | 17.813 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.82341 | 17.809 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.83344 | 16.82 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99859 | 0.8243 | 17.429 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99859 | 0.91603 | 8.256 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.82419 | 17.647 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99803 | 0.81098 | 18.705 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99803 | 0.82449 | 17.353 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.79637 | 20.815 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98917 | 0.7684 | 22.076 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98917 | 0.78873 | 20.044 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98917 | 0.8091 | 18.007 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98917 | 0.82819 | 16.098 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.90022 | 10.174 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99854 | 0.77779 | 22.076 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.82212 | 18.358 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.82488 | 17.495 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99845 | 0.79043 | 20.802 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.79085 | 20.76 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.82153 | 18.536 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0069 | 0.92319 | 8.37 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99614 | 0.81051 | 18.562 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99614 | 0.82276 | 17.337 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.90958 | 9.471 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91103 | 9.022 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.9218 | 8.238 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.9223 | 8.185 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.81958 | 18.198 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.91863 | 8.294 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.82506 | 17.74 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.83049 | 17.188 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91541 | 8.873 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.92299 | 8.057 | Yes
Active | 2025W1-N11-WVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.82941 | 17.28 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99339 | 0.90711 | 8.628 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99339 | 0.91152 | 8.187 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99591 | 0.90659 | 8.932 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99591 | 0.90702 | 8.889 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99714 | 0.91 | 8.714 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99729 | 0.90807 | 8.921 | Yes
Active | 2025W1-N11-WVD243091 | 243091 | 05S.CALDWELL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99729 | 0.91431 | 8.298 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90116 | 9.976 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89863 | 10.27 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.89828 | 10.269 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.89261 | 10.882 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99437 | 0.85494 | 13.943 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99437 | 0.86358 | 13.079 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99437 | 0.8683 | 12.607 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99437 | 0.87668 | 11.769 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99437 | 0.88917 | 10.521 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99437 | 0.88934 | 10.504 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99437 | 0.88972 | 10.465 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.885 | 11.655 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.89421 | 10.685 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.89446 | 10.667 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99946 | 0.89038 | 10.908 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.87482 | 11.641 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.8934 | 10.732 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.88505 | 11.499 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1 | 0.8935 | 10.654 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.87345 | 12.787 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99761 | 0.85434 | 14.327 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99761 | 0.86497 | 13.264 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99761 | 0.8882 | 10.941 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99761 | 0.89711 | 10.05 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.86114 | 13.899 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.89226 | 10.984 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.89953 | 10.116 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1 | 0.8669 | 13.314 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.8687 | 13.134 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.88948 | 11.25 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99988 | 0.88557 | 11.431 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99988 | 0.89314 | 10.674 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.89176 | 10.93 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89541 | 10.59 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89819 | 10.308 | Yes
Active | 2025W1-N11-WVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.89757 | 10.366 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9918 | 0.9058 | 8.6 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9918 | 0.91034 | 8.146 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99417 | 0.90508 | 8.909 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99417 | 0.90569 | 8.848 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99547 | 0.90877 | 8.67 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99566 | 0.90655 | 8.911 | Yes
Active | 2025W1-N11-WVD243096 | 243096 | 05SCUMBL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99566 | 0.91312 | 8.255 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.87841 | 12.756 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87791 | 12.865 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.87803 | 12.8 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.87083 | 13.589 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.82925 | 17.091 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0002 | 0.83835 | 16.181 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0002 | 0.84074 | 15.942 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0002 | 0.85538 | 14.478 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0002 | 0.86781 | 13.235 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0002 | 0.86942 | 13.074 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0002 | 0.87034 | 12.982 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0081 | 0.85804 | 15.004 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.87292 | 13.298 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87322 | 13.288 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.87365 | 13.212 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99793 | 0.85992 | 13.801 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.8721 | 13.336 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.86185 | 14.245 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0043 | 0.87228 | 13.202 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.84811 | 15.943 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.82663 | 17.471 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0013 | 0.83368 | 16.766 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0013 | 0.86347 | 13.786 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0013 | 0.8774 | 12.394 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.83463 | 16.905 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.87086 | 13.733 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87576 | 12.957 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.83736 | 16.46 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.83872 | 16.324 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.86525 | 14.195 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.8619 | 14.192 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0038 | 0.87134 | 13.248 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.86975 | 13.602 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.87437 | 13.215 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.87735 | 12.905 | Yes
Active | 2025W1-N11-WVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87658 | 12.974 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.89848 | 9.77 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99577 | 0.89748 | 9.829 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99508 | 0.89631 | 9.876 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99608 | 0.8987 | 9.738 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98573 | 0.848 | 13.773 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98573 | 0.85413 | 13.16 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98573 | 0.8738 | 11.193 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98573 | 0.87728 | 10.845 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98573 | 0.88986 | 9.587 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98573 | 0.89229 | 9.344 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98573 | 0.89484 | 9.089 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99766 | 0.87451 | 12.315 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99728 | 0.90239 | 9.489 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.90233 | 9.506 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9959 | 0.89715 | 9.875 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.89284 | 10.086 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.894 | 10.073 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99285 | 0.88799 | 10.485 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99285 | 0.8882 | 10.465 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.87096 | 12.598 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98603 | 0.83637 | 14.966 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98603 | 0.85361 | 13.242 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98603 | 0.88106 | 10.497 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98603 | 0.89238 | 9.365 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.88497 | 10.659 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.89866 | 9.924 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.89684 | 9.889 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97412 | 0.84077 | 13.335 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97412 | 0.85157 | 12.255 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.8766 | 11.62 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99139 | 0.88627 | 10.512 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99139 | 0.88662 | 10.477 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.89832 | 9.699 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.90254 | 9.489 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99541 | 0.89663 | 9.879 | Yes
Active | 2025W1-N11-WVD243099 | 243099 | 05SHAWNR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.89625 | 9.906 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.90033 | 9.971 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99985 | 0.89921 | 10.064 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99941 | 0.89881 | 10.06 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99967 | 0.89623 | 10.344 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99997 | 0.86009 | 13.988 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99997 | 0.86527 | 13.47 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99997 | 0.88733 | 11.264 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99997 | 0.88759 | 11.238 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99997 | 0.88819 | 11.178 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99997 | 0.90072 | 9.925 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99997 | 0.90234 | 9.763 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.87975 | 12.183 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9999 | 0.89895 | 10.095 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.89904 | 10.1 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.89635 | 10.282 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.88829 | 10.601 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99885 | 0.89515 | 10.371 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.88811 | 10.915 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99726 | 0.89166 | 10.56 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.87405 | 12.709 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99746 | 0.84832 | 14.914 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99746 | 0.8611 | 13.636 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99746 | 0.88983 | 10.764 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99746 | 0.90035 | 9.711 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.8761 | 11.917 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.89718 | 10.439 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99958 | 0.89851 | 10.107 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99081 | 0.85657 | 13.423 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99081 | 0.86374 | 12.707 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.88115 | 11.624 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.88762 | 10.884 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99647 | 0.89053 | 10.593 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99893 | 0.89569 | 10.324 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.89964 | 10.065 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99963 | 0.89859 | 10.104 | Yes
Active | 2025W1-N11-WVD243103 | 243103 | 05SKENTO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99955 | 0.8981 | 10.146 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.84006 | 16.645 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.83998 | 16.767 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.84093 | 16.582 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.82963 | 17.9 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.91905 | 8.73 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9904 | 0.78022 | 21.018 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9904 | 0.79061 | 19.979 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9904 | 0.79811 | 19.229 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9904 | 0.8096 | 18.08 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9904 | 0.82271 | 16.769 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9904 | 0.82284 | 16.756 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9904 | 0.82856 | 16.184 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9904 | 0.90644 | 8.396 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9904 | 0.90646 | 8.394 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0104 | 0.81666 | 19.378 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.83134 | 17.471 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.83185 | 17.464 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.84186 | 16.519 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.83131 | 17.142 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.92124 | 8.149 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.83376 | 17.2 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.81716 | 18.53 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.83014 | 17.232 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0089 | 0.806 | 20.288 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.77957 | 21.562 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99519 | 0.79565 | 19.954 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99519 | 0.82064 | 17.455 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99519 | 0.83541 | 15.978 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.90966 | 9.821 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.78797 | 21.51 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0107 | 0.83211 | 17.856 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.83629 | 16.899 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.79755 | 20.51 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.7988 | 20.385 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0107 | 0.82908 | 18.166 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0107 | 0.92878 | 8.196 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.8184 | 18.278 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0012 | 0.82998 | 17.12 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0092 | 0.91864 | 9.059 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.91905 | 8.73 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.82783 | 17.872 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0066 | 0.92551 | 8.104 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.83356 | 17.386 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.83928 | 16.806 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0091 | 0.92314 | 8.599 | Yes
Active | 2025W1-N11-WVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.83821 | 16.898 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87245 | 13.365 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87101 | 13.592 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87087 | 13.538 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.86212 | 14.51 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99429 | 0.81885 | 17.544 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99429 | 0.8279 | 16.639 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99429 | 0.83228 | 16.201 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99429 | 0.84474 | 14.955 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99429 | 0.85232 | 14.197 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99429 | 0.85661 | 13.768 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99429 | 0.85872 | 13.557 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0088 | 0.85317 | 15.563 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.86413 | 14.172 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.8645 | 14.162 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.87017 | 13.58 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.8572 | 14.294 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87036 | 13.62 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.84743 | 15.352 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.001 | 0.85711 | 14.384 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.84143 | 16.554 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99689 | 0.81806 | 17.882 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99689 | 0.8283 | 16.858 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99689 | 0.85651 | 14.038 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99689 | 0.86572 | 13.116 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.82555 | 17.727 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0092 | 0.86419 | 14.498 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86983 | 13.551 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.83079 | 17.139 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.83338 | 16.881 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.85927 | 14.889 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.85269 | 14.931 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.86129 | 14.072 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.86082 | 14.51 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.86585 | 14.088 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87014 | 13.648 | Yes
Active | 2025W1-N11-WVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.8694 | 13.713 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99579 | 0.9002 | 9.559 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.89922 | 9.617 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.89802 | 9.666 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99576 | 0.90029 | 9.546 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98615 | 0.85008 | 13.607 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98615 | 0.85719 | 12.896 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98615 | 0.87479 | 11.137 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98615 | 0.87992 | 10.623 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98615 | 0.89289 | 9.327 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98615 | 0.89485 | 9.13 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98615 | 0.89726 | 8.89 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99719 | 0.87679 | 12.04 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99681 | 0.90378 | 9.303 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.90373 | 9.319 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.89877 | 9.671 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99329 | 0.89449 | 9.881 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.89581 | 9.856 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99255 | 0.88996 | 10.259 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99255 | 0.88997 | 10.258 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99645 | 0.87313 | 12.332 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98636 | 0.83839 | 14.798 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98636 | 0.85666 | 12.97 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98636 | 0.88378 | 10.258 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98636 | 0.89473 | 9.164 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.88751 | 10.378 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.90048 | 9.697 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.89861 | 9.674 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97301 | 0.84289 | 13.012 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97301 | 0.85375 | 11.926 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.87779 | 11.434 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99121 | 0.88821 | 10.3 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99121 | 0.88874 | 10.247 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.89994 | 9.508 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99697 | 0.90395 | 9.302 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.89839 | 9.666 | Yes
Active | 2025W1-N11-WVD243108 | 243108 | 05STRLN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99495 | 0.89803 | 9.693 | Yes
Active | 2025W1-N11-WVD243110 | 243110 | 05STIFFI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0052 | 0.92327 | 8.192 | Yes
Active | 2025W1-N11-WVD243110 | 243110 | 05STIFFI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0054 | 0.91676 | 8.867 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99994 | 0.91896 | 8.098 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99693 | 0.8935 | 10.343 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99693 | 0.89379 | 10.314 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99693 | 0.9044 | 9.252 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99693 | 0.91033 | 8.66 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99693 | 0.91356 | 8.337 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.91016 | 9.058 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99895 | 0.9178 | 8.115 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.90996 | 8.394 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99935 | 0.91903 | 8.032 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99851 | 0.91326 | 8.525 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99851 | 0.91821 | 8.029 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.90334 | 9.717 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99724 | 0.88738 | 10.985 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.8911 | 10.614 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99724 | 0.91532 | 8.191 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.89865 | 9.899 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.91909 | 8.185 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99518 | 0.8921 | 10.308 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99518 | 0.89554 | 9.964 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.91112 | 8.803 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.91332 | 8.486 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99819 | 0.91768 | 8.05 | Yes
Active | 2025W1-N11-WVD243117 | 243117 | 05SULFRS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9995 | 0.91849 | 8.101 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.89826 | 9.914 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.89725 | 9.973 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.89611 | 10.019 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99723 | 0.89849 | 9.874 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98637 | 0.84773 | 13.864 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98637 | 0.85295 | 13.342 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98637 | 0.87409 | 11.228 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98637 | 0.8764 | 10.997 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98637 | 0.88875 | 9.762 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98637 | 0.89146 | 9.491 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98637 | 0.89412 | 9.225 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99893 | 0.87386 | 12.507 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99851 | 0.9023 | 9.622 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99863 | 0.90224 | 9.639 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.89699 | 10.013 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.89266 | 10.226 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99591 | 0.89371 | 10.22 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.8876 | 10.64 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99399 | 0.88793 | 10.606 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.87043 | 12.78 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98672 | 0.83613 | 15.058 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.85243 | 13.429 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98672 | 0.88009 | 10.663 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98672 | 0.89169 | 9.503 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.88421 | 10.848 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99916 | 0.89837 | 10.078 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.8966 | 10.034 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97595 | 0.84043 | 13.552 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97595 | 0.85119 | 12.475 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.87675 | 11.746 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99245 | 0.88588 | 10.657 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99245 | 0.88611 | 10.634 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99643 | 0.89809 | 9.834 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99867 | 0.90246 | 9.621 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99661 | 0.89637 | 10.024 | Yes
Active | 2025W1-N11-WVD243122 | 243122 | 05SW LIM | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9965 | 0.89599 | 10.051 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99627 | 0.90432 | 9.195 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99589 | 0.90327 | 9.262 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.90231 | 9.299 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9961 | 0.9033 | 9.28 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98731 | 0.85631 | 13.1 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98731 | 0.86279 | 12.452 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98731 | 0.87953 | 10.778 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98731 | 0.88477 | 10.254 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98731 | 0.89722 | 9.008 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98731 | 0.89929 | 8.801 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98731 | 0.9015 | 8.581 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99758 | 0.88169 | 11.588 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99682 | 0.90637 | 9.045 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.90635 | 9.059 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99589 | 0.90255 | 9.334 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.89833 | 9.538 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99496 | 0.9 | 9.496 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9933 | 0.8944 | 9.89 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9933 | 0.8944 | 9.89 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99691 | 0.87809 | 11.882 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98729 | 0.84478 | 14.251 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.86207 | 12.522 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98729 | 0.88838 | 9.891 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98729 | 0.89899 | 8.83 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99219 | 0.89205 | 10.014 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99779 | 0.90447 | 9.332 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.90279 | 9.308 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97411 | 0.84914 | 12.497 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97411 | 0.85962 | 11.449 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.88195 | 11.012 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99221 | 0.89292 | 9.929 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.89341 | 9.88 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.90295 | 9.246 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.90664 | 9.04 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99561 | 0.90255 | 9.306 | Yes
Active | 2025W1-N11-WVD243125 | 243125 | 05THAYER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.90218 | 9.334 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.89416 | 9.769 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.89316 | 9.831 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99076 | 0.89202 | 9.875 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99181 | 0.89396 | 9.785 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98143 | 0.84354 | 13.79 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98143 | 0.84961 | 13.183 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98143 | 0.86931 | 11.213 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98143 | 0.87286 | 10.857 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98143 | 0.8855 | 9.593 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98143 | 0.88809 | 9.334 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98143 | 0.89053 | 9.09 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99329 | 0.87019 | 12.31 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99281 | 0.89746 | 9.536 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99293 | 0.89742 | 9.552 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99155 | 0.89268 | 9.887 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98932 | 0.88831 | 10.101 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99044 | 0.88966 | 10.078 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98862 | 0.88367 | 10.495 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98862 | 0.88399 | 10.463 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.86651 | 12.61 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9817 | 0.83184 | 14.986 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9817 | 0.84896 | 13.274 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9817 | 0.87668 | 10.501 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9817 | 0.88818 | 9.351 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9874 | 0.88064 | 10.676 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99354 | 0.89431 | 9.924 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9914 | 0.89252 | 9.888 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96947 | 0.8362 | 13.328 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96947 | 0.84692 | 12.255 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98806 | 0.87182 | 11.624 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98731 | 0.88222 | 10.509 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.88245 | 10.486 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.89357 | 9.747 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.993 | 0.89767 | 9.533 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.89234 | 9.88 | Yes
Active | 2025W1-N11-WVD243136 | 243136 | 05W LIMA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.89196 | 9.908 | Yes
Active | 2025W1-N11-WVD243137 | 243137 | 05W.END FOS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0059 | 0.92124 | 8.469 | Yes
Active | 2025W1-N11-WVD243137 | 243137 | 05W.END FOS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0062 | 0.91421 | 9.201 | Yes
Active | 2025W1-N11-WVD243137 | 243137 | 05W.END FOS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92504 | 8.118 | Yes
Active | 2025W1-N11-WVD243137 | 243137 | 05W.END FOS1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.91918 | 8.127 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98956 | 0.89235 | 9.721 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98956 | 0.89854 | 9.103 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98956 | 0.90181 | 8.776 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98956 | 0.90793 | 8.164 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99425 | 0.91392 | 8.032 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.90954 | 8.013 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99404 | 0.90544 | 8.859 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.89217 | 9.945 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99162 | 0.89413 | 9.749 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.89671 | 9.674 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99379 | 0.89567 | 9.811 | Yes
Active | 2025W1-N11-WVD243144 | 243144 | 05WCAMBR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99379 | 0.90197 | 9.182 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99977 | 0.89935 | 10.041 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.8972 | 10.287 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.89704 | 10.279 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.89109 | 10.912 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99467 | 0.85346 | 14.121 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99467 | 0.86227 | 13.24 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99467 | 0.86663 | 12.804 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99467 | 0.87545 | 11.923 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99467 | 0.88775 | 10.692 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99467 | 0.88815 | 10.652 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99467 | 0.88858 | 10.609 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.88241 | 11.798 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99979 | 0.89265 | 10.714 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99987 | 0.89292 | 10.696 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99919 | 0.88921 | 10.998 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99126 | 0.8747 | 11.656 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99957 | 0.892 | 10.757 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99902 | 0.88362 | 11.54 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99902 | 0.89142 | 10.76 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.87198 | 12.828 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99685 | 0.85277 | 14.408 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99685 | 0.8623 | 13.455 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99685 | 0.8858 | 11.105 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99685 | 0.89493 | 10.192 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99899 | 0.8596 | 13.939 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.89088 | 10.983 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99954 | 0.89758 | 10.197 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99886 | 0.86418 | 13.468 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.8669 | 13.197 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.88819 | 11.263 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.88393 | 11.478 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99871 | 0.8908 | 10.791 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99982 | 0.89019 | 10.963 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.89389 | 10.616 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.89676 | 10.324 | Yes
Active | 2025W1-N11-WVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99997 | 0.89612 | 10.385 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99865 | 0.91826 | 8.039 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.91065 | 8.628 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99484 | 0.81784 | 17.7 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99568 | 0.81873 | 17.695 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.81997 | 17.472 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.80916 | 18.764 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.90065 | 9.344 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97563 | 0.75552 | 22.011 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97563 | 0.7677 | 20.793 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97563 | 0.77838 | 19.726 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97563 | 0.78743 | 18.82 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97563 | 0.80312 | 17.252 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97563 | 0.80571 | 16.992 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97563 | 0.80958 | 16.605 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97563 | 0.88682 | 8.881 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97563 | 0.89091 | 8.472 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99884 | 0.79067 | 20.816 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99405 | 0.8107 | 18.335 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.81118 | 18.333 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.91592 | 8.151 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99454 | 0.82063 | 17.391 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99161 | 0.81247 | 17.914 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99161 | 0.90692 | 8.468 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.91445 | 8.154 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99353 | 0.81136 | 18.216 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.80004 | 19.133 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99138 | 0.81401 | 17.737 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99789 | 0.78337 | 21.451 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9814 | 0.7547 | 22.67 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9814 | 0.77703 | 20.437 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9814 | 0.79505 | 18.635 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9814 | 0.81673 | 16.467 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99447 | 0.88882 | 10.564 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.76455 | 22.707 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99878 | 0.80904 | 18.973 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.81364 | 17.97 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99167 | 0.77856 | 21.311 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99167 | 0.77859 | 21.308 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.8098 | 19.073 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.9146 | 8.593 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.79848 | 19.053 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98901 | 0.8112 | 17.781 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99728 | 0.89832 | 9.896 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.90065 | 9.344 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99716 | 0.91175 | 8.541 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99713 | 0.91226 | 8.487 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.80743 | 18.714 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99458 | 0.90921 | 8.537 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9955 | 0.81282 | 18.269 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.81818 | 17.721 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9972 | 0.90547 | 9.173 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99655 | 0.91312 | 8.343 | Yes
Active | 2025W1-N11-WVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.81708 | 17.815 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.89919 | 10.329 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.89809 | 10.428 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.89781 | 10.414 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.89438 | 10.775 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0021 | 0.85858 | 14.349 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0021 | 0.8629 | 13.918 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0021 | 0.88312 | 11.896 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0021 | 0.88559 | 11.648 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0021 | 0.88696 | 11.511 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0021 | 0.89855 | 10.353 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0021 | 0.90003 | 10.204 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0041 | 0.8789 | 12.523 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.89705 | 10.52 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.89717 | 10.522 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.89477 | 10.679 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9959 | 0.88551 | 11.039 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89376 | 10.758 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99976 | 0.88622 | 11.354 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99976 | 0.89084 | 10.891 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.87254 | 13.119 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99991 | 0.84766 | 15.225 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99991 | 0.85868 | 14.122 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99991 | 0.88845 | 11.146 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99991 | 0.89919 | 10.071 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99762 | 0.87148 | 12.615 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.89517 | 10.89 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.89726 | 10.474 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99367 | 0.85551 | 13.816 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99367 | 0.86174 | 13.193 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.88083 | 11.949 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99901 | 0.88584 | 11.318 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99901 | 0.88977 | 10.924 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.89377 | 10.76 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.89785 | 10.482 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.89748 | 10.467 | Yes
Active | 2025W1-N11-WVD243147 | 243147 | 05WILDCRK SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.89695 | 10.513 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.89508 | 11.058 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.89409 | 11.164 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.894 | 11.131 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.88907 | 11.642 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.004 | 0.85414 | 14.985 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.004 | 0.85545 | 14.853 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.004 | 0.87131 | 13.267 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.004 | 0.87903 | 12.495 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.004 | 0.88386 | 12.012 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.004 | 0.89194 | 11.204 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.004 | 0.89319 | 11.08 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0075 | 0.87514 | 13.233 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.89159 | 11.375 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.89178 | 11.374 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.89009 | 11.47 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99788 | 0.87876 | 11.912 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.88924 | 11.543 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.88075 | 12.241 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.88744 | 11.572 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.86751 | 13.958 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0028 | 0.84519 | 15.756 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.85149 | 15.125 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0028 | 0.88343 | 11.932 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0028 | 0.89487 | 10.788 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.86111 | 13.999 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88956 | 11.784 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.89293 | 11.22 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99798 | 0.85188 | 14.61 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99798 | 0.85632 | 14.166 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.87844 | 12.61 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.88056 | 12.196 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.88645 | 11.606 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.88832 | 11.636 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.89262 | 11.323 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.8935 | 11.203 | Yes
Active | 2025W1-N11-WVD243148 | 243148 | 05WINDFL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.8929 | 11.257 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0089 | 0.92819 | 8.075 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.83603 | 16.975 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.83595 | 17.091 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.83708 | 16.885 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.82547 | 18.25 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.91618 | 8.916 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98903 | 0.77579 | 21.324 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98903 | 0.78641 | 20.262 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98903 | 0.79412 | 19.49 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98903 | 0.80545 | 18.357 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98903 | 0.81853 | 17.049 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98903 | 0.81883 | 17.02 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98903 | 0.82476 | 16.426 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98903 | 0.90368 | 8.535 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98903 | 0.90478 | 8.425 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0098 | 0.81186 | 19.796 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.82709 | 17.809 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.82761 | 17.802 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.83828 | 16.795 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.8283 | 17.402 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.91968 | 8.264 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.82951 | 17.537 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.81325 | 18.841 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.82629 | 17.537 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.80185 | 20.642 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99394 | 0.77517 | 21.877 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99394 | 0.7916 | 20.235 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99394 | 0.8159 | 17.804 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99394 | 0.83121 | 16.273 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.90659 | 10.03 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.78375 | 21.844 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.01 | 0.8281 | 18.19 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.83214 | 17.235 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.79342 | 20.838 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.79478 | 20.702 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0103 | 0.82532 | 18.493 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0103 | 0.92657 | 8.368 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.81409 | 18.601 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.82569 | 17.441 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.91588 | 9.267 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.91618 | 8.916 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.92741 | 8.11 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.92791 | 8.058 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.8236 | 18.215 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.9229 | 8.285 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.82937 | 17.726 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.83527 | 17.127 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.92064 | 8.776 | Yes
Active | 2025W1-N11-WVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.83417 | 17.221 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.91902 | 8.384 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.82683 | 17.326 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.82986 | 17.176 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.83093 | 16.973 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.82045 | 18.219 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90953 | 9.073 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98188 | 0.76675 | 21.514 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98188 | 0.77872 | 20.316 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98188 | 0.7895 | 19.238 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98188 | 0.79854 | 18.334 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98188 | 0.81425 | 16.763 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98188 | 0.81649 | 16.539 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98188 | 0.82032 | 16.156 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98188 | 0.89554 | 8.634 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98188 | 0.89949 | 8.239 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0046 | 0.80269 | 20.191 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.82206 | 17.801 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.82252 | 17.798 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.8323 | 16.816 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.82357 | 17.427 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99783 | 0.91532 | 8.252 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99957 | 0.82269 | 17.687 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99733 | 0.8111 | 18.624 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99733 | 0.82485 | 17.248 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.79474 | 20.89 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98776 | 0.76607 | 22.169 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98776 | 0.78826 | 19.95 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98776 | 0.80694 | 18.082 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98776 | 0.82786 | 15.99 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.89819 | 10.241 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99765 | 0.7758 | 22.185 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.82027 | 18.432 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99842 | 0.8223 | 17.611 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99768 | 0.78989 | 20.779 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99768 | 0.78991 | 20.778 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.82074 | 18.544 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0062 | 0.92244 | 8.373 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99521 | 0.80991 | 18.53 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99521 | 0.82249 | 17.272 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.90748 | 9.569 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90953 | 9.073 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.92006 | 8.3 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.92056 | 8.247 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.81878 | 18.176 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.91756 | 8.298 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.82411 | 17.733 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.8293 | 17.204 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.91388 | 8.92 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.92132 | 8.115 | Yes
Active | 2025W1-N11-WVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.82824 | 17.295 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99172 | 0.90821 | 8.351 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98623 | 0.87936 | 10.687 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98623 | 0.88647 | 9.976 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98623 | 0.88965 | 9.658 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98623 | 0.89628 | 8.996 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98623 | 0.90609 | 8.014 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98623 | 0.90614 | 8.01 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98623 | 0.90614 | 8.009 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99159 | 0.90262 | 8.897 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99141 | 0.90948 | 8.193 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99148 | 0.90967 | 8.181 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99056 | 0.9063 | 8.427 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9848 | 0.89453 | 9.026 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.90879 | 8.238 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99064 | 0.90235 | 8.829 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99064 | 0.90652 | 8.412 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99163 | 0.89325 | 9.839 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98869 | 0.87888 | 10.981 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98869 | 0.88314 | 10.555 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98869 | 0.90554 | 8.315 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99071 | 0.88411 | 10.66 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.90793 | 8.428 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99073 | 0.88473 | 10.599 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99073 | 0.88962 | 10.11 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.90544 | 8.685 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.90284 | 8.764 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99047 | 0.90623 | 8.425 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99141 | 0.90758 | 8.383 | Yes
Active | 2025W1-N11-WVD243151 | 243151 | 05WMILLS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.91038 | 8.124 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.89618 | 9.659 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.8953 | 9.7 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9916 | 0.89378 | 9.781 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99271 | 0.89876 | 9.394 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98267 | 0.84721 | 13.546 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98267 | 0.85346 | 12.921 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98267 | 0.87231 | 11.036 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98267 | 0.87567 | 10.7 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98267 | 0.88569 | 9.698 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98267 | 0.88948 | 9.319 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98267 | 0.89231 | 9.036 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99424 | 0.87332 | 12.092 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.90328 | 9.144 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.90315 | 9.166 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99251 | 0.89505 | 9.746 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.89085 | 9.962 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.89176 | 9.953 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9894 | 0.88569 | 10.372 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9894 | 0.88624 | 10.316 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99347 | 0.86957 | 12.39 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98312 | 0.83643 | 14.669 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98312 | 0.853 | 13.012 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98312 | 0.87969 | 10.343 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98312 | 0.88993 | 9.319 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.988 | 0.88108 | 10.692 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99444 | 0.89585 | 9.859 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.89454 | 9.777 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97528 | 0.84269 | 13.259 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97528 | 0.85275 | 12.253 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98988 | 0.87496 | 11.492 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98763 | 0.88396 | 10.367 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98763 | 0.88399 | 10.363 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99198 | 0.89842 | 9.356 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.90316 | 9.151 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99187 | 0.89427 | 9.761 | Yes
Active | 2025W1-N11-WVD243152 | 243152 | 05W.MOULTON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.89393 | 9.782 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88266 | 12.443 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.88202 | 12.558 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88211 | 12.499 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.8752 | 13.254 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.83443 | 16.731 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0017 | 0.84281 | 15.893 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0017 | 0.84633 | 15.54 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0017 | 0.86016 | 14.157 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0017 | 0.87188 | 12.986 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0017 | 0.87406 | 12.768 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0017 | 0.87499 | 12.674 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0091 | 0.86242 | 14.664 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.87731 | 12.971 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.87759 | 12.961 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.87754 | 12.925 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99891 | 0.86391 | 13.5 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87633 | 13.022 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.86637 | 13.906 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0054 | 0.87637 | 12.906 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.8527 | 15.585 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.83178 | 17.092 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0027 | 0.83784 | 16.486 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0027 | 0.86801 | 13.47 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0027 | 0.88158 | 12.113 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.84005 | 16.473 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0092 | 0.87527 | 13.391 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.8801 | 12.639 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.84173 | 16.126 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.84336 | 15.963 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0081 | 0.86922 | 13.886 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.86639 | 13.857 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.005 | 0.87543 | 12.953 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87416 | 13.268 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.8787 | 12.889 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88147 | 12.598 | Yes
Active | 2025W1-N11-WVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88072 | 12.665 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99974 | 0.90427 | 9.548 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99947 | 0.90316 | 9.631 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99898 | 0.90255 | 9.643 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99944 | 0.90141 | 9.804 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9956 | 0.8606 | 13.5 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9956 | 0.86642 | 12.918 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9956 | 0.88582 | 10.978 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9956 | 0.88845 | 10.715 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9956 | 0.89445 | 10.115 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9956 | 0.90214 | 9.346 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9956 | 0.904 | 9.16 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0012 | 0.88286 | 11.83 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99985 | 0.90423 | 9.562 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99998 | 0.90427 | 9.571 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99909 | 0.90125 | 9.784 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99546 | 0.89497 | 10.049 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99852 | 0.89949 | 9.902 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.89317 | 10.375 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99692 | 0.89505 | 10.187 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.87817 | 12.247 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99423 | 0.84897 | 14.526 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99423 | 0.86384 | 13.039 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99423 | 0.89129 | 10.294 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99423 | 0.90178 | 9.245 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99534 | 0.88567 | 10.967 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.90263 | 9.862 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99932 | 0.9026 | 9.672 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98443 | 0.85535 | 12.908 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98443 | 0.86402 | 12.041 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99627 | 0.88359 | 11.268 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.89249 | 10.354 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99603 | 0.89381 | 10.222 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99873 | 0.90096 | 9.778 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.90474 | 9.543 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99923 | 0.90251 | 9.672 | Yes
Active | 2025W1-N11-WVD243155 | 243155 | 05W.NEWTONSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.90208 | 9.707 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.89486 | 9.719 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99168 | 0.89385 | 9.782 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99098 | 0.89272 | 9.825 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.992 | 0.89457 | 9.743 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98175 | 0.84444 | 13.731 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98175 | 0.85055 | 13.121 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98175 | 0.87001 | 11.174 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98175 | 0.8737 | 10.805 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98175 | 0.88631 | 9.544 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98175 | 0.88887 | 9.288 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98175 | 0.89129 | 9.046 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99348 | 0.87101 | 12.247 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.89803 | 9.495 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.89799 | 9.511 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99175 | 0.89334 | 9.84 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.88898 | 10.054 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99065 | 0.89037 | 10.028 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98885 | 0.88441 | 10.443 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98885 | 0.88471 | 10.413 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.86732 | 12.548 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98199 | 0.83277 | 14.923 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98199 | 0.84989 | 13.211 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98199 | 0.8775 | 10.449 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98199 | 0.88894 | 9.306 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98764 | 0.88143 | 10.621 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99373 | 0.895 | 9.873 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99161 | 0.89322 | 9.838 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96968 | 0.83712 | 13.257 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96968 | 0.84781 | 12.188 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98821 | 0.8725 | 11.571 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98756 | 0.88297 | 10.459 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98756 | 0.88322 | 10.435 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.89419 | 9.705 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.89824 | 9.492 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.89304 | 9.831 | Yes
Active | 2025W1-N11-WVD243157 | 243157 | 05WOODLA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99125 | 0.89266 | 9.859 | Yes
Active | 2025W1-N11-WVD243158 | 243158 | 05WOOSTE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98242 | 0.89952 | 8.29 | Yes
Active | 2025W1-N11-WVD243158 | 243158 | 05WOOSTE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98523 | 0.89916 | 8.608 | Yes
Active | 2025W1-N11-WVD243158 | 243158 | 05WOOSTE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98523 | 0.89966 | 8.557 | Yes
Active | 2025W1-N11-WVD243158 | 243158 | 05WOOSTE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98724 | 0.90328 | 8.396 | Yes
Active | 2025W1-N11-WVD243158 | 243158 | 05WOOSTE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98731 | 0.90106 | 8.625 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.88157 | 12.493 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87953 | 12.734 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87962 | 12.695 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87198 | 13.507 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0012 | 0.8262 | 17.496 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0012 | 0.83703 | 16.412 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0012 | 0.8414 | 15.975 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0012 | 0.85314 | 14.802 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0012 | 0.86778 | 13.337 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0012 | 0.86863 | 13.253 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0012 | 0.86902 | 13.213 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 1.0012 | 0.91163 | 8.953 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0076 | 0.85987 | 14.773 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.87384 | 13.267 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87418 | 13.244 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.8708 | 13.527 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.85115 | 14.102 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87322 | 13.303 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86295 | 14.262 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0056 | 0.87427 | 13.131 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.84879 | 15.847 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.82507 | 17.798 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.003 | 0.83894 | 16.411 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.003 | 0.86394 | 13.911 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.003 | 0.87823 | 12.482 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.83364 | 17.179 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.87191 | 13.583 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.87921 | 12.698 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0049 | 0.84133 | 16.361 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.84196 | 16.298 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.86865 | 13.898 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.86302 | 14.213 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0051 | 0.87332 | 13.183 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.87081 | 13.573 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87541 | 13.145 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.879 | 12.78 | Yes
Active | 2025W1-N11-WVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.87819 | 12.856 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0126 | 0.8847 | 12.784 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0133 | 0.88244 | 13.089 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0129 | 0.88241 | 13.047 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0136 | 0.87444 | 13.915 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.004 | 0.82899 | 17.504 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.004 | 0.83895 | 16.508 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.004 | 0.8447 | 15.933 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.004 | 0.85554 | 14.849 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.004 | 0.86903 | 13.5 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.004 | 0.86955 | 13.448 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.004 | 0.87142 | 13.261 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 1.004 | 0.9198 | 8.423 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0144 | 0.86412 | 15.026 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0127 | 0.87634 | 13.638 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0129 | 0.87669 | 13.62 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0117 | 0.87703 | 13.468 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.85905 | 14.237 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0125 | 0.8771 | 13.538 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.86395 | 14.667 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0106 | 0.87494 | 13.569 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0135 | 0.8519 | 16.163 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.82817 | 17.885 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.007 | 0.84197 | 16.505 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.007 | 0.86774 | 13.928 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.007 | 0.87994 | 12.708 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.011 | 0.83623 | 17.476 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0147 | 0.8749 | 13.982 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0121 | 0.88238 | 12.967 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0107 | 0.84423 | 16.65 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0107 | 0.84538 | 16.535 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0144 | 0.87151 | 14.292 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0105 | 0.86537 | 14.511 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0105 | 0.87531 | 13.517 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0128 | 0.87324 | 13.956 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0133 | 0.87796 | 13.53 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0132 | 0.88183 | 13.136 | Yes
Active | 2025W1-N11-WVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0131 | 0.88104 | 13.21 | Yes
Active | 2025W1-N11-WVD243211 | 243211 | 05ALLEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97865 | 0.8657 | 11.296 | Yes
Active | 2025W1-N11-WVD243211 | 243211 | 05ALLEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97865 | 0.89645 | 8.22 | Yes
Active | 2025W1-N11-WVD243211 | 243211 | 05ALLEN | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96066 | 0.87661 | 8.405 | Yes
Active | 2025W1-N11-WVD243225 | 243225 | 05KEYSTN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99558 | 0.89583 | 9.976 | Yes
Active | 2025W1-N11-WVD243228 | 243228 | 05MERIDN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97561 | 0.86037 | 11.524 | Yes
Active | 2025W1-N11-WVD243228 | 243228 | 05MERIDN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97333 | 0.88984 | 8.349 | Yes
Active | 2025W1-N11-WVD243231 | 243231 | 05ROB PK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98026 | 0.86812 | 11.214 | Yes
Active | 2025W1-N11-WVD243231 | 243231 | 05ROB PK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97839 | 0.89827 | 8.012 | Yes
Active | 2025W1-N11-WVD243232 | 243232 | 05SORENS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97842 | 0.86265 | 11.577 | Yes
Active | 2025W1-N11-WVD243232 | 243232 | 05SORENS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97598 | 0.89504 | 8.094 | Yes
Active | 2025W1-N11-WVD243232 | 243232 | 05SORENS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95846 | 0.87335 | 8.511 | Yes
Active | 2025W1-N11-WVD243237 | 243237 | 05ADAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9964 | 0.90816 | 8.825 | Yes
Active | 2025W1-N11-WVD243241 | 243241 | 05ALBION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0077 | 0.90113 | 10.658 | Yes
Active | 2025W1-N11-WVD243241 | 243241 | 05ALBION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0062 | 0.92586 | 8.031 | Yes
Active | 2025W1-N11-WVD243242 | 243242 | 05ALLEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98529 | 0.87486 | 11.043 | Yes
Active | 2025W1-N11-WVD243242 | 243242 | 05ALLEN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96795 | 0.88629 | 8.166 | Yes
Active | 2025W1-N11-WVD243246 | 243246 | 05AUBUNC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99656 | 0.88442 | 11.214 | Yes
Active | 2025W1-N11-WVD243246 | 243246 | 05AUBUNC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99467 | 0.91439 | 8.028 | Yes
Active | 2025W1-N11-WVD243247 | 243247 | 05AUBURN1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99675 | 0.88487 | 11.188 | Yes
Active | 2025W1-N11-WVD243251 | 243251 | 05BIXLER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0079 | 0.89586 | 11.206 | Yes
Active | 2025W1-N11-WVD243251 | 243251 | 05BIXLER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0062 | 0.92353 | 8.263 | Yes
Active | 2025W1-N11-WVD243254 | 243254 | 05BURNWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0047 | 0.90239 | 10.226 | Yes
Active | 2025W1-N11-WVD243263 | 243263 | 05COLUMBIA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99045 | 0.87749 | 11.296 | Yes
Active | 2025W1-N11-WVD243263 | 243263 | 05COLUMBIA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98882 | 0.90583 | 8.298 | Yes
Active | 2025W1-N11-WVD243267 | 243267 | 05COUNTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99468 | 0.88259 | 11.21 | Yes
Active | 2025W1-N11-WVD243279 | 243279 | 05DIAMND | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98743 | 0.89077 | 9.666 | Yes
Active | 2025W1-N11-WVD243284 | 243284 | 05DUPONT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99301 | 0.88075 | 11.226 | Yes
Active | 2025W1-N11-WVD243288 | 243288 | 05EGE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0021 | 0.89252 | 10.962 | Yes
Active | 2025W1-N11-WVD243288 | 243288 | 05EGE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0005 | 0.91934 | 8.118 | Yes
Active | 2025W1-N11-WVD243291 | 243291 | 05ENGLER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99699 | 0.88127 | 11.572 | Yes
Active | 2025W1-N11-WVD243291 | 243291 | 05ENGLER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99522 | 0.91384 | 8.138 | Yes
Active | 2025W1-N11-WVD243291 | 243291 | 05ENGLER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97641 | 0.89435 | 8.206 | Yes
Active | 2025W1-N11-WVD243295 | 243295 | 05GARRETT N | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99771 | 0.88527 | 11.243 | Yes
Active | 2025W1-N11-WVD243295 | 243295 | 05GARRETT N | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99584 | 0.91489 | 8.094 | Yes
Active | 2025W1-N11-WVD243304 | 243304 | 05GUARDN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98758 | 0.89311 | 9.447 | Yes
Active | 2025W1-N11-WVD243305 | 243305 | 05HACIEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99002 | 0.87752 | 11.25 | Yes
Active | 2025W1-N11-WVD243306 | 243306 | 05HARPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98812 | 0.87562 | 11.251 | Yes
Active | 2025W1-N11-WVD243309 | 243309 | 05HILLCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99623 | 0.882 | 11.423 | Yes
Active | 2025W1-N11-WVD243309 | 243309 | 05HILLCR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97692 | 0.89456 | 8.237 | Yes
Active | 2025W1-N11-WVD243313 | 243313 | 05HUNT J | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98922 | 0.88056 | 10.865 | Yes
Active | 2025W1-N11-WVD243313 | 243313 | 05HUNT J | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99012 | 0.90944 | 8.068 | Yes
Active | 2025W1-N11-WVD243314 | 243314 | 05HUNTR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99459 | 0.88244 | 11.215 | Yes
Active | 2025W1-N11-WVD243314 | 243314 | 05HUNTR8 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99286 | 0.91247 | 8.039 | Yes
Active | 2025W1-N11-WVD243315 | 243315 | 05ILLINO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9895 | 0.87429 | 11.521 | Yes
Active | 2025W1-N11-WVD243315 | 243315 | 05ILLINO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98773 | 0.90585 | 8.188 | Yes
Active | 2025W1-N11-WVD243315 | 243315 | 05ILLINO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96802 | 0.88718 | 8.084 | Yes
Active | 2025W1-N11-WVD243316 | 243316 | 05INDUST PK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99646 | 0.88151 | 11.495 | Yes
Active | 2025W1-N11-WVD243316 | 243316 | 05INDUST PK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99469 | 0.91354 | 8.115 | Yes
Active | 2025W1-N11-WVD243316 | 243316 | 05INDUST PK1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97572 | 0.89503 | 8.069 | Yes
Active | 2025W1-N11-WVD243321 | 243321 | 05KENDAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.012 | 0.90064 | 11.139 | Yes
Active | 2025W1-N11-WVD243321 | 243321 | 05KENDAL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0103 | 0.92762 | 8.271 | Yes
Active | 2025W1-N11-WVD243326 | 243326 | 05LAOTTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99861 | 0.88756 | 11.105 | Yes
Active | 2025W1-N11-WVD243326 | 243326 | 05LAOTTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99694 | 0.91577 | 8.117 | Yes
Active | 2025W1-N11-WVD243330 | 243330 | 05LINCOLN1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98892 | 0.87727 | 11.165 | Yes
Active | 2025W1-N11-WVD243330 | 243330 | 05LINCOLN1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97037 | 0.88955 | 8.082 | Yes
Active | 2025W1-N11-WVD243334 | 243334 | 05MAGLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99206 | 0.89409 | 9.797 | Yes
Active | 2025W1-N11-WVD243338 | 243338 | 05MCKINLEY3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99888 | 0.88308 | 11.581 | Yes
Active | 2025W1-N11-WVD243338 | 243338 | 05MCKINLEY3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99711 | 0.91574 | 8.137 | Yes
Active | 2025W1-N11-WVD243338 | 243338 | 05MCKINLEY3 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97836 | 0.89623 | 8.213 | Yes
Active | 2025W1-N11-WVD243342 | 243342 | 05MILAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98391 | 0.87133 | 11.258 | Yes
Active | 2025W1-N11-WVD243342 | 243342 | 05MILAN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96447 | 0.88418 | 8.029 | Yes
Active | 2025W1-N11-WVD243361 | 243361 | 05RABER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98961 | 0.87614 | 11.347 | Yes
Active | 2025W1-N11-WVD243361 | 243361 | 05RABER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98796 | 0.90495 | 8.301 | Yes
Active | 2025W1-N11-WVD243363 | 243363 | 05REED | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99129 | 0.87915 | 11.215 | Yes
Active | 2025W1-N11-WVD243366 | 243366 | 05ROB PK12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99344 | 0.88112 | 11.231 | Yes
Active | 2025W1-N11-WVD243367 | 243367 | 05ROCKCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99209 | 0.88945 | 10.264 | Yes
Active | 2025W1-N11-WVD243372 | 243372 | 05SATURN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98825 | 0.87398 | 11.427 | Yes
Active | 2025W1-N11-WVD243372 | 243372 | 05SATURN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98657 | 0.90365 | 8.292 | Yes
Active | 2025W1-N11-WVD243375 | 243375 | 05SKINNRLKSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0083 | 0.90076 | 10.75 | Yes
Active | 2025W1-N11-WVD243375 | 243375 | 05SKINNRLKSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0067 | 0.92587 | 8.082 | Yes
Active | 2025W1-N11-WVD243377 | 243377 | 05SORENS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98626 | 0.87114 | 11.512 | Yes
Active | 2025W1-N11-WVD243377 | 243377 | 05SORENS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98451 | 0.90236 | 8.215 | Yes
Active | 2025W1-N11-WVD243377 | 243377 | 05SORENS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96434 | 0.88363 | 8.071 | Yes
Active | 2025W1-N11-WVD243378 | 243378 | 05SPY RUN2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99307 | 0.87896 | 11.411 | Yes
Active | 2025W1-N11-WVD243378 | 243378 | 05SPY RUN2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9913 | 0.91081 | 8.049 | Yes
Active | 2025W1-N11-WVD243378 | 243378 | 05SPY RUN2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97276 | 0.89275 | 8.002 | Yes
Active | 2025W1-N11-WVD243379 | 243379 | 05STATES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98977 | 0.87788 | 11.189 | Yes
Active | 2025W1-N11-WVD243379 | 243379 | 05STATES | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97069 | 0.89052 | 8.017 | Yes
Active | 2025W1-N11-WVD243381 | 243381 | 05SUMMIT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99521 | 0.88089 | 11.432 | Yes
Active | 2025W1-N11-WVD243381 | 243381 | 05SUMMIT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99343 | 0.91264 | 8.08 | Yes
Active | 2025W1-N11-WVD243383 | 243383 | 05TILLMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99153 | 0.88127 | 11.026 | Yes
Active | 2025W1-N11-WVD243383 | 243383 | 05TILLMA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99153 | 0.90599 | 8.554 | Yes
Active | 2025W1-N11-WVD243383 | 243383 | 05TILLMA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.91738 | 8.023 | Yes
Active | 2025W1-N11-WVD243383 | 243383 | 05TILLMA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.90681 | 8.328 | Yes
Active | 2025W1-N11-WVD243383 | 243383 | 05TILLMA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9776 | 0.89197 | 8.563 | Yes
Active | 2025W1-N11-WVD243384 | 243384 | 05TRIER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99044 | 0.87842 | 11.203 | Yes
Active | 2025W1-N11-WVD243387 | 243387 | 05VANBUR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99783 | 0.90808 | 8.974 | Yes
Active | 2025W1-N11-WVD243389 | 243389 | 05WALLEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99459 | 0.88097 | 11.362 | Yes
Active | 2025W1-N11-WVD243389 | 243389 | 05WALLEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99282 | 0.91246 | 8.036 | Yes
Active | 2025W1-N11-WVD243390 | 243390 | 05WAYNED | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99676 | 0.88141 | 11.535 | Yes
Active | 2025W1-N11-WVD243390 | 243390 | 05WAYNED | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.995 | 0.91425 | 8.075 | Yes
Active | 2025W1-N11-WVD243390 | 243390 | 05WAYNED | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97656 | 0.89435 | 8.221 | Yes
Active | 2025W1-N11-WVD243391 | 243391 | 05WAYNET | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99349 | 0.88017 | 11.332 | Yes
Active | 2025W1-N11-WVD243391 | 243391 | 05WAYNET | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97469 | 0.89247 | 8.222 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98773 | 0.83067 | 15.706 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98787 | 0.8222 | 16.567 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98679 | 0.82741 | 15.938 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99349 | 0.81023 | 18.327 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98582 | 0.90273 | 8.309 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97193 | 0.77328 | 19.866 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97193 | 0.78364 | 18.83 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97193 | 0.7849 | 18.704 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97193 | 0.80137 | 17.057 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97193 | 0.80145 | 17.049 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97193 | 0.81372 | 15.821 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97193 | 0.81654 | 15.539 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99107 | 0.80391 | 18.717 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98448 | 0.80696 | 17.751 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98544 | 0.80794 | 17.75 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98784 | 0.83126 | 15.658 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98491 | 0.82471 | 16.02 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.82009 | 16.536 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98331 | 0.80836 | 17.496 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98331 | 0.81838 | 16.494 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98985 | 0.79776 | 19.209 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97587 | 0.77296 | 20.291 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97587 | 0.78051 | 19.536 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97587 | 0.80828 | 16.759 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97587 | 0.81183 | 16.404 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98474 | 0.88901 | 9.573 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9821 | 0.78072 | 20.138 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9909 | 0.82308 | 16.782 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98677 | 0.82753 | 15.924 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97936 | 0.7813 | 19.806 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97936 | 0.78501 | 19.435 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99054 | 0.81712 | 17.342 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97803 | 0.79689 | 18.114 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97803 | 0.80593 | 17.21 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.9033 | 8.656 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98582 | 0.90273 | 8.309 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98844 | 0.80591 | 18.253 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98844 | 0.90516 | 8.328 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98749 | 0.81073 | 17.676 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98762 | 0.82229 | 16.533 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98908 | 0.90647 | 8.261 | Yes
Active | 2025W1-N11-WVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98725 | 0.82035 | 16.69 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98987 | 0.82672 | 16.316 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99017 | 0.82295 | 16.723 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98931 | 0.82569 | 16.362 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99273 | 0.81219 | 18.054 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98823 | 0.90146 | 8.677 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97271 | 0.76735 | 20.537 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97271 | 0.77796 | 19.475 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97271 | 0.78333 | 18.939 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97271 | 0.7967 | 17.601 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97271 | 0.8044 | 16.832 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97271 | 0.80901 | 16.371 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97271 | 0.81404 | 15.867 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97271 | 0.89085 | 8.186 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99359 | 0.80058 | 19.301 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98786 | 0.81221 | 17.566 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98851 | 0.81286 | 17.565 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99018 | 0.82749 | 16.269 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98677 | 0.82048 | 16.629 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98864 | 0.81339 | 17.525 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9881 | 0.8036 | 18.45 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9881 | 0.81558 | 17.252 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.79323 | 19.893 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97727 | 0.76696 | 21.032 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97727 | 0.77992 | 19.735 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97727 | 0.8047 | 17.258 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97727 | 0.81571 | 16.156 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98897 | 0.89055 | 9.842 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98503 | 0.77527 | 20.976 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99354 | 0.81835 | 17.519 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98874 | 0.8233 | 16.543 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98352 | 0.78125 | 20.226 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98352 | 0.78383 | 19.969 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.81475 | 17.879 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99355 | 0.91159 | 8.196 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98184 | 0.80031 | 18.153 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98184 | 0.81023 | 17.161 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.90214 | 8.972 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98823 | 0.90146 | 8.677 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98949 | 0.80956 | 17.993 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98949 | 0.90663 | 8.286 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9899 | 0.81492 | 17.498 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98984 | 0.82252 | 16.732 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.90614 | 8.562 | Yes
Active | 2025W1-N11-WVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9896 | 0.82117 | 16.843 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99568 | 0.84294 | 15.274 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9966 | 0.84097 | 15.564 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.84163 | 15.42 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.83261 | 16.462 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.91457 | 8.161 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97962 | 0.77986 | 19.976 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97962 | 0.79217 | 18.745 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97962 | 0.80054 | 17.908 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97962 | 0.81052 | 16.911 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97962 | 0.827 | 15.262 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97962 | 0.8293 | 15.033 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97962 | 0.83094 | 14.869 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97962 | 0.89787 | 8.176 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99896 | 0.81481 | 18.415 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99549 | 0.83443 | 16.106 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.83482 | 16.099 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99688 | 0.83607 | 16.082 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.8288 | 16.057 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.83424 | 16.077 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99327 | 0.82413 | 16.913 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99327 | 0.83705 | 15.622 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99838 | 0.80677 | 19.161 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98473 | 0.77923 | 20.551 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98473 | 0.79935 | 18.539 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98473 | 0.81904 | 16.569 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98473 | 0.83982 | 14.492 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.90239 | 9.291 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99295 | 0.78931 | 20.363 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99892 | 0.83188 | 16.705 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.84022 | 15.464 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.80109 | 19.153 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99262 | 0.80112 | 19.149 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.83139 | 16.889 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.82283 | 16.865 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99147 | 0.83474 | 15.673 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90209 | 10.133 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.91457 | 8.161 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99569 | 0.83122 | 16.447 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99651 | 0.83621 | 16.03 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99639 | 0.84043 | 15.596 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.9173 | 8.042 | Yes
Active | 2025W1-N11-WVD243455 | 243455 | 05CONES | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99627 | 0.83949 | 15.678 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98795 | 0.90421 | 8.374 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.89323 | 9.239 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98449 | 0.80364 | 18.085 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.90572 | 8.039 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98505 | 0.80287 | 18.218 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98395 | 0.80416 | 17.978 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98588 | 0.7939 | 19.198 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98415 | 0.88641 | 9.774 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9615 | 0.73613 | 22.537 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9615 | 0.75294 | 20.855 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9615 | 0.76635 | 19.515 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9615 | 0.77035 | 19.115 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9615 | 0.78768 | 17.381 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9615 | 0.87722 | 8.427 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98902 | 0.7649 | 22.412 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98813 | 0.90564 | 8.249 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98219 | 0.8998 | 8.239 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.79567 | 18.776 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98389 | 0.7961 | 18.778 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98673 | 0.9011 | 8.563 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98723 | 0.90475 | 8.248 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9873 | 0.90475 | 8.255 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98457 | 0.80524 | 17.932 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98132 | 0.79812 | 18.32 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98132 | 0.89406 | 8.726 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98495 | 0.89901 | 8.594 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.90491 | 8.283 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98279 | 0.79648 | 18.631 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98014 | 0.78612 | 19.401 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98014 | 0.80054 | 17.959 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.76648 | 22.253 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96791 | 0.73577 | 23.215 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96791 | 0.76604 | 20.187 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96791 | 0.76997 | 19.794 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96791 | 0.80267 | 16.524 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98224 | 0.8703 | 11.194 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98293 | 0.74992 | 23.301 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98592 | 0.90563 | 8.029 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.79188 | 19.66 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98324 | 0.80006 | 18.318 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9837 | 0.76681 | 21.689 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9837 | 0.76738 | 21.632 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.79793 | 19.513 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99306 | 0.90434 | 8.872 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97777 | 0.78362 | 19.415 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97777 | 0.7971 | 18.068 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98752 | 0.88284 | 10.468 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98262 | 0.9018 | 8.082 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98262 | 0.9018 | 8.082 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.9036 | 8.352 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98415 | 0.88641 | 9.774 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98652 | 0.89636 | 9.017 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98649 | 0.89689 | 8.96 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98367 | 0.79234 | 19.133 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98367 | 0.89479 | 8.888 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98489 | 0.79762 | 18.727 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98475 | 0.80234 | 18.241 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98661 | 0.89045 | 9.616 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98592 | 0.89807 | 8.784 | Yes
Active | 2025W1-N11-WVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98458 | 0.80128 | 18.33 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97898 | 0.8869 | 9.209 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98175 | 0.80894 | 17.281 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98197 | 0.80436 | 17.761 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98086 | 0.80748 | 17.338 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98496 | 0.79413 | 19.083 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97943 | 0.88648 | 9.295 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96369 | 0.74653 | 21.715 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96369 | 0.76066 | 20.303 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96369 | 0.76724 | 19.645 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96369 | 0.778 | 18.569 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96369 | 0.78768 | 17.601 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96369 | 0.87805 | 8.563 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96369 | 0.88203 | 8.165 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9857 | 0.77543 | 21.027 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97948 | 0.79369 | 18.579 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98019 | 0.79436 | 18.583 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98188 | 0.80975 | 17.213 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97856 | 0.80284 | 17.573 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97856 | 0.89499 | 8.357 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98204 | 0.9017 | 8.034 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97956 | 0.79992 | 17.965 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97699 | 0.78871 | 18.828 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97699 | 0.79984 | 17.715 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98531 | 0.77327 | 21.204 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96864 | 0.74617 | 22.246 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96864 | 0.76386 | 20.478 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96864 | 0.78106 | 18.758 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96864 | 0.79923 | 16.941 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97858 | 0.8722 | 10.639 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97647 | 0.7568 | 21.966 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9851 | 0.80108 | 18.403 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98067 | 0.80564 | 17.503 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97698 | 0.76402 | 21.296 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97698 | 0.76663 | 21.035 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98775 | 0.79877 | 18.897 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98775 | 0.90142 | 8.633 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97347 | 0.78251 | 19.096 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97347 | 0.79255 | 18.092 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98437 | 0.88655 | 9.782 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97943 | 0.88648 | 9.295 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98305 | 0.89794 | 8.512 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98301 | 0.89846 | 8.454 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98135 | 0.79134 | 19 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98135 | 0.89326 | 8.808 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98171 | 0.79643 | 18.529 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.80409 | 17.758 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98341 | 0.89216 | 9.125 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98256 | 0.90016 | 8.24 | Yes
Active | 2025W1-N11-WVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9814 | 0.80263 | 17.878 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98501 | 0.90449 | 8.052 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98158 | 0.89124 | 9.034 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9819 | 0.80935 | 17.255 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98204 | 0.80718 | 17.485 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98096 | 0.80866 | 17.231 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98295 | 0.79839 | 18.456 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98131 | 0.88729 | 9.402 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95993 | 0.74139 | 21.854 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95993 | 0.75972 | 20.021 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95993 | 0.77012 | 18.981 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95993 | 0.77577 | 18.416 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95993 | 0.79223 | 16.77 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.95993 | 0.87928 | 8.065 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.986 | 0.76969 | 21.631 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98038 | 0.80011 | 18.028 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98086 | 0.80054 | 18.032 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98364 | 0.90117 | 8.247 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98201 | 0.81007 | 17.193 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9786 | 0.8033 | 17.529 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9786 | 0.89336 | 8.523 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98222 | 0.89959 | 8.263 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98474 | 0.9046 | 8.015 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9799 | 0.8017 | 17.82 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97714 | 0.79142 | 18.572 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97714 | 0.80309 | 17.405 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98641 | 0.77153 | 21.488 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96525 | 0.74098 | 22.427 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96525 | 0.76752 | 19.772 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96525 | 0.77503 | 19.022 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96525 | 0.80437 | 16.088 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97848 | 0.87041 | 10.807 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97672 | 0.75647 | 22.025 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98515 | 0.80179 | 18.336 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98083 | 0.80613 | 17.47 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97971 | 0.76865 | 21.106 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97971 | 0.77039 | 20.932 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99016 | 0.8025 | 18.766 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99016 | 0.9032 | 8.696 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97449 | 0.78791 | 18.657 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97449 | 0.79861 | 17.588 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98472 | 0.88398 | 10.074 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98406 | 0.90358 | 8.048 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98131 | 0.88729 | 9.402 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98331 | 0.89604 | 8.727 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98326 | 0.89656 | 8.671 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9806 | 0.79674 | 18.387 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9806 | 0.89327 | 8.733 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9819 | 0.80207 | 17.983 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98173 | 0.80668 | 17.504 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98357 | 0.89085 | 9.272 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98285 | 0.89822 | 8.463 | Yes
Active | 2025W1-N11-WVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98155 | 0.80562 | 17.593 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98871 | 0.90277 | 8.594 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98658 | 0.81125 | 17.532 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98738 | 0.81173 | 17.564 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.81324 | 17.315 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.80231 | 18.641 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98605 | 0.89303 | 9.303 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96617 | 0.74873 | 21.744 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96617 | 0.76139 | 20.477 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96617 | 0.77239 | 19.378 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96617 | 0.78081 | 18.535 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96617 | 0.79568 | 17.048 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96617 | 0.87846 | 8.771 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96617 | 0.88393 | 8.224 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99074 | 0.78276 | 20.798 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98563 | 0.80356 | 18.207 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98612 | 0.80405 | 18.207 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.90794 | 8.121 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.81441 | 17.194 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9838 | 0.80705 | 17.675 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9838 | 0.89997 | 8.382 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98754 | 0.90613 | 8.141 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98539 | 0.80429 | 18.11 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98346 | 0.79393 | 18.953 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98346 | 0.80752 | 17.593 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.77727 | 21.262 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97227 | 0.74832 | 22.396 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97227 | 0.77122 | 20.106 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97227 | 0.78709 | 18.518 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97227 | 0.80937 | 16.291 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98581 | 0.88028 | 10.553 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98349 | 0.75867 | 22.482 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99058 | 0.80228 | 18.83 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98508 | 0.80717 | 17.792 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98341 | 0.77267 | 21.074 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98341 | 0.77291 | 21.05 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.80386 | 18.884 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9927 | 0.90684 | 8.585 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9802 | 0.79169 | 18.85 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9802 | 0.80401 | 17.619 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.89065 | 9.849 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98605 | 0.89303 | 9.303 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98884 | 0.9035 | 8.534 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.90401 | 8.48 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98631 | 0.80048 | 18.583 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98631 | 0.90075 | 8.556 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98719 | 0.80571 | 18.149 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98708 | 0.81122 | 17.586 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98891 | 0.89735 | 9.156 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9882 | 0.90492 | 8.329 | Yes
Active | 2025W1-N11-WVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9869 | 0.8101 | 17.68 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97946 | 0.88743 | 9.203 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98175 | 0.80741 | 17.433 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98199 | 0.80291 | 17.907 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98087 | 0.80601 | 17.485 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98495 | 0.79268 | 19.226 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97908 | 0.88529 | 9.378 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96413 | 0.74532 | 21.881 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96413 | 0.75932 | 20.48 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96413 | 0.76605 | 19.807 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96413 | 0.77673 | 18.739 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96413 | 0.78653 | 17.759 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96413 | 0.87754 | 8.659 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96413 | 0.88161 | 8.252 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98575 | 0.77393 | 21.182 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9795 | 0.79229 | 18.721 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98021 | 0.79296 | 18.725 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98369 | 0.90322 | 8.047 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98188 | 0.80826 | 17.362 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97854 | 0.80128 | 17.726 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97854 | 0.89442 | 8.412 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98205 | 0.90119 | 8.086 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97955 | 0.79835 | 18.12 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97696 | 0.78706 | 18.99 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97696 | 0.79827 | 17.869 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98534 | 0.77174 | 21.36 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96914 | 0.74496 | 22.418 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96914 | 0.76274 | 20.64 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96914 | 0.77982 | 18.932 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96914 | 0.79815 | 17.099 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97861 | 0.87146 | 10.715 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97652 | 0.7552 | 22.132 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98513 | 0.79944 | 18.569 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98065 | 0.80408 | 17.658 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97713 | 0.76264 | 21.449 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97713 | 0.76518 | 21.195 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98781 | 0.79724 | 19.057 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98781 | 0.90095 | 8.686 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97358 | 0.7811 | 19.248 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97358 | 0.79118 | 18.24 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98439 | 0.8859 | 9.849 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97908 | 0.88529 | 9.378 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98307 | 0.89737 | 8.57 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98302 | 0.89791 | 8.512 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98134 | 0.78992 | 19.141 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98134 | 0.89276 | 8.858 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98173 | 0.79501 | 18.672 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98168 | 0.80264 | 17.905 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98344 | 0.89157 | 9.187 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98258 | 0.89965 | 8.294 | Yes
Active | 2025W1-N11-WVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98142 | 0.80118 | 18.024 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97994 | 0.88795 | 9.199 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98223 | 0.80802 | 17.421 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98247 | 0.80353 | 17.895 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98136 | 0.80663 | 17.473 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98543 | 0.79329 | 19.214 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97957 | 0.88585 | 9.372 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96462 | 0.74589 | 21.873 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96462 | 0.75991 | 20.471 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96462 | 0.76664 | 19.798 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96462 | 0.77733 | 18.729 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96462 | 0.78714 | 17.748 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96462 | 0.87809 | 8.653 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96462 | 0.88216 | 8.246 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98623 | 0.77453 | 21.17 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97999 | 0.7929 | 18.709 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9807 | 0.79357 | 18.713 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.90376 | 8.042 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98237 | 0.80887 | 17.35 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97902 | 0.80189 | 17.713 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97902 | 0.89496 | 8.406 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98254 | 0.90172 | 8.081 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.79897 | 18.107 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97745 | 0.78767 | 18.978 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97745 | 0.79889 | 17.857 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98582 | 0.77233 | 21.349 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96963 | 0.74553 | 22.41 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96963 | 0.76332 | 20.63 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96963 | 0.78042 | 18.921 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96963 | 0.79876 | 17.087 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9791 | 0.87202 | 10.708 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97702 | 0.75579 | 22.123 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.80006 | 18.556 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98114 | 0.80469 | 17.645 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97762 | 0.76322 | 21.439 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97762 | 0.76577 | 21.185 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.79786 | 19.044 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98829 | 0.90148 | 8.681 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97407 | 0.7817 | 19.237 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97407 | 0.79178 | 18.229 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98488 | 0.88645 | 9.843 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97957 | 0.88585 | 9.372 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98356 | 0.89791 | 8.564 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98351 | 0.89845 | 8.506 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98182 | 0.79053 | 19.129 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98182 | 0.8933 | 8.853 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98222 | 0.79562 | 18.659 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.80325 | 17.892 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98392 | 0.89211 | 9.181 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98307 | 0.90018 | 8.289 | Yes
Active | 2025W1-N11-WVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9819 | 0.80179 | 18.011 | Yes
Active | 2025W1-N11-WVD243464 | 243464 | 05ADAMS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0015 | 0.91573 | 8.579 | Yes
Active | 2025W1-N11-WVD243464 | 243464 | 05ADAMS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0016 | 0.91345 | 8.819 | Yes
Active | 2025W1-N11-WVD243464 | 243464 | 05ADAMS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99988 | 0.91702 | 8.286 | Yes
Active | 2025W1-N11-WVD243464 | 243464 | 05ADAMS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99988 | 0.91874 | 8.115 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0025 | 0.91658 | 8.592 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.92182 | 8.068 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0022 | 0.9161 | 8.614 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.92117 | 8.107 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.92308 | 8.202 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.91916 | 8.411 | Yes
Active | 2025W1-N11-WVD243465 | 243465 | 05ADDISO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.91952 | 8.375 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.90719 | 8.517 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99013 | 0.81267 | 17.746 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99072 | 0.81053 | 18.018 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.81278 | 17.695 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.80012 | 19.264 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98705 | 0.89248 | 9.457 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9722 | 0.75073 | 22.147 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9722 | 0.76254 | 20.966 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9722 | 0.7707 | 20.151 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9722 | 0.78153 | 19.067 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9722 | 0.79325 | 17.895 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9722 | 0.80183 | 17.037 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9722 | 0.8826 | 8.96 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9722 | 0.88714 | 8.506 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99424 | 0.78362 | 21.063 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98861 | 0.80076 | 18.785 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.80135 | 18.785 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99261 | 0.91162 | 8.099 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99032 | 0.81426 | 17.606 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98691 | 0.80657 | 18.034 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98691 | 0.90228 | 8.463 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99096 | 0.90976 | 8.12 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98856 | 0.80294 | 18.562 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98695 | 0.79177 | 19.518 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98695 | 0.80472 | 18.223 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.77763 | 21.554 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97762 | 0.75023 | 22.739 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97762 | 0.76832 | 20.93 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97762 | 0.78815 | 18.947 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97762 | 0.806 | 17.162 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.88242 | 10.656 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98601 | 0.75947 | 22.654 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.80325 | 19.077 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98884 | 0.8089 | 17.994 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98593 | 0.76945 | 21.648 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98593 | 0.77086 | 21.507 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.80221 | 19.322 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99543 | 0.90843 | 8.7 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98334 | 0.7888 | 19.454 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98334 | 0.80004 | 18.329 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99265 | 0.89413 | 9.852 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98705 | 0.89248 | 9.457 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.90665 | 8.552 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99214 | 0.90719 | 8.495 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98981 | 0.79785 | 19.196 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98981 | 0.9024 | 8.74 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99049 | 0.80327 | 18.722 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9904 | 0.81005 | 18.034 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.90022 | 9.208 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99152 | 0.9083 | 8.321 | Yes
Active | 2025W1-N11-WVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99018 | 0.80876 | 18.142 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.91453 | 8.016 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.90697 | 8.612 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99095 | 0.81245 | 17.849 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99167 | 0.81084 | 18.083 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.81294 | 17.775 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.80063 | 19.298 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.8932 | 9.509 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97254 | 0.75015 | 22.24 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97254 | 0.76205 | 21.05 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97254 | 0.77082 | 20.173 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97254 | 0.78127 | 19.127 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97254 | 0.7939 | 17.864 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97254 | 0.80205 | 17.05 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97254 | 0.88238 | 9.016 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97254 | 0.88715 | 8.539 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99512 | 0.78329 | 21.183 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.80139 | 18.826 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.80196 | 18.826 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99349 | 0.9118 | 8.169 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99118 | 0.81426 | 17.692 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.8065 | 18.125 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98774 | 0.90257 | 8.517 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.90997 | 8.188 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98958 | 0.80339 | 18.619 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98793 | 0.79236 | 19.557 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98793 | 0.80553 | 18.24 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.77736 | 21.673 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9781 | 0.74962 | 22.848 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9781 | 0.76867 | 20.943 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9781 | 0.78782 | 19.028 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9781 | 0.80689 | 17.121 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98987 | 0.88261 | 10.726 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98696 | 0.75896 | 22.799 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99489 | 0.80286 | 19.203 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98963 | 0.80864 | 18.099 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98691 | 0.76984 | 21.707 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98691 | 0.77098 | 21.592 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99645 | 0.80243 | 19.402 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99645 | 0.90905 | 8.74 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98441 | 0.78946 | 19.496 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98441 | 0.80099 | 18.342 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.89402 | 9.948 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.8932 | 9.509 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.90691 | 8.617 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.90744 | 8.56 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99075 | 0.79844 | 19.231 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99075 | 0.90311 | 8.764 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.80383 | 18.763 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.81035 | 18.1 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99322 | 0.90052 | 9.27 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.90855 | 8.389 | Yes
Active | 2025W1-N11-WVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.80909 | 18.206 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99246 | 0.82576 | 16.67 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.81892 | 17.338 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99126 | 0.8231 | 16.815 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99634 | 0.80746 | 18.888 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98935 | 0.90042 | 8.893 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97678 | 0.76678 | 21 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97678 | 0.77816 | 19.862 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97678 | 0.7811 | 19.568 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97678 | 0.79582 | 18.096 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97678 | 0.79936 | 17.743 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97678 | 0.8092 | 16.759 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97678 | 0.81263 | 16.415 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97678 | 0.89327 | 8.352 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9961 | 0.79729 | 19.881 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98936 | 0.80592 | 18.344 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.80674 | 18.346 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.82645 | 16.611 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.81958 | 16.992 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9895 | 0.90946 | 8.004 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98995 | 0.81585 | 17.41 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98846 | 0.80319 | 18.528 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98846 | 0.81386 | 17.46 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.7916 | 20.331 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98091 | 0.76638 | 21.453 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98091 | 0.77688 | 20.403 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98091 | 0.80217 | 17.874 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98091 | 0.81009 | 17.082 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98998 | 0.8884 | 10.157 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98711 | 0.77475 | 21.236 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99585 | 0.81777 | 17.808 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.82247 | 16.895 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98556 | 0.77738 | 20.818 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98556 | 0.78082 | 20.474 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.8127 | 18.348 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99618 | 0.91259 | 8.359 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98298 | 0.79445 | 18.853 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98298 | 0.80371 | 17.927 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99477 | 0.90252 | 9.226 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98935 | 0.90042 | 8.893 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.91119 | 8.198 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.91172 | 8.137 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.992 | 0.80391 | 18.809 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.992 | 0.9058 | 8.621 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.992 | 0.80921 | 18.279 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.81875 | 17.324 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.90648 | 8.741 | Yes
Active | 2025W1-N11-WVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99167 | 0.81706 | 17.461 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99015 | 0.90758 | 8.257 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98567 | 0.89196 | 9.37 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98675 | 0.80325 | 18.35 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98698 | 0.79962 | 18.736 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98583 | 0.80219 | 18.365 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98929 | 0.78974 | 19.955 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98295 | 0.88384 | 9.912 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96913 | 0.74035 | 22.878 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96913 | 0.75559 | 21.353 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96913 | 0.76379 | 20.534 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96913 | 0.77253 | 19.659 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96913 | 0.78448 | 18.464 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96913 | 0.87758 | 9.154 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96913 | 0.88204 | 8.708 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99103 | 0.76804 | 22.299 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.90894 | 8.136 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98559 | 0.90456 | 8.103 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98469 | 0.79013 | 19.456 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98535 | 0.79073 | 19.462 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.90423 | 8.458 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98935 | 0.90802 | 8.133 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98942 | 0.90803 | 8.139 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98685 | 0.80419 | 18.267 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98338 | 0.79707 | 18.63 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98338 | 0.89518 | 8.819 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98701 | 0.90203 | 8.499 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.90819 | 8.17 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98458 | 0.79453 | 19.005 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.982 | 0.78338 | 19.863 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.982 | 0.79507 | 18.693 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99072 | 0.76692 | 22.38 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97455 | 0.73999 | 23.457 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97455 | 0.76091 | 21.365 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97455 | 0.77462 | 19.993 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97455 | 0.79656 | 17.799 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98371 | 0.87114 | 11.257 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98248 | 0.75085 | 23.163 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.79509 | 19.513 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98559 | 0.79981 | 18.578 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98351 | 0.76028 | 22.323 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98351 | 0.76237 | 22.114 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99378 | 0.79406 | 19.972 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99378 | 0.90312 | 9.066 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97904 | 0.77849 | 20.055 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97904 | 0.78897 | 19.006 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98949 | 0.88577 | 10.371 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98923 | 0.90683 | 8.24 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98295 | 0.88384 | 9.912 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98818 | 0.89811 | 9.006 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98812 | 0.89867 | 8.945 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.986 | 0.78739 | 19.861 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.986 | 0.89407 | 9.193 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98676 | 0.79261 | 19.415 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98665 | 0.79924 | 18.741 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98857 | 0.89226 | 9.631 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98771 | 0.90058 | 8.712 | Yes
Active | 2025W1-N11-WVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98641 | 0.79791 | 18.849 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.9151 | 8.549 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.81974 | 17.91 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99927 | 0.81663 | 18.263 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9982 | 0.8192 | 17.9 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.80595 | 19.563 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.89509 | 9.646 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98373 | 0.75708 | 22.665 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98373 | 0.76984 | 21.388 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98373 | 0.7776 | 20.613 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98373 | 0.78829 | 19.544 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98373 | 0.79922 | 18.451 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98373 | 0.80399 | 17.973 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98373 | 0.80914 | 17.459 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98373 | 0.89214 | 9.159 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98373 | 0.89682 | 8.69 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.78845 | 21.463 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99697 | 0.80634 | 19.062 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99761 | 0.80697 | 19.064 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.92096 | 8.025 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.999 | 0.82106 | 17.793 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.81343 | 18.21 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99553 | 0.91145 | 8.408 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9995 | 0.91891 | 8.059 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.80972 | 18.707 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.79782 | 19.699 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99481 | 0.8105 | 18.432 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.7839 | 21.832 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98913 | 0.75665 | 23.248 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98913 | 0.77491 | 21.422 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98913 | 0.79363 | 19.551 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98913 | 0.81187 | 17.726 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.88995 | 10.712 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99477 | 0.76629 | 22.848 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.81038 | 19.226 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.81603 | 18.156 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99613 | 0.77552 | 22.061 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.77733 | 21.88 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.80914 | 19.552 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.91799 | 8.668 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99268 | 0.79427 | 19.841 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99268 | 0.80528 | 18.741 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.90314 | 9.839 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.89509 | 9.646 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.91545 | 8.526 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.91599 | 8.467 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99835 | 0.80348 | 19.486 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99835 | 0.91077 | 8.757 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99901 | 0.80897 | 19.003 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99893 | 0.81618 | 18.275 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90901 | 9.187 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.9174 | 8.268 | Yes
Active | 2025W1-N11-WVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99869 | 0.81481 | 18.388 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.9142 | 8.087 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.82127 | 17.125 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99293 | 0.81788 | 17.505 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99198 | 0.82054 | 17.144 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.8071 | 18.83 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98884 | 0.89748 | 9.137 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97598 | 0.76045 | 21.553 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97598 | 0.77174 | 20.424 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97598 | 0.77803 | 19.795 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97598 | 0.79046 | 18.552 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97598 | 0.79973 | 17.625 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97598 | 0.80431 | 17.167 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97598 | 0.80918 | 16.68 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97598 | 0.88953 | 8.645 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97598 | 0.89342 | 8.256 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99646 | 0.79321 | 20.325 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.80728 | 18.335 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99127 | 0.80793 | 18.335 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.82238 | 17.037 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98931 | 0.81489 | 17.442 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98931 | 0.90746 | 8.185 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99078 | 0.80992 | 18.086 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98958 | 0.79858 | 19.1 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98958 | 0.81086 | 17.872 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9952 | 0.78664 | 20.856 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98089 | 0.76003 | 22.086 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98089 | 0.77488 | 20.601 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98089 | 0.79771 | 18.318 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98089 | 0.81163 | 16.925 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99134 | 0.88857 | 10.277 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98789 | 0.76872 | 21.916 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99628 | 0.81249 | 18.378 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99133 | 0.81769 | 17.364 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98744 | 0.77593 | 21.15 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98744 | 0.77823 | 20.921 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.8096 | 18.739 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.91231 | 8.469 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98526 | 0.79528 | 18.997 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98526 | 0.80568 | 17.958 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99484 | 0.90073 | 9.411 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98884 | 0.89748 | 9.137 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.91205 | 8.234 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99435 | 0.91257 | 8.179 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.80453 | 18.763 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99216 | 0.90668 | 8.548 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99266 | 0.80997 | 18.27 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.81743 | 17.516 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.9056 | 8.892 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.91367 | 8.003 | Yes
Active | 2025W1-N11-WVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.81607 | 17.629 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.91794 | 8.244 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.90786 | 9.029 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99664 | 0.8124 | 18.425 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.81059 | 18.667 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99617 | 0.81263 | 18.354 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99901 | 0.80044 | 19.857 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.89353 | 9.891 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9782 | 0.74825 | 22.995 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9782 | 0.76203 | 21.616 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9782 | 0.772 | 20.62 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9782 | 0.78047 | 19.772 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9782 | 0.79408 | 18.412 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9782 | 0.79827 | 17.992 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9782 | 0.80329 | 17.491 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9782 | 0.88483 | 9.337 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9782 | 0.89026 | 8.794 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0011 | 0.77946 | 22.162 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.91982 | 8.064 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99407 | 0.913 | 8.107 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99522 | 0.80141 | 19.381 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99579 | 0.80197 | 19.383 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99911 | 0.91491 | 8.42 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99965 | 0.91876 | 8.089 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.91874 | 8.097 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.81415 | 18.264 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.80647 | 18.693 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99339 | 0.90603 | 8.736 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99737 | 0.91287 | 8.45 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91911 | 8.099 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.8038 | 19.106 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.79242 | 20.015 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99257 | 0.80577 | 18.68 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.7762 | 22.427 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98413 | 0.74779 | 23.634 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98413 | 0.77022 | 21.391 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98413 | 0.78457 | 19.956 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98413 | 0.80762 | 17.651 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99489 | 0.88365 | 11.123 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.7586 | 23.481 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.8024 | 19.814 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.80856 | 18.676 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99437 | 0.77105 | 22.332 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.7719 | 22.247 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.80349 | 20.001 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.91402 | 8.947 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99028 | 0.78936 | 20.092 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99028 | 0.80127 | 18.901 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9995 | 0.8964 | 10.31 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99954 | 0.91757 | 8.197 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.89353 | 9.891 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.90965 | 8.906 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99867 | 0.9102 | 8.847 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99616 | 0.79835 | 19.781 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99616 | 0.9062 | 8.996 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99704 | 0.80379 | 19.324 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.8101 | 18.684 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99887 | 0.90328 | 9.558 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99809 | 0.91153 | 8.656 | Yes
Active | 2025W1-N11-WVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99672 | 0.80883 | 18.789 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99542 | 0.91179 | 8.363 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99267 | 0.90002 | 9.266 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99183 | 0.8064 | 18.543 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.80436 | 18.795 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.80632 | 18.487 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.7946 | 19.929 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98802 | 0.8879 | 10.012 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97223 | 0.74118 | 23.106 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97223 | 0.75663 | 21.561 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97223 | 0.76749 | 20.474 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97223 | 0.77411 | 19.812 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97223 | 0.78851 | 18.372 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97223 | 0.79844 | 17.379 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97223 | 0.87853 | 9.37 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97223 | 0.88442 | 8.781 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99636 | 0.77024 | 22.612 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.91337 | 8.22 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98893 | 0.9065 | 8.244 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99032 | 0.79571 | 19.461 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.79624 | 19.465 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99414 | 0.90859 | 8.556 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.9124 | 8.227 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99474 | 0.9124 | 8.234 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.80789 | 18.407 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.80047 | 18.807 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98854 | 0.90022 | 8.832 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.90637 | 8.593 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99518 | 0.91264 | 8.255 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.7982 | 19.174 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98735 | 0.78708 | 20.027 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98735 | 0.80038 | 18.697 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99609 | 0.76969 | 22.64 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97832 | 0.7408 | 23.752 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97832 | 0.76598 | 21.233 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97832 | 0.7757 | 20.262 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97832 | 0.80221 | 17.611 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98948 | 0.87632 | 11.316 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98924 | 0.75304 | 23.621 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.7961 | 19.948 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.80273 | 18.784 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99039 | 0.76664 | 22.375 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99039 | 0.7673 | 22.309 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99962 | 0.79864 | 20.098 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99962 | 0.90934 | 9.027 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98518 | 0.78374 | 20.144 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98518 | 0.7958 | 18.938 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99476 | 0.88984 | 10.492 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.90963 | 8.047 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.90963 | 8.047 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99456 | 0.91121 | 8.335 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98802 | 0.8879 | 10.012 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99376 | 0.90318 | 9.057 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.90374 | 8.998 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.79263 | 19.848 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99111 | 0.90015 | 9.097 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.79798 | 19.413 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.80388 | 18.812 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99393 | 0.89699 | 9.694 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.90518 | 8.798 | Yes
Active | 2025W1-N11-WVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99179 | 0.80265 | 18.913 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.88876 | 11.6 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.88739 | 11.775 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.88619 | 11.822 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.87857 | 12.642 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99269 | 0.84314 | 14.954 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99269 | 0.84974 | 14.295 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99269 | 0.84992 | 14.277 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99269 | 0.86409 | 12.859 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99269 | 0.86505 | 12.763 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99269 | 0.87278 | 11.991 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99269 | 0.87319 | 11.95 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0072 | 0.87316 | 13.401 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.8808 | 12.313 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.88111 | 12.309 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.88822 | 11.632 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.87865 | 12.267 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.89585 | 11.086 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.8603 | 13.529 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99559 | 0.8664 | 12.92 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.86266 | 14.183 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.84257 | 15.104 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99361 | 0.8448 | 14.881 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99361 | 0.87575 | 11.786 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99361 | 0.8793 | 11.431 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99985 | 0.84847 | 15.139 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88186 | 12.559 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.88658 | 11.75 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99832 | 0.84786 | 15.046 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99832 | 0.85183 | 14.65 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.87427 | 13.093 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99918 | 0.87028 | 12.89 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99918 | 0.87582 | 12.336 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.8775 | 12.622 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.88228 | 12.253 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.88606 | 11.859 | Yes
Active | 2025W1-N11-WVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.88561 | 11.894 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98996 | 0.90616 | 8.38 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98664 | 0.89482 | 9.182 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98602 | 0.80585 | 18.016 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98619 | 0.80386 | 18.233 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98525 | 0.80509 | 18.016 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98659 | 0.7958 | 19.079 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98549 | 0.88828 | 9.721 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96459 | 0.74138 | 22.321 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96459 | 0.75658 | 20.801 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96459 | 0.76474 | 19.985 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96459 | 0.77292 | 19.167 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96459 | 0.78858 | 17.601 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96459 | 0.87769 | 8.69 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99059 | 0.7713 | 21.929 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.90831 | 8.157 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98544 | 0.90419 | 8.126 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98499 | 0.79838 | 18.661 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98543 | 0.79876 | 18.667 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98796 | 0.90275 | 8.52 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98856 | 0.90664 | 8.192 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98863 | 0.90661 | 8.202 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.80553 | 18.081 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98204 | 0.79819 | 18.385 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98204 | 0.89364 | 8.84 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.90112 | 8.521 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98951 | 0.90761 | 8.19 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98441 | 0.79817 | 18.624 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98122 | 0.78744 | 19.378 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98122 | 0.80001 | 18.121 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.76958 | 22.052 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97034 | 0.74114 | 22.92 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97034 | 0.76331 | 20.703 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97034 | 0.77557 | 19.477 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97034 | 0.80169 | 16.865 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98282 | 0.87084 | 11.199 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9823 | 0.75377 | 22.853 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.79636 | 19.386 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98495 | 0.8026 | 18.235 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98203 | 0.76468 | 21.735 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98203 | 0.76542 | 21.661 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99272 | 0.7968 | 19.592 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99272 | 0.90317 | 8.955 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97861 | 0.78451 | 19.41 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97861 | 0.79606 | 18.255 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98902 | 0.88348 | 10.554 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98846 | 0.90545 | 8.3 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98549 | 0.88828 | 9.721 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98464 | 0.89208 | 9.256 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98449 | 0.89266 | 9.183 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98463 | 0.79448 | 19.015 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98463 | 0.89573 | 8.889 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98631 | 0.80015 | 18.616 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98583 | 0.80321 | 18.261 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98764 | 0.89172 | 9.592 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98689 | 0.89956 | 8.733 | Yes
Active | 2025W1-N11-WVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98565 | 0.8022 | 18.345 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98717 | 0.90449 | 8.268 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98283 | 0.88913 | 9.37 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98379 | 0.80099 | 18.281 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98399 | 0.79757 | 18.642 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98285 | 0.79995 | 18.29 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98606 | 0.78786 | 19.82 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98053 | 0.88169 | 9.884 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96531 | 0.7375 | 22.781 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96531 | 0.75334 | 21.197 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96531 | 0.76199 | 20.332 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96531 | 0.76991 | 19.54 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96531 | 0.78238 | 18.292 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96531 | 0.87876 | 8.655 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9881 | 0.76499 | 22.31 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98733 | 0.90581 | 8.153 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98269 | 0.90155 | 8.114 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9818 | 0.7885 | 19.33 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98243 | 0.78906 | 19.337 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98583 | 0.90114 | 8.469 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98636 | 0.9049 | 8.146 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98643 | 0.90491 | 8.152 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98389 | 0.8019 | 18.199 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98042 | 0.79485 | 18.557 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98042 | 0.89225 | 8.817 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98403 | 0.89896 | 8.508 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98692 | 0.90505 | 8.186 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98163 | 0.79244 | 18.919 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97898 | 0.78141 | 19.757 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97898 | 0.79312 | 18.585 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98793 | 0.7646 | 22.332 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97075 | 0.73714 | 23.361 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97075 | 0.75924 | 21.151 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97075 | 0.7713 | 19.945 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97075 | 0.79451 | 17.624 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98069 | 0.86819 | 11.251 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97986 | 0.7489 | 23.096 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98718 | 0.79296 | 19.422 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98264 | 0.79759 | 18.506 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98094 | 0.75895 | 22.2 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98094 | 0.76091 | 22.004 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.79239 | 19.877 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99117 | 0.9007 | 9.046 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97604 | 0.77674 | 19.93 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97604 | 0.78729 | 18.875 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98655 | 0.88277 | 10.379 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98624 | 0.90372 | 8.252 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98053 | 0.88169 | 9.884 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9852 | 0.89508 | 9.012 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98515 | 0.89564 | 8.951 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98292 | 0.78564 | 19.729 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98292 | 0.89126 | 9.166 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98378 | 0.79088 | 19.29 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98367 | 0.79717 | 18.65 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9856 | 0.88934 | 9.626 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98476 | 0.89756 | 8.72 | Yes
Active | 2025W1-N11-WVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.79589 | 18.754 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99684 | 0.91389 | 8.295 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.81957 | 17.55 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.81546 | 17.996 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99442 | 0.81848 | 17.594 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9983 | 0.80449 | 19.381 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98931 | 0.89513 | 9.418 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97941 | 0.75797 | 22.143 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97941 | 0.76972 | 20.968 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97941 | 0.77568 | 20.373 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97941 | 0.78827 | 19.114 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97941 | 0.79725 | 18.215 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97941 | 0.80291 | 17.65 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97941 | 0.8073 | 17.21 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97941 | 0.89052 | 8.888 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97941 | 0.89472 | 8.468 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99905 | 0.78997 | 20.908 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.80431 | 18.866 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99367 | 0.805 | 18.867 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.82066 | 17.461 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.81314 | 17.871 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99185 | 0.90864 | 8.321 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.80954 | 18.38 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9916 | 0.79686 | 19.474 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9916 | 0.80893 | 18.267 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99785 | 0.78411 | 21.374 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98438 | 0.75758 | 22.68 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98438 | 0.77231 | 21.208 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98438 | 0.79485 | 18.953 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98438 | 0.80914 | 17.524 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.88799 | 10.534 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.76638 | 22.373 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99879 | 0.81072 | 18.808 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.81598 | 17.791 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9902 | 0.77299 | 21.721 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.77554 | 21.465 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99972 | 0.80743 | 19.229 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99972 | 0.91341 | 8.631 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.988 | 0.79247 | 19.552 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.988 | 0.80272 | 18.528 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.90104 | 9.64 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98931 | 0.89513 | 9.418 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99672 | 0.91257 | 8.415 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99667 | 0.91311 | 8.356 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99476 | 0.80171 | 19.305 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99476 | 0.90729 | 8.747 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99517 | 0.80713 | 18.804 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.81506 | 18.003 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.90629 | 9.07 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.91464 | 8.147 | Yes
Active | 2025W1-N11-WVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99483 | 0.8136 | 18.123 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99761 | 0.9139 | 8.371 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99614 | 0.81905 | 17.709 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9965 | 0.8147 | 18.18 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.81787 | 17.761 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99954 | 0.80367 | 19.587 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98953 | 0.89429 | 9.524 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98088 | 0.75723 | 22.366 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98088 | 0.76913 | 21.176 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98088 | 0.77495 | 20.593 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98088 | 0.78761 | 19.327 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98088 | 0.79652 | 18.436 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98088 | 0.80246 | 17.843 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98088 | 0.80676 | 17.412 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98088 | 0.89104 | 8.984 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98088 | 0.89537 | 8.552 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.78885 | 21.13 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.80334 | 19.064 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.80404 | 19.066 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99634 | 0.82014 | 17.621 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99292 | 0.8126 | 18.032 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99292 | 0.90923 | 8.369 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.80945 | 18.492 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.79628 | 19.616 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99243 | 0.80825 | 18.418 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99898 | 0.78332 | 21.566 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98588 | 0.75684 | 22.903 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98588 | 0.77149 | 21.439 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98588 | 0.79389 | 19.199 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98588 | 0.80839 | 17.749 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99416 | 0.88787 | 10.629 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99105 | 0.76564 | 22.541 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99985 | 0.81016 | 18.969 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99497 | 0.81546 | 17.951 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99138 | 0.77201 | 21.937 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.77467 | 21.671 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.80677 | 19.412 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0009 | 0.914 | 8.688 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98919 | 0.7916 | 19.76 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98919 | 0.80178 | 18.742 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99855 | 0.90133 | 9.723 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98953 | 0.89429 | 9.524 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99771 | 0.9129 | 8.48 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99766 | 0.91345 | 8.421 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99588 | 0.80081 | 19.507 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99588 | 0.9077 | 8.818 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99624 | 0.80621 | 19.003 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99617 | 0.81432 | 18.185 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99804 | 0.90671 | 9.134 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99714 | 0.91516 | 8.198 | Yes
Active | 2025W1-N11-WVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99589 | 0.81283 | 18.307 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.91346 | 8.253 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.90321 | 8.958 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99201 | 0.81521 | 17.68 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99233 | 0.81338 | 17.896 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.81443 | 17.699 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.80528 | 18.751 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99168 | 0.89664 | 9.504 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97155 | 0.75064 | 22.09 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97155 | 0.7652 | 20.634 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97155 | 0.77343 | 19.812 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97155 | 0.78208 | 18.946 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97155 | 0.79826 | 17.329 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97155 | 0.80452 | 16.703 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97155 | 0.88277 | 8.878 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97155 | 0.88471 | 8.683 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99629 | 0.78221 | 21.408 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9912 | 0.80775 | 18.345 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99161 | 0.80813 | 18.348 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.91047 | 8.352 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.91442 | 8.02 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.91437 | 8.032 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.81428 | 17.832 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98765 | 0.80653 | 18.112 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98765 | 0.90075 | 8.69 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99251 | 0.90922 | 8.329 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.80747 | 18.316 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.79677 | 19.097 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98774 | 0.8097 | 17.804 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99574 | 0.77868 | 21.706 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97724 | 0.75031 | 22.693 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97724 | 0.77224 | 20.5 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97724 | 0.78644 | 19.08 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97724 | 0.81159 | 16.565 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98944 | 0.88019 | 10.924 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98843 | 0.76239 | 22.604 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.80542 | 19.061 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.991 | 0.812 | 17.9 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98807 | 0.7737 | 21.438 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98807 | 0.77408 | 21.399 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99796 | 0.80546 | 19.251 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99796 | 0.91072 | 8.724 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98528 | 0.79414 | 19.114 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98528 | 0.80603 | 17.925 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.89086 | 10.433 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99454 | 0.91324 | 8.13 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99168 | 0.89664 | 9.504 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.90113 | 9.002 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.90169 | 8.933 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.80394 | 18.7 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99094 | 0.90426 | 8.668 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.80952 | 18.292 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.992 | 0.81274 | 17.926 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.89997 | 9.374 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99299 | 0.90761 | 8.537 | Yes
Active | 2025W1-N11-WVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99184 | 0.81173 | 18.011 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.85189 | 14.876 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.84779 | 15.263 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99977 | 0.84897 | 15.08 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.83632 | 16.541 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98619 | 0.79715 | 18.904 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98619 | 0.80571 | 18.048 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98619 | 0.80612 | 18.006 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98619 | 0.81623 | 16.995 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98619 | 0.82331 | 16.288 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98619 | 0.82849 | 15.77 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98619 | 0.83482 | 15.136 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0036 | 0.82941 | 17.418 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99848 | 0.83757 | 16.091 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99899 | 0.83812 | 16.087 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.85213 | 14.845 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99804 | 0.84495 | 15.309 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.86553 | 13.638 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.81081 | 18.477 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99559 | 0.82087 | 17.472 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.82022 | 18.129 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98886 | 0.79675 | 19.211 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98886 | 0.80075 | 18.811 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98886 | 0.83301 | 15.585 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98886 | 0.83674 | 15.212 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.91158 | 8.91 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.80351 | 19.15 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.84416 | 15.949 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99982 | 0.84894 | 15.088 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99255 | 0.80283 | 18.972 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99255 | 0.80744 | 18.511 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.83602 | 16.579 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99238 | 0.82481 | 16.757 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99238 | 0.83183 | 16.055 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92147 | 8.135 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99922 | 0.83419 | 16.503 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.83994 | 16.014 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99992 | 0.84648 | 15.344 | Yes
Active | 2025W1-N11-WVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99972 | 0.84566 | 15.406 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.91306 | 8.725 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99958 | 0.81777 | 18.18 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99982 | 0.81371 | 18.611 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99869 | 0.81663 | 18.206 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.80289 | 19.962 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98996 | 0.89132 | 9.864 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98609 | 0.75532 | 23.077 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98609 | 0.76862 | 21.747 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98609 | 0.77562 | 21.047 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98609 | 0.78655 | 19.954 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98609 | 0.79653 | 18.956 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98609 | 0.80242 | 18.367 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98609 | 0.80733 | 17.876 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98609 | 0.89275 | 9.334 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98609 | 0.89744 | 8.865 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0038 | 0.78535 | 21.848 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99732 | 0.80292 | 19.439 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99802 | 0.80359 | 19.443 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.92105 | 8.079 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.81887 | 18.084 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99621 | 0.81137 | 18.484 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99621 | 0.91135 | 8.486 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.9188 | 8.122 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99746 | 0.80824 | 18.922 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.7957 | 19.938 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99509 | 0.80786 | 18.723 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.7816 | 22.144 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.75495 | 23.651 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99146 | 0.77258 | 21.889 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99146 | 0.79115 | 20.031 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99146 | 0.80883 | 18.263 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99721 | 0.88833 | 10.889 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.7645 | 23.059 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.80874 | 19.455 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99836 | 0.81416 | 18.421 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99709 | 0.7725 | 22.459 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99709 | 0.77475 | 22.234 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.80679 | 19.873 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.91781 | 8.771 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.79099 | 20.239 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99338 | 0.80154 | 19.184 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.90262 | 9.965 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98996 | 0.89132 | 9.864 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91486 | 8.632 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.91543 | 8.57 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99896 | 0.80023 | 19.873 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99896 | 0.90989 | 8.907 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99954 | 0.80567 | 19.387 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99948 | 0.81331 | 18.616 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.90854 | 9.293 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91721 | 8.34 | Yes
Active | 2025W1-N11-WVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99921 | 0.81187 | 18.734 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99775 | 0.91728 | 8.047 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99429 | 0.90413 | 9.017 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99426 | 0.81188 | 18.238 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99453 | 0.80823 | 18.631 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.81093 | 18.246 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.7978 | 19.914 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98745 | 0.88881 | 9.864 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97907 | 0.74928 | 22.979 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97907 | 0.76347 | 21.56 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97907 | 0.7715 | 20.756 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97907 | 0.78108 | 19.799 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97907 | 0.79221 | 18.686 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97907 | 0.79792 | 18.115 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97907 | 0.803 | 17.607 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97907 | 0.88638 | 9.269 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97907 | 0.89129 | 8.778 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99858 | 0.77793 | 22.065 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.79808 | 19.409 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.7987 | 19.413 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.91403 | 8.243 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.81303 | 18.136 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99092 | 0.80561 | 18.531 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99092 | 0.9048 | 8.611 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.91183 | 8.284 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.80271 | 18.939 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98958 | 0.79085 | 19.873 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98958 | 0.80304 | 18.655 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99808 | 0.77561 | 22.247 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98456 | 0.7489 | 23.566 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98456 | 0.76877 | 21.579 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98456 | 0.78431 | 20.025 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98456 | 0.80468 | 17.988 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99165 | 0.8813 | 11.035 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.75886 | 23.133 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99787 | 0.8028 | 19.507 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.80829 | 18.476 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99183 | 0.76828 | 22.355 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99183 | 0.7702 | 22.163 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.80202 | 19.889 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0009 | 0.91223 | 8.868 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98748 | 0.78627 | 20.12 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98748 | 0.79704 | 19.043 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.89564 | 10.14 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99688 | 0.91667 | 8.022 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98745 | 0.88881 | 9.864 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.90802 | 8.785 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99582 | 0.90858 | 8.724 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.79532 | 19.825 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99358 | 0.90362 | 8.996 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.80068 | 19.359 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9942 | 0.80783 | 18.638 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99616 | 0.90187 | 9.429 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99533 | 0.91035 | 8.498 | Yes
Active | 2025W1-N11-WVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99395 | 0.80644 | 18.751 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.9206 | 8.026 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99715 | 0.90722 | 8.993 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.81539 | 18.2 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99775 | 0.81146 | 18.629 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99664 | 0.81441 | 18.224 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.80093 | 19.959 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99071 | 0.89233 | 9.839 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98251 | 0.75308 | 22.944 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98251 | 0.76668 | 21.583 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98251 | 0.77403 | 20.849 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98251 | 0.78472 | 19.78 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98251 | 0.79543 | 18.709 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98251 | 0.80148 | 18.104 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98251 | 0.80597 | 17.654 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98251 | 0.8902 | 9.232 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98251 | 0.89493 | 8.758 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.78214 | 21.949 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.80087 | 19.443 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.80153 | 19.448 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99959 | 0.91736 | 8.223 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99755 | 0.81649 | 18.106 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99407 | 0.80907 | 18.499 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99407 | 0.90797 | 8.609 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99779 | 0.91513 | 8.266 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.80607 | 18.916 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.79415 | 19.876 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99291 | 0.80616 | 18.675 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.77905 | 22.191 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98788 | 0.7527 | 23.518 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98788 | 0.77097 | 21.691 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98788 | 0.78868 | 19.92 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98788 | 0.80769 | 18.019 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.88457 | 11.016 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.76187 | 23.082 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.80649 | 19.452 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9962 | 0.81182 | 18.438 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99399 | 0.77023 | 22.376 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.77249 | 22.15 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.80475 | 19.877 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.91462 | 8.89 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99056 | 0.78924 | 20.132 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99056 | 0.79979 | 19.077 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.89899 | 10.109 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.91999 | 8.002 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99071 | 0.89233 | 9.839 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99894 | 0.91116 | 8.778 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99889 | 0.91172 | 8.716 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.79828 | 19.869 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99698 | 0.90671 | 9.026 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.80358 | 19.393 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.81109 | 18.633 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99931 | 0.90511 | 9.419 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99842 | 0.91361 | 8.481 | Yes
Active | 2025W1-N11-WVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99716 | 0.80965 | 18.751 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.91413 | 8.174 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99247 | 0.90098 | 9.149 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99234 | 0.80844 | 18.39 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.80524 | 18.75 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.80778 | 18.385 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.79511 | 19.991 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98642 | 0.88693 | 9.949 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9758 | 0.74511 | 23.069 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9758 | 0.75947 | 21.632 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9758 | 0.76829 | 20.751 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9758 | 0.77725 | 19.855 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9758 | 0.78948 | 18.632 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9758 | 0.79976 | 17.604 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9758 | 0.88266 | 9.314 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9758 | 0.88779 | 8.801 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99671 | 0.77392 | 22.279 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.91569 | 8.034 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99058 | 0.91029 | 8.03 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.79555 | 19.493 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.79615 | 19.498 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.91087 | 8.371 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.9147 | 8.041 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99518 | 0.9147 | 8.048 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99251 | 0.80968 | 18.283 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.80227 | 18.674 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98901 | 0.90182 | 8.719 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.90865 | 8.411 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.91496 | 8.068 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.79962 | 19.068 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98781 | 0.78809 | 19.972 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98781 | 0.80044 | 18.737 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99626 | 0.77201 | 22.425 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98145 | 0.74473 | 23.672 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98145 | 0.76577 | 21.568 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98145 | 0.78011 | 20.135 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98145 | 0.80214 | 17.931 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.87803 | 11.167 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.75509 | 23.325 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.79926 | 19.669 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.80485 | 18.628 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98987 | 0.76551 | 22.436 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98987 | 0.76721 | 22.265 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99925 | 0.79903 | 20.022 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99925 | 0.9096 | 8.965 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.78381 | 20.186 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98566 | 0.79479 | 19.087 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99514 | 0.89227 | 10.287 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.9135 | 8.149 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98642 | 0.88693 | 9.949 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.90493 | 8.908 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99396 | 0.90549 | 8.847 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99178 | 0.79276 | 19.902 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99178 | 0.90102 | 9.075 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.79805 | 19.447 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.80483 | 18.759 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.89884 | 9.549 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.90724 | 8.624 | Yes
Active | 2025W1-N11-WVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99218 | 0.80348 | 18.869 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98742 | 0.83386 | 15.355 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98821 | 0.8322 | 15.601 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9875 | 0.83275 | 15.475 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98877 | 0.82369 | 16.508 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98777 | 0.90702 | 8.075 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97309 | 0.77151 | 20.158 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97309 | 0.78311 | 18.998 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97309 | 0.79097 | 18.212 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97309 | 0.80135 | 17.174 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97309 | 0.81814 | 15.495 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97309 | 0.82019 | 15.29 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97309 | 0.82164 | 15.146 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97309 | 0.88764 | 8.545 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99026 | 0.80697 | 18.329 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98724 | 0.82559 | 16.165 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98753 | 0.82599 | 16.154 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.82701 | 16.103 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98021 | 0.81765 | 16.255 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98679 | 0.82528 | 16.151 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98525 | 0.81471 | 17.054 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98525 | 0.82816 | 15.709 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98964 | 0.79747 | 19.217 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97773 | 0.77072 | 20.701 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97773 | 0.78988 | 18.785 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97773 | 0.81119 | 16.654 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97773 | 0.83121 | 14.652 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9872 | 0.89516 | 9.204 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98485 | 0.78015 | 20.47 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99033 | 0.823 | 16.732 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98666 | 0.831 | 15.567 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9844 | 0.79141 | 19.299 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9844 | 0.79172 | 19.269 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.82187 | 16.935 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98367 | 0.81363 | 17.004 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98367 | 0.82602 | 15.766 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99016 | 0.89491 | 9.525 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98777 | 0.90702 | 8.075 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9874 | 0.82228 | 16.512 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98814 | 0.8274 | 16.074 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98802 | 0.83164 | 15.638 | Yes
Active | 2025W1-N11-WVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98792 | 0.83069 | 15.722 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.90938 | 8.47 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.89795 | 9.36 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99051 | 0.80504 | 18.547 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99267 | 0.91209 | 8.058 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99107 | 0.8037 | 18.737 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98995 | 0.80532 | 18.463 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.79433 | 19.796 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98855 | 0.8885 | 10.006 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96886 | 0.73873 | 23.013 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96886 | 0.75481 | 21.405 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96886 | 0.76696 | 20.19 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96886 | 0.77224 | 19.662 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96886 | 0.78817 | 18.07 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96886 | 0.87548 | 9.338 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96886 | 0.88183 | 8.703 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99509 | 0.76768 | 22.741 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.91091 | 8.334 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98687 | 0.90319 | 8.368 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98926 | 0.79578 | 19.348 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98978 | 0.79626 | 19.352 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99282 | 0.9062 | 8.662 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.90997 | 8.337 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.90997 | 8.344 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.80662 | 18.401 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98725 | 0.79931 | 18.795 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98725 | 0.89839 | 8.887 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99099 | 0.90401 | 8.697 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99386 | 0.91018 | 8.368 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.79736 | 19.137 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98873 | 0.90868 | 8.005 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.78664 | 19.946 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98611 | 0.80049 | 18.561 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.76812 | 22.682 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97519 | 0.73836 | 23.683 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97519 | 0.76605 | 20.914 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97519 | 0.77291 | 20.228 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97519 | 0.80251 | 17.269 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9882 | 0.87431 | 11.389 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.75153 | 23.696 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.91145 | 8.076 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99434 | 0.79403 | 20.031 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98924 | 0.8014 | 18.784 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98935 | 0.76706 | 22.229 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98935 | 0.76711 | 22.224 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99877 | 0.79831 | 20.046 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99877 | 0.90823 | 9.054 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9838 | 0.78377 | 20.003 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9838 | 0.79651 | 18.728 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.88744 | 10.606 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98819 | 0.90652 | 8.167 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98819 | 0.90652 | 8.167 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99323 | 0.90879 | 8.444 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98855 | 0.8885 | 10.006 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99253 | 0.90109 | 9.144 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.90164 | 9.085 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98978 | 0.79257 | 19.721 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98978 | 0.8988 | 9.098 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.79788 | 19.301 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99076 | 0.80319 | 18.757 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99267 | 0.89497 | 9.77 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99192 | 0.90295 | 8.897 | Yes
Active | 2025W1-N11-WVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.80205 | 18.852 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.90868 | 9.427 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.9078 | 9.538 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.90523 | 9.711 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.89981 | 10.276 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99282 | 0.87154 | 12.127 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99282 | 0.87235 | 12.047 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99282 | 0.87648 | 11.633 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99282 | 0.88627 | 10.654 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99282 | 0.88947 | 10.334 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99282 | 0.89192 | 10.089 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99282 | 0.89567 | 9.714 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0045 | 0.89654 | 10.794 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.90208 | 9.999 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.9023 | 9.998 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.90822 | 9.435 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90002 | 10.025 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.92198 | 8.436 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.88323 | 10.982 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99304 | 0.88746 | 10.559 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.88749 | 11.465 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99281 | 0.86831 | 12.45 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99281 | 0.87099 | 12.182 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99281 | 0.89868 | 9.413 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99281 | 0.90017 | 9.264 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.87545 | 12.262 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.90261 | 10.206 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.90704 | 9.539 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99585 | 0.87182 | 12.403 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99585 | 0.87501 | 12.084 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.89381 | 10.829 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99772 | 0.89334 | 10.437 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99772 | 0.89746 | 10.026 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.89902 | 10.259 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.9032 | 9.953 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.90613 | 9.643 | Yes
Active | 2025W1-N11-WVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.90598 | 9.65 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98618 | 0.90236 | 8.382 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98283 | 0.89058 | 9.225 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98228 | 0.80186 | 18.043 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98237 | 0.79979 | 18.259 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98144 | 0.80109 | 18.034 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98274 | 0.79177 | 19.097 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98165 | 0.88409 | 9.756 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96055 | 0.73753 | 22.302 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96055 | 0.75306 | 20.749 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96055 | 0.76118 | 19.938 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96055 | 0.7691 | 19.145 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96055 | 0.78447 | 17.609 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98698 | 0.76655 | 22.043 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98622 | 0.90426 | 8.196 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.90015 | 8.152 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98115 | 0.79441 | 18.674 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9816 | 0.79479 | 18.681 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98418 | 0.89876 | 8.542 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98476 | 0.90259 | 8.218 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98484 | 0.90257 | 8.226 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98246 | 0.80178 | 18.068 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97851 | 0.7947 | 18.381 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97851 | 0.88999 | 8.852 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9825 | 0.89696 | 8.553 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98583 | 0.90355 | 8.228 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98057 | 0.79423 | 18.634 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97726 | 0.78349 | 19.376 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97726 | 0.79585 | 18.14 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98653 | 0.76579 | 22.074 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96627 | 0.73734 | 22.894 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96627 | 0.7596 | 20.668 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96627 | 0.77086 | 19.542 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96627 | 0.79742 | 16.885 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97879 | 0.86627 | 11.252 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97854 | 0.75025 | 22.829 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98654 | 0.79256 | 19.398 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9812 | 0.79861 | 18.259 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97832 | 0.76092 | 21.74 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97832 | 0.76186 | 21.646 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98933 | 0.79322 | 19.611 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98933 | 0.89928 | 9.005 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97458 | 0.78042 | 19.416 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97458 | 0.79177 | 18.281 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98517 | 0.87979 | 10.538 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98141 | 0.90129 | 8.012 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98141 | 0.90129 | 8.012 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98466 | 0.90141 | 8.325 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98165 | 0.88409 | 9.756 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98066 | 0.88753 | 9.313 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9805 | 0.88811 | 9.239 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98074 | 0.79046 | 19.029 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98074 | 0.89139 | 8.936 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98249 | 0.79617 | 18.632 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.982 | 0.79914 | 18.286 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98386 | 0.88756 | 9.63 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9831 | 0.89545 | 8.765 | Yes
Active | 2025W1-N11-WVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98182 | 0.79813 | 18.369 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.90624 | 8.791 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.81032 | 18.309 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99366 | 0.80629 | 18.736 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99253 | 0.80919 | 18.334 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.79558 | 20.08 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98373 | 0.8843 | 9.943 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97966 | 0.74829 | 23.137 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97966 | 0.76147 | 21.819 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97966 | 0.7684 | 21.126 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97966 | 0.77923 | 20.043 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97966 | 0.78912 | 19.054 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97966 | 0.79495 | 18.471 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97966 | 0.79982 | 17.984 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97966 | 0.8856 | 9.406 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97966 | 0.89032 | 8.934 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99769 | 0.77819 | 21.95 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.79561 | 19.553 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.79627 | 19.558 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99569 | 0.9143 | 8.139 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.8114 | 18.214 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.80397 | 18.605 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99003 | 0.90452 | 8.551 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99387 | 0.91203 | 8.183 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.80088 | 19.041 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.78839 | 20.042 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98881 | 0.80043 | 18.838 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9969 | 0.77448 | 22.242 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98515 | 0.74799 | 23.716 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98515 | 0.76545 | 21.97 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98515 | 0.78386 | 20.13 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98515 | 0.80137 | 18.378 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.88128 | 10.975 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.75747 | 23.134 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99716 | 0.80137 | 19.579 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99219 | 0.80674 | 18.546 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99074 | 0.76533 | 22.541 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99074 | 0.76756 | 22.318 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9994 | 0.79944 | 19.996 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9994 | 0.91103 | 8.837 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98708 | 0.78369 | 20.338 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98708 | 0.79415 | 19.293 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.89571 | 10.041 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98373 | 0.8843 | 9.943 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99503 | 0.90806 | 8.697 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99498 | 0.90863 | 8.635 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.79294 | 19.985 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99279 | 0.90304 | 8.976 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.79833 | 19.505 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.8059 | 18.741 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.90168 | 9.364 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99446 | 0.91043 | 8.403 | Yes
Active | 2025W1-N11-WVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99305 | 0.80447 | 18.858 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9854 | 0.90301 | 8.239 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98065 | 0.88679 | 9.385 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98202 | 0.79872 | 18.33 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98221 | 0.79493 | 18.727 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98106 | 0.79756 | 18.35 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98459 | 0.78504 | 19.955 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97834 | 0.87945 | 9.889 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96454 | 0.7365 | 22.803 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96454 | 0.75157 | 21.296 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96454 | 0.7594 | 20.514 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96454 | 0.76835 | 19.618 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96454 | 0.77982 | 18.471 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96454 | 0.87757 | 8.697 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98627 | 0.76398 | 22.23 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98556 | 0.90436 | 8.119 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98091 | 0.90006 | 8.085 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97988 | 0.78535 | 19.452 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98054 | 0.78595 | 19.459 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98407 | 0.89966 | 8.441 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.90345 | 8.116 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98468 | 0.90345 | 8.122 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98212 | 0.79962 | 18.25 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97865 | 0.79257 | 18.608 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97865 | 0.89055 | 8.81 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98229 | 0.89747 | 8.482 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98515 | 0.90362 | 8.153 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97982 | 0.78999 | 18.983 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97724 | 0.77888 | 19.836 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97724 | 0.7904 | 18.685 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98596 | 0.76272 | 22.324 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96991 | 0.73614 | 23.377 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96991 | 0.75644 | 21.347 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96991 | 0.77056 | 19.935 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96991 | 0.79172 | 17.819 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97896 | 0.86653 | 11.243 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97762 | 0.74681 | 23.081 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98549 | 0.79062 | 19.486 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98087 | 0.79531 | 18.555 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9786 | 0.75575 | 22.285 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9786 | 0.75792 | 22.067 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98895 | 0.78943 | 19.952 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98895 | 0.89835 | 9.06 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97412 | 0.7738 | 20.032 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97412 | 0.78412 | 19 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98476 | 0.88124 | 10.352 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98449 | 0.90226 | 8.223 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97834 | 0.87945 | 9.889 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.89352 | 8.991 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98338 | 0.89408 | 8.93 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98124 | 0.78265 | 19.859 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98124 | 0.88929 | 9.196 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98197 | 0.78784 | 19.413 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98188 | 0.79457 | 18.732 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98381 | 0.88764 | 9.617 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98295 | 0.89599 | 8.697 | Yes
Active | 2025W1-N11-WVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98163 | 0.79323 | 18.84 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99825 | 0.8714 | 12.685 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99787 | 0.86894 | 12.894 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.86808 | 12.918 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99793 | 0.8582 | 13.973 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98479 | 0.82348 | 16.132 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98479 | 0.82447 | 16.032 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98479 | 0.82778 | 15.702 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98479 | 0.83019 | 15.46 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98479 | 0.84641 | 13.838 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98479 | 0.85152 | 13.328 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98479 | 0.85327 | 13.153 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.85384 | 14.694 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99624 | 0.86039 | 13.585 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99663 | 0.86079 | 13.584 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99803 | 0.87127 | 12.676 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.86432 | 13.143 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90018 | 10.373 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.81981 | 16.901 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98882 | 0.82804 | 16.079 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9982 | 0.8439 | 15.431 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98631 | 0.82242 | 16.388 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98631 | 0.82303 | 16.327 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98631 | 0.85671 | 12.96 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98631 | 0.8579 | 12.84 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.8286 | 16.37 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.86452 | 13.649 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99753 | 0.86896 | 12.857 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98892 | 0.82533 | 16.359 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.82992 | 15.9 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99779 | 0.855 | 14.279 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98985 | 0.84853 | 14.132 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98985 | 0.85403 | 13.582 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99614 | 0.85673 | 13.94 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99742 | 0.8622 | 13.523 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.86699 | 13.021 | Yes
Active | 2025W1-N11-WVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99704 | 0.86669 | 13.035 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98405 | 0.90033 | 8.372 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98069 | 0.88828 | 9.241 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98019 | 0.79985 | 18.034 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98023 | 0.79774 | 18.249 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97929 | 0.7991 | 18.019 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98057 | 0.78977 | 19.08 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9795 | 0.88183 | 9.767 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95828 | 0.73564 | 22.264 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95828 | 0.75139 | 20.689 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95828 | 0.75948 | 19.879 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95828 | 0.76726 | 19.102 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95828 | 0.78241 | 17.587 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98496 | 0.76408 | 22.088 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98416 | 0.90206 | 8.211 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97955 | 0.89796 | 8.159 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.79245 | 18.655 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97945 | 0.79282 | 18.663 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98206 | 0.89661 | 8.545 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98263 | 0.90039 | 8.224 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9827 | 0.90038 | 8.232 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98027 | 0.79995 | 18.032 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97657 | 0.79305 | 18.352 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97657 | 0.88809 | 8.848 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98034 | 0.8947 | 8.564 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98377 | 0.90134 | 8.243 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97841 | 0.79228 | 18.613 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97501 | 0.78155 | 19.347 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97501 | 0.79376 | 18.125 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98453 | 0.76396 | 22.058 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96398 | 0.73548 | 22.85 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96398 | 0.75781 | 20.617 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96398 | 0.76841 | 19.557 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96398 | 0.79525 | 16.873 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97651 | 0.86378 | 11.273 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97643 | 0.74858 | 22.785 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98449 | 0.79071 | 19.378 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97909 | 0.79662 | 18.248 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97624 | 0.75911 | 21.713 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97624 | 0.76018 | 21.606 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98745 | 0.79152 | 19.593 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98745 | 0.89719 | 9.026 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97231 | 0.77838 | 19.392 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97231 | 0.7896 | 18.271 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.983 | 0.87787 | 10.513 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97925 | 0.89903 | 8.022 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97925 | 0.89903 | 8.022 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98252 | 0.89921 | 8.33 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9795 | 0.88183 | 9.767 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9784 | 0.88501 | 9.339 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97823 | 0.88559 | 9.264 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97855 | 0.78846 | 19.009 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97855 | 0.88901 | 8.955 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98035 | 0.7942 | 18.616 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97985 | 0.79709 | 18.275 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98173 | 0.88531 | 9.642 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98097 | 0.89322 | 8.775 | Yes
Active | 2025W1-N11-WVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97966 | 0.79609 | 18.357 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98223 | 0.89971 | 8.252 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97744 | 0.8833 | 9.415 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97887 | 0.79604 | 18.283 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97902 | 0.79236 | 18.666 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97787 | 0.79487 | 18.299 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98125 | 0.78259 | 19.866 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97568 | 0.87699 | 9.87 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96059 | 0.7335 | 22.708 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96059 | 0.74889 | 21.17 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96059 | 0.75696 | 20.363 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96059 | 0.76542 | 19.517 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96059 | 0.7771 | 18.349 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98314 | 0.76091 | 22.223 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9824 | 0.90104 | 8.137 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97781 | 0.89684 | 8.097 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97674 | 0.78304 | 19.369 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97739 | 0.78362 | 19.377 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98089 | 0.89635 | 8.454 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98143 | 0.90012 | 8.13 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9815 | 0.90013 | 8.137 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97897 | 0.79692 | 18.205 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97549 | 0.78994 | 18.555 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97549 | 0.88735 | 8.815 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97913 | 0.8942 | 8.493 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98199 | 0.90029 | 8.17 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97665 | 0.78743 | 18.922 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.974 | 0.77643 | 19.757 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.974 | 0.78791 | 18.61 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98293 | 0.76012 | 22.281 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96597 | 0.73314 | 23.282 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96597 | 0.75408 | 21.189 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96597 | 0.76718 | 19.879 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96597 | 0.78897 | 17.699 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97574 | 0.86327 | 11.247 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97457 | 0.74446 | 23.011 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98228 | 0.78805 | 19.424 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97772 | 0.79268 | 18.504 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97565 | 0.75374 | 22.191 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97565 | 0.75583 | 21.982 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98603 | 0.78717 | 19.886 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98603 | 0.8955 | 9.053 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97085 | 0.77145 | 19.94 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97085 | 0.78177 | 18.908 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98164 | 0.87801 | 10.363 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98131 | 0.89894 | 8.237 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97568 | 0.87699 | 9.87 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98027 | 0.89028 | 8.999 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98022 | 0.89084 | 8.939 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97799 | 0.78028 | 19.771 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97799 | 0.88612 | 9.188 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97879 | 0.78547 | 19.332 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9787 | 0.79199 | 18.671 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98064 | 0.88443 | 9.62 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9798 | 0.89273 | 8.707 | Yes
Active | 2025W1-N11-WVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97845 | 0.79068 | 18.777 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0057 | 0.90999 | 9.57 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.91523 | 9.047 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0057 | 0.91828 | 8.741 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0057 | 0.92569 | 8.001 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.014 | 0.93369 | 8.034 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0123 | 0.92686 | 8.548 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0055 | 0.90801 | 9.754 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.9147 | 9.085 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0089 | 0.91747 | 9.147 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0056 | 0.91172 | 9.391 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.91301 | 9.261 | Yes
Active | 2025W1-N11-WVD243501 | 243501 | 05E.BEAV | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.011 | 0.92786 | 8.315 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.92151 | 8.2 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.91186 | 8.956 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99977 | 0.816 | 18.378 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.81407 | 18.63 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99929 | 0.81618 | 18.311 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.80381 | 19.84 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.89667 | 9.859 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98177 | 0.75205 | 22.972 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98177 | 0.76552 | 21.625 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98177 | 0.77512 | 20.665 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98177 | 0.78412 | 19.764 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98177 | 0.79735 | 18.442 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98177 | 0.80157 | 18.02 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98177 | 0.80654 | 17.522 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98177 | 0.88853 | 9.324 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98177 | 0.89379 | 8.798 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0042 | 0.78366 | 22.051 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.92346 | 8.012 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.91667 | 8.059 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99829 | 0.8047 | 19.359 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99888 | 0.80527 | 19.361 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.91852 | 8.373 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92237 | 8.042 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92235 | 8.049 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99992 | 0.81771 | 18.221 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.80999 | 18.651 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99649 | 0.90947 | 8.703 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.9165 | 8.402 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.92276 | 8.047 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99796 | 0.80715 | 19.082 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.79567 | 20.009 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99575 | 0.80899 | 18.676 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.77986 | 22.363 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98762 | 0.75158 | 23.604 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98762 | 0.7732 | 21.442 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98762 | 0.78872 | 19.89 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98762 | 0.81078 | 17.684 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9981 | 0.88741 | 11.069 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99636 | 0.76209 | 23.427 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.80608 | 19.76 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.81216 | 18.629 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9973 | 0.77406 | 22.324 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9973 | 0.77502 | 22.228 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.80673 | 19.965 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0064 | 0.91718 | 8.919 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.7926 | 20.082 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99342 | 0.80443 | 18.899 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.90008 | 10.252 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.92118 | 8.15 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.89667 | 9.859 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.91326 | 8.857 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.91381 | 8.798 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99931 | 0.80166 | 19.765 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99931 | 0.90961 | 8.97 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.80713 | 19.302 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.81358 | 18.647 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.90684 | 9.514 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91513 | 8.609 | Yes
Active | 2025W1-N11-WVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.8123 | 18.753 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.8827 | 11.423 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.88096 | 11.647 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99673 | 0.88008 | 11.665 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99738 | 0.8726 | 12.478 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98495 | 0.83678 | 14.816 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98495 | 0.84384 | 14.111 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98495 | 0.8451 | 13.985 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98495 | 0.85875 | 12.62 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98495 | 0.85923 | 12.572 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98495 | 0.86731 | 11.764 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98495 | 0.86743 | 11.752 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99942 | 0.86714 | 13.228 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.87475 | 12.158 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.87506 | 12.154 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99661 | 0.88204 | 11.456 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.87189 | 12.15 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99827 | 0.88615 | 11.212 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.8555 | 13.284 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98834 | 0.86129 | 12.705 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99643 | 0.85643 | 14 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98554 | 0.83619 | 14.935 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98554 | 0.83992 | 14.562 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98554 | 0.86965 | 11.589 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98554 | 0.87322 | 11.232 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99222 | 0.84246 | 14.975 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99984 | 0.87561 | 12.423 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99626 | 0.88061 | 11.566 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9917 | 0.8429 | 14.88 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.84705 | 14.465 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.86878 | 12.912 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.86446 | 12.759 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99205 | 0.86983 | 12.222 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.87158 | 12.462 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99718 | 0.8762 | 12.097 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.87989 | 11.716 | Yes
Active | 2025W1-N11-WVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99696 | 0.87936 | 11.76 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.90799 | 8.92 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99723 | 0.81601 | 18.122 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.81174 | 18.571 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.81478 | 18.155 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.80104 | 19.922 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99061 | 0.89276 | 9.785 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98264 | 0.75414 | 22.85 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98264 | 0.76776 | 21.487 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98264 | 0.77466 | 20.797 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98264 | 0.78552 | 19.712 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98264 | 0.79542 | 18.722 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98264 | 0.80176 | 18.087 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98264 | 0.80647 | 17.617 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98264 | 0.89073 | 9.191 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98264 | 0.89533 | 8.731 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.783 | 21.844 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.80092 | 19.402 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99565 | 0.80159 | 19.406 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9994 | 0.91766 | 8.175 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99736 | 0.81704 | 18.032 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9939 | 0.80965 | 18.425 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9939 | 0.90819 | 8.571 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99761 | 0.91543 | 8.218 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.80653 | 18.846 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99261 | 0.79441 | 19.82 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99261 | 0.8063 | 18.631 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.77985 | 22.093 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9879 | 0.75377 | 23.413 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9879 | 0.77151 | 21.639 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9879 | 0.78954 | 19.836 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9879 | 0.80755 | 18.035 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.88493 | 10.964 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.76296 | 22.967 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.8072 | 19.364 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99605 | 0.81245 | 18.36 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99382 | 0.77076 | 22.306 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.77312 | 22.07 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.80523 | 19.806 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.91474 | 8.855 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.78922 | 20.082 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99004 | 0.79962 | 19.042 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99993 | 0.89944 | 10.049 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99061 | 0.89276 | 9.785 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.91136 | 8.735 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99865 | 0.91192 | 8.673 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.79833 | 19.832 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99665 | 0.90661 | 9.004 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.80368 | 19.35 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99713 | 0.81139 | 18.574 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99906 | 0.90532 | 9.374 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9982 | 0.91386 | 8.434 | Yes
Active | 2025W1-N11-WVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99686 | 0.80992 | 18.694 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.91578 | 8.668 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.82064 | 18.104 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.81663 | 18.531 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.81953 | 18.128 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.80579 | 19.88 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.89329 | 9.83 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98852 | 0.75791 | 23.061 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98852 | 0.77128 | 21.724 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98852 | 0.7784 | 21.012 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98852 | 0.78929 | 19.923 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98852 | 0.79942 | 18.91 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98852 | 0.80525 | 18.327 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98852 | 0.81022 | 17.83 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98852 | 0.8954 | 9.312 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98852 | 0.90009 | 8.843 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0059 | 0.78806 | 21.788 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99945 | 0.80585 | 19.36 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.80652 | 19.364 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.92368 | 8.027 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.82175 | 18.006 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99833 | 0.81422 | 18.411 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99833 | 0.91403 | 8.43 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.92145 | 8.07 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99958 | 0.81109 | 18.85 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99722 | 0.79852 | 19.87 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99722 | 0.81076 | 18.645 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.78433 | 22.083 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.75753 | 23.636 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99389 | 0.77538 | 21.851 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99389 | 0.79387 | 20.002 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99389 | 0.81179 | 18.21 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99935 | 0.8911 | 10.825 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.76716 | 23.011 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.81154 | 19.386 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.817 | 18.347 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99946 | 0.77534 | 22.412 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99946 | 0.77755 | 22.191 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.80969 | 19.797 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0076 | 0.92053 | 8.712 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99572 | 0.79388 | 20.183 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99572 | 0.80451 | 19.121 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.90531 | 9.907 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.89329 | 9.83 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.91754 | 8.576 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.91811 | 8.514 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.80314 | 19.793 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0011 | 0.91262 | 8.845 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.8086 | 19.306 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.81623 | 18.537 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.91123 | 9.235 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.91987 | 8.286 | Yes
Active | 2025W1-N11-WVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.81478 | 18.655 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9876 | 0.90112 | 8.648 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98735 | 0.8111 | 17.625 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98743 | 0.80582 | 18.161 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.80934 | 17.7 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99079 | 0.79506 | 19.573 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9834 | 0.88868 | 9.472 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97167 | 0.75079 | 22.088 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97167 | 0.76368 | 20.799 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97167 | 0.76887 | 20.28 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97167 | 0.78122 | 19.045 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97167 | 0.78895 | 18.272 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97167 | 0.80051 | 17.116 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97167 | 0.88323 | 8.844 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97167 | 0.88744 | 8.423 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99131 | 0.77975 | 21.155 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98474 | 0.7943 | 19.044 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98552 | 0.79502 | 19.049 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98941 | 0.90905 | 8.035 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98746 | 0.81195 | 17.551 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.80486 | 17.931 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98417 | 0.89964 | 8.452 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98761 | 0.90678 | 8.084 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98499 | 0.8016 | 18.338 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98302 | 0.78978 | 19.324 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98302 | 0.80092 | 18.21 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99045 | 0.7758 | 21.465 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97646 | 0.75041 | 22.605 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97646 | 0.76519 | 21.127 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97646 | 0.78596 | 19.05 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97646 | 0.80029 | 17.617 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.87696 | 10.764 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98227 | 0.75911 | 22.316 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99085 | 0.80286 | 18.799 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98623 | 0.80769 | 17.854 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98195 | 0.76457 | 21.737 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98195 | 0.76748 | 21.447 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.79943 | 19.306 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99249 | 0.90478 | 8.77 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97883 | 0.78295 | 19.588 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97883 | 0.79273 | 18.61 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.89143 | 9.843 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9834 | 0.88868 | 9.472 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.90217 | 8.631 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98842 | 0.90271 | 8.57 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98687 | 0.79204 | 19.483 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98687 | 0.89726 | 8.961 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98716 | 0.79722 | 18.994 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.80556 | 18.155 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.89672 | 9.229 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98809 | 0.90512 | 8.297 | Yes
Active | 2025W1-N11-WVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98682 | 0.80401 | 18.281 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99801 | 0.91506 | 8.295 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99556 | 0.90429 | 9.127 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99429 | 0.80991 | 18.438 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.80832 | 18.662 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99385 | 0.81024 | 18.36 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99656 | 0.79843 | 19.813 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99065 | 0.89149 | 9.916 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97513 | 0.74521 | 22.991 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97513 | 0.75962 | 21.551 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97513 | 0.77025 | 20.488 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97513 | 0.77786 | 19.726 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97513 | 0.79221 | 18.291 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97513 | 0.80143 | 17.37 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97513 | 0.88186 | 9.327 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97513 | 0.88756 | 8.756 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99878 | 0.77591 | 22.287 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.91682 | 8.129 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.90998 | 8.165 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.79952 | 19.345 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99353 | 0.80005 | 19.348 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99675 | 0.912 | 8.475 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99728 | 0.91581 | 8.147 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99734 | 0.9158 | 8.154 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99446 | 0.81174 | 18.272 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9911 | 0.80415 | 18.695 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9911 | 0.90344 | 8.767 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99498 | 0.9099 | 8.508 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99774 | 0.9161 | 8.163 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99259 | 0.80182 | 19.077 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99017 | 0.79059 | 19.958 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99017 | 0.80402 | 18.615 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9983 | 0.77356 | 22.474 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98118 | 0.74478 | 23.64 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98118 | 0.76869 | 21.249 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98118 | 0.78112 | 20.006 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98118 | 0.80592 | 17.526 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.88059 | 11.182 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99136 | 0.75616 | 23.52 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.79982 | 19.834 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.80611 | 18.687 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99234 | 0.76951 | 22.284 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99234 | 0.77015 | 22.22 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.80166 | 19.989 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.91187 | 8.967 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98794 | 0.78751 | 20.043 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98794 | 0.79961 | 18.833 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.89342 | 10.377 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99717 | 0.91463 | 8.254 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99065 | 0.89149 | 9.916 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99636 | 0.90675 | 8.961 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.9073 | 8.902 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9938 | 0.79644 | 19.737 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9938 | 0.90367 | 9.013 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.80182 | 19.292 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.80783 | 18.68 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99653 | 0.90049 | 9.604 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99576 | 0.90864 | 8.712 | Yes
Active | 2025W1-N11-WVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.8066 | 18.782 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.91421 | 8.397 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.8193 | 17.749 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99716 | 0.81493 | 18.222 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.81812 | 17.801 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.8039 | 19.633 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.89458 | 9.549 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9816 | 0.75743 | 22.417 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9816 | 0.76938 | 21.222 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9816 | 0.77521 | 20.639 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9816 | 0.78786 | 19.374 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9816 | 0.7968 | 18.48 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9816 | 0.80279 | 17.881 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9816 | 0.80708 | 17.452 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9816 | 0.89152 | 9.008 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9816 | 0.89588 | 8.572 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.78894 | 21.187 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.80354 | 19.108 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.80424 | 19.11 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.82038 | 17.66 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99356 | 0.81285 | 18.071 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99356 | 0.90972 | 8.384 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.91725 | 8.001 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99495 | 0.80966 | 18.529 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99301 | 0.79656 | 19.644 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99301 | 0.80853 | 18.448 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99966 | 0.78352 | 21.615 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98661 | 0.75705 | 22.956 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98661 | 0.77175 | 21.485 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98661 | 0.79404 | 19.256 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98661 | 0.80869 | 17.792 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.88818 | 10.657 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99169 | 0.76585 | 22.585 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.8104 | 19.01 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99561 | 0.8157 | 17.991 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99207 | 0.77222 | 21.984 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.77489 | 21.718 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.80704 | 19.454 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.91455 | 8.703 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98987 | 0.79182 | 19.805 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98987 | 0.80201 | 18.786 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99922 | 0.90176 | 9.746 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.89458 | 9.549 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99834 | 0.91333 | 8.501 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99829 | 0.91388 | 8.441 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99655 | 0.80103 | 19.552 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99655 | 0.90819 | 8.836 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9969 | 0.80642 | 19.048 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99682 | 0.81455 | 18.227 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99869 | 0.90717 | 9.152 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99779 | 0.91564 | 8.214 | Yes
Active | 2025W1-N11-WVD243511 | 243511 | 05GAY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99655 | 0.81305 | 18.349 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.90986 | 8.267 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.89594 | 9.288 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98902 | 0.80428 | 18.475 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98935 | 0.80104 | 18.83 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98821 | 0.80349 | 18.472 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99149 | 0.79109 | 20.039 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98413 | 0.88423 | 9.99 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97149 | 0.74082 | 23.067 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97149 | 0.75583 | 21.566 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97149 | 0.76473 | 20.676 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97149 | 0.77307 | 19.842 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97149 | 0.78548 | 18.601 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97149 | 0.87852 | 9.297 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97149 | 0.88348 | 8.801 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99342 | 0.76906 | 22.436 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.91133 | 8.136 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98747 | 0.90628 | 8.119 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.79167 | 19.544 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98775 | 0.79225 | 19.55 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9912 | 0.90653 | 8.467 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99173 | 0.91036 | 8.137 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99181 | 0.91037 | 8.144 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98917 | 0.80542 | 18.375 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.79811 | 18.755 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98566 | 0.89753 | 8.813 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98939 | 0.90432 | 8.507 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.91059 | 8.17 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98692 | 0.79557 | 19.135 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98433 | 0.78425 | 20.008 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98433 | 0.79639 | 18.795 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9931 | 0.76788 | 22.522 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97712 | 0.74045 | 23.667 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97712 | 0.76219 | 21.493 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97712 | 0.77522 | 20.19 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97712 | 0.79798 | 17.915 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9862 | 0.87345 | 11.275 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98516 | 0.75149 | 23.366 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99255 | 0.79547 | 19.708 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98782 | 0.80074 | 18.709 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98656 | 0.762 | 22.456 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98656 | 0.76373 | 22.282 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99626 | 0.79532 | 20.094 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99626 | 0.90577 | 9.049 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98191 | 0.77991 | 20.2 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98191 | 0.79077 | 19.114 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99184 | 0.88791 | 10.394 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.90916 | 8.246 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98413 | 0.88423 | 9.99 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.90054 | 9.008 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.9011 | 8.947 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98831 | 0.78883 | 19.948 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98831 | 0.89668 | 9.163 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98913 | 0.79411 | 19.501 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98902 | 0.80063 | 18.839 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99096 | 0.89454 | 9.642 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99012 | 0.90292 | 8.72 | Yes
Active | 2025W1-N11-WVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98878 | 0.79932 | 18.946 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.90728 | 8.431 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.89499 | 9.374 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98809 | 0.80386 | 18.423 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.80198 | 18.656 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9874 | 0.80371 | 18.37 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98984 | 0.7926 | 19.723 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98567 | 0.88572 | 9.995 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96677 | 0.73703 | 22.974 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96677 | 0.75441 | 21.236 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96677 | 0.7663 | 20.046 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96677 | 0.77091 | 19.586 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96677 | 0.78654 | 18.023 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96677 | 0.8748 | 9.196 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96677 | 0.88023 | 8.654 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99265 | 0.76492 | 22.773 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.90863 | 8.312 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9858 | 0.90277 | 8.304 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98667 | 0.79399 | 19.268 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9872 | 0.79447 | 19.273 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.90401 | 8.629 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99081 | 0.90774 | 8.307 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99088 | 0.90775 | 8.313 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98823 | 0.80522 | 18.301 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98483 | 0.79803 | 18.68 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98483 | 0.89598 | 8.885 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.90165 | 8.669 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.90789 | 8.347 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98617 | 0.79596 | 19.02 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98617 | 0.90602 | 8.014 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98345 | 0.78518 | 19.827 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98345 | 0.79832 | 18.513 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99273 | 0.76657 | 22.616 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97281 | 0.73667 | 23.614 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97281 | 0.7648 | 20.802 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97281 | 0.77043 | 20.238 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97281 | 0.80018 | 17.263 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98534 | 0.87158 | 11.376 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98666 | 0.7509 | 23.576 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.90984 | 8.021 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.79505 | 19.63 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98688 | 0.80034 | 18.654 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98737 | 0.76561 | 22.176 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98737 | 0.76629 | 22.108 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99674 | 0.7974 | 19.935 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99674 | 0.90623 | 9.051 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98118 | 0.78199 | 19.92 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98118 | 0.79401 | 18.717 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.88545 | 10.552 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98673 | 0.90545 | 8.128 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98673 | 0.90545 | 8.128 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.90656 | 8.413 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98567 | 0.88572 | 9.995 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98996 | 0.8987 | 9.126 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.89925 | 9.067 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98724 | 0.7908 | 19.644 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98724 | 0.89595 | 9.129 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98835 | 0.79611 | 19.224 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98822 | 0.80148 | 18.674 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99014 | 0.89269 | 9.745 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.90067 | 8.87 | Yes
Active | 2025W1-N11-WVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98802 | 0.80033 | 18.77 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97923 | 0.89722 | 8.201 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97546 | 0.88313 | 9.233 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97591 | 0.79626 | 17.965 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97609 | 0.79343 | 18.266 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97496 | 0.79539 | 17.956 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97761 | 0.78408 | 19.353 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97343 | 0.87605 | 9.738 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95601 | 0.73149 | 22.451 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95601 | 0.74848 | 20.752 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95601 | 0.75822 | 19.779 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95601 | 0.76438 | 19.162 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95601 | 0.77818 | 17.783 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98025 | 0.75869 | 22.156 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97942 | 0.89845 | 8.097 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97482 | 0.89433 | 8.049 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97413 | 0.78525 | 18.888 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9747 | 0.78575 | 18.894 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97788 | 0.89389 | 8.4 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97841 | 0.89757 | 8.084 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97848 | 0.89757 | 8.091 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.976 | 0.79716 | 17.884 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97257 | 0.79021 | 18.236 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97257 | 0.88544 | 8.713 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97611 | 0.89178 | 8.434 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.8977 | 8.13 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97381 | 0.78808 | 18.573 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97104 | 0.7773 | 19.375 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97104 | 0.78916 | 18.188 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98034 | 0.75973 | 22.061 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96148 | 0.73114 | 23.034 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96148 | 0.75583 | 20.565 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96148 | 0.76442 | 19.706 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96148 | 0.79051 | 17.098 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97278 | 0.86164 | 11.114 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9728 | 0.74469 | 22.811 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9791 | 0.78838 | 19.072 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97478 | 0.79292 | 18.186 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97408 | 0.75625 | 21.782 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97408 | 0.75784 | 21.623 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98394 | 0.78889 | 19.505 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98394 | 0.8949 | 8.904 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96838 | 0.77329 | 19.509 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96838 | 0.78405 | 18.432 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97869 | 0.87587 | 10.283 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97829 | 0.8964 | 8.189 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97343 | 0.87605 | 9.738 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97729 | 0.88805 | 8.924 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97724 | 0.8886 | 8.864 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97484 | 0.78215 | 19.269 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97484 | 0.88483 | 9.001 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97591 | 0.78743 | 18.847 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97577 | 0.79297 | 18.279 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97769 | 0.88258 | 9.511 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9769 | 0.89051 | 8.639 | Yes
Active | 2025W1-N11-WVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97556 | 0.79179 | 18.376 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99876 | 0.91554 | 8.322 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99652 | 0.82121 | 17.531 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.81798 | 17.896 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.8206 | 17.535 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99935 | 0.80723 | 19.212 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99178 | 0.89798 | 9.38 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98014 | 0.75949 | 22.065 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98014 | 0.77125 | 20.888 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98014 | 0.77816 | 20.198 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98014 | 0.79001 | 19.012 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98014 | 0.80006 | 18.007 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98014 | 0.80481 | 17.533 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98014 | 0.80955 | 17.059 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98014 | 0.89133 | 8.881 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98014 | 0.89555 | 8.459 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.79202 | 20.856 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99465 | 0.80751 | 18.714 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99529 | 0.80815 | 18.714 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99673 | 0.82244 | 17.429 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99327 | 0.81486 | 17.841 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99327 | 0.90995 | 8.331 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99474 | 0.81046 | 18.428 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99327 | 0.79894 | 19.433 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99327 | 0.81143 | 18.184 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99943 | 0.78602 | 21.341 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98527 | 0.75907 | 22.621 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98527 | 0.77519 | 21.009 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98527 | 0.79672 | 18.855 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98527 | 0.8123 | 17.297 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.89006 | 10.51 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99202 | 0.76808 | 22.394 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.81218 | 18.814 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.81756 | 17.773 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99212 | 0.77611 | 21.6 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.77822 | 21.39 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.80985 | 19.161 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.91537 | 8.608 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98957 | 0.79546 | 19.411 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98957 | 0.80614 | 18.343 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99896 | 0.90253 | 9.643 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99178 | 0.89798 | 9.38 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99841 | 0.91435 | 8.405 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99837 | 0.91488 | 8.348 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.80471 | 19.141 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99612 | 0.90926 | 8.686 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99668 | 0.81017 | 18.651 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99661 | 0.81753 | 17.908 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99855 | 0.90787 | 9.068 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99774 | 0.91609 | 8.164 | Yes
Active | 2025W1-N11-WVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.81617 | 18.02 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98891 | 0.90551 | 8.34 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98761 | 0.81413 | 17.348 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98762 | 0.80835 | 17.927 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98655 | 0.81211 | 17.444 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.79736 | 19.387 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98395 | 0.89095 | 9.299 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97188 | 0.75424 | 21.763 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97188 | 0.76658 | 20.53 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97188 | 0.771 | 20.088 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97188 | 0.78417 | 18.77 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97188 | 0.7906 | 18.128 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97188 | 0.80261 | 16.927 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97188 | 0.8849 | 8.698 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97188 | 0.889 | 8.288 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99147 | 0.78375 | 20.772 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98485 | 0.79633 | 18.853 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98565 | 0.79708 | 18.857 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98772 | 0.81494 | 17.279 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9845 | 0.8079 | 17.66 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9845 | 0.90129 | 8.321 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9852 | 0.80448 | 18.072 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9834 | 0.79242 | 19.099 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9834 | 0.8034 | 18.001 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99049 | 0.77918 | 21.131 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97645 | 0.75386 | 22.259 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97645 | 0.76712 | 20.933 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97645 | 0.78949 | 18.696 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97645 | 0.80172 | 17.473 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98495 | 0.8791 | 10.585 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98241 | 0.76242 | 21.999 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99108 | 0.80596 | 18.512 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98652 | 0.81076 | 17.577 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98165 | 0.76689 | 21.476 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98165 | 0.76999 | 21.167 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.80192 | 19.035 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99227 | 0.90572 | 8.654 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97878 | 0.78499 | 19.379 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97878 | 0.79457 | 18.421 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99006 | 0.89347 | 9.659 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98395 | 0.89095 | 9.299 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98861 | 0.90356 | 8.505 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.9041 | 8.444 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98716 | 0.79417 | 19.299 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98716 | 0.8985 | 8.865 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98734 | 0.79937 | 18.798 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.80813 | 17.919 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.89835 | 9.085 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98828 | 0.90672 | 8.156 | Yes
Active | 2025W1-N11-WVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98701 | 0.80652 | 18.049 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.83761 | 16.305 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.83289 | 16.801 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99997 | 0.83542 | 16.455 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.8215 | 18.204 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99736 | 0.9106 | 8.676 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98564 | 0.77931 | 20.633 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98564 | 0.78944 | 19.62 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98564 | 0.79222 | 19.342 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98564 | 0.80747 | 17.817 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98564 | 0.81139 | 17.425 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98564 | 0.81377 | 17.187 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98564 | 0.82278 | 16.286 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98564 | 0.90343 | 8.221 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0041 | 0.8112 | 19.292 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99852 | 0.82152 | 17.7 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99918 | 0.82219 | 17.699 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.83821 | 16.252 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99766 | 0.83073 | 16.693 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.83716 | 16.338 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.80557 | 18.901 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99458 | 0.8164 | 17.818 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.80374 | 19.887 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9894 | 0.77891 | 21.049 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9894 | 0.78769 | 20.171 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9894 | 0.81557 | 17.382 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9894 | 0.82386 | 16.554 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99929 | 0.90143 | 9.787 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.78658 | 20.872 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.82932 | 17.464 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99966 | 0.83434 | 16.532 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99392 | 0.78894 | 20.498 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99392 | 0.79267 | 20.124 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.82334 | 18.03 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0036 | 0.92102 | 8.262 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99294 | 0.80938 | 18.356 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99294 | 0.81803 | 17.491 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.91365 | 8.934 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99736 | 0.9106 | 8.676 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.81876 | 18.144 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.91682 | 8.338 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.8243 | 17.628 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.83215 | 16.834 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.91684 | 8.525 | Yes
Active | 2025W1-N11-WVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.83089 | 16.935 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.91476 | 8.288 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99482 | 0.90295 | 9.187 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99403 | 0.80904 | 18.499 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.80673 | 18.778 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.80886 | 18.454 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.79677 | 19.953 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98925 | 0.88934 | 9.992 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97558 | 0.74431 | 23.126 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97558 | 0.75928 | 21.63 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97558 | 0.76948 | 20.61 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97558 | 0.77699 | 19.858 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97558 | 0.7907 | 18.487 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97558 | 0.80065 | 17.492 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97558 | 0.88184 | 9.374 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97558 | 0.88752 | 8.805 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99851 | 0.77379 | 22.473 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99778 | 0.91639 | 8.14 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99154 | 0.90997 | 8.158 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.79769 | 19.475 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99303 | 0.79824 | 19.479 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99636 | 0.91157 | 8.479 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99689 | 0.9154 | 8.149 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99696 | 0.91539 | 8.156 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99417 | 0.81053 | 18.364 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99074 | 0.80305 | 18.769 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99074 | 0.90292 | 8.783 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99453 | 0.90936 | 8.517 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.91566 | 8.174 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.80063 | 19.151 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98961 | 0.78929 | 20.031 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98961 | 0.80237 | 18.724 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99814 | 0.77241 | 22.573 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98154 | 0.74392 | 23.761 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98154 | 0.76765 | 21.388 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98154 | 0.77935 | 20.219 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98154 | 0.80412 | 17.742 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.87927 | 11.245 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.75553 | 23.552 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.79908 | 19.865 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.80535 | 18.742 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99232 | 0.76814 | 22.419 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.76911 | 22.322 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.80065 | 20.081 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.91151 | 8.994 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98752 | 0.78574 | 20.178 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98752 | 0.79749 | 19.003 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99691 | 0.89286 | 10.405 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.9142 | 8.258 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98925 | 0.88934 | 9.992 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99592 | 0.90604 | 8.989 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99588 | 0.90659 | 8.929 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.79468 | 19.871 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99339 | 0.90267 | 9.071 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.80004 | 19.426 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.80626 | 18.793 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.89982 | 9.631 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99534 | 0.90809 | 8.724 | Yes
Active | 2025W1-N11-WVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.805 | 18.898 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99756 | 0.9082 | 8.936 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99763 | 0.81612 | 18.152 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99789 | 0.81193 | 18.596 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.81494 | 18.182 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.80124 | 19.943 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.89282 | 9.804 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98308 | 0.75417 | 22.891 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98308 | 0.76779 | 21.529 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98308 | 0.77478 | 20.829 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98308 | 0.78559 | 19.749 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98308 | 0.79565 | 18.743 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98308 | 0.80186 | 18.122 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98308 | 0.80661 | 17.647 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98308 | 0.89095 | 9.213 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98308 | 0.89558 | 8.749 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.78305 | 21.881 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.80115 | 19.424 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99609 | 0.80182 | 19.428 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99981 | 0.91797 | 8.184 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99776 | 0.81716 | 18.06 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.80975 | 18.454 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9943 | 0.9085 | 8.579 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99803 | 0.91575 | 8.228 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.80663 | 18.876 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99301 | 0.79451 | 19.85 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99301 | 0.80644 | 18.656 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.77992 | 22.128 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98837 | 0.75379 | 23.458 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98837 | 0.77166 | 21.671 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98837 | 0.78959 | 19.878 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98837 | 0.80782 | 18.055 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99498 | 0.88521 | 10.978 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99303 | 0.76298 | 23.005 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.80727 | 19.398 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99645 | 0.81255 | 18.39 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9943 | 0.77091 | 22.339 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.77324 | 22.106 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.80537 | 19.835 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0037 | 0.9151 | 8.862 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99056 | 0.78945 | 20.111 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99056 | 0.79989 | 19.067 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.89972 | 10.063 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.89282 | 9.804 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99914 | 0.91171 | 8.743 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99908 | 0.91227 | 8.681 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99708 | 0.79855 | 19.853 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99708 | 0.90699 | 9.009 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99762 | 0.8039 | 19.372 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99756 | 0.81157 | 18.599 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99949 | 0.90564 | 9.385 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99862 | 0.91418 | 8.444 | Yes
Active | 2025W1-N11-WVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99729 | 0.81011 | 18.718 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.90911 | 8.284 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98819 | 0.89505 | 9.314 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98845 | 0.80356 | 18.489 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98876 | 0.80032 | 18.844 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98762 | 0.80276 | 18.486 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99088 | 0.79041 | 20.047 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98376 | 0.88379 | 9.997 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97073 | 0.74009 | 23.064 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97073 | 0.75521 | 21.552 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97073 | 0.76414 | 20.659 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97073 | 0.77236 | 19.837 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97073 | 0.7848 | 18.593 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97073 | 0.8778 | 9.293 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97073 | 0.88273 | 8.8 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99285 | 0.76821 | 22.465 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.91057 | 8.155 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98694 | 0.90559 | 8.135 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98654 | 0.79102 | 19.552 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98717 | 0.79159 | 19.558 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.90578 | 8.484 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.9096 | 8.155 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.90961 | 8.162 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98859 | 0.80469 | 18.391 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98508 | 0.7974 | 18.768 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98508 | 0.89678 | 8.83 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9888 | 0.90356 | 8.524 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.90982 | 8.189 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.79488 | 19.146 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98373 | 0.7836 | 20.014 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98373 | 0.7957 | 18.804 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.76718 | 22.539 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97636 | 0.73972 | 23.664 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97636 | 0.7616 | 21.476 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97636 | 0.77437 | 20.199 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97636 | 0.79726 | 17.91 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98559 | 0.87265 | 11.295 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98461 | 0.75089 | 23.372 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.79482 | 19.714 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.80003 | 18.722 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98599 | 0.76142 | 22.457 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98599 | 0.76316 | 22.284 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.7947 | 20.105 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99575 | 0.90511 | 9.064 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98125 | 0.77924 | 20.201 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98125 | 0.79008 | 19.117 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.88715 | 10.413 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.9084 | 8.263 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98376 | 0.88379 | 9.997 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.89977 | 9.026 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98998 | 0.90033 | 8.965 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9877 | 0.78816 | 19.955 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9877 | 0.89592 | 9.178 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.79344 | 19.51 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98843 | 0.79991 | 18.853 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99038 | 0.89379 | 9.659 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98954 | 0.90216 | 8.738 | Yes
Active | 2025W1-N11-WVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9882 | 0.7986 | 18.959 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97699 | 0.89534 | 8.166 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9732 | 0.88123 | 9.197 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97373 | 0.79605 | 17.769 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9739 | 0.79338 | 18.052 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97278 | 0.79521 | 17.757 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97528 | 0.78424 | 19.104 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97188 | 0.87541 | 9.647 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95315 | 0.73055 | 22.26 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95315 | 0.74813 | 20.502 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95315 | 0.75812 | 19.502 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95315 | 0.76377 | 18.937 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95315 | 0.77826 | 17.489 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97802 | 0.7577 | 22.031 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97716 | 0.89647 | 8.069 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9728 | 0.89268 | 8.012 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97204 | 0.78555 | 18.649 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97258 | 0.78603 | 18.655 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97564 | 0.89201 | 8.363 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97616 | 0.89564 | 8.052 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97623 | 0.89565 | 8.058 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9738 | 0.79686 | 17.694 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9704 | 0.79001 | 18.039 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9704 | 0.88375 | 8.666 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97387 | 0.88992 | 8.395 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97674 | 0.89572 | 8.102 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97167 | 0.78805 | 18.362 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96891 | 0.77747 | 19.144 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96891 | 0.78929 | 17.963 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97819 | 0.75926 | 21.893 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95856 | 0.7302 | 22.837 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95856 | 0.75573 | 20.283 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95856 | 0.76332 | 19.524 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95856 | 0.79056 | 16.8 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97052 | 0.86012 | 11.041 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97076 | 0.74448 | 22.628 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97684 | 0.78856 | 18.829 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97263 | 0.79276 | 17.986 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97196 | 0.75632 | 21.563 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97196 | 0.75792 | 21.403 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98189 | 0.789 | 19.289 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98189 | 0.89341 | 8.848 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9662 | 0.77354 | 19.265 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9662 | 0.78431 | 18.188 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97646 | 0.87417 | 10.229 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97604 | 0.89449 | 8.155 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97188 | 0.87541 | 9.647 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97504 | 0.88623 | 8.88 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97499 | 0.88677 | 8.821 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97263 | 0.78239 | 19.023 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97263 | 0.88329 | 8.933 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97374 | 0.78766 | 18.608 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97358 | 0.79291 | 18.067 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97547 | 0.88095 | 9.452 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97469 | 0.88871 | 8.598 | Yes
Active | 2025W1-N11-WVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97338 | 0.79177 | 18.161 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98347 | 0.90015 | 8.332 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97989 | 0.88747 | 9.241 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97971 | 0.7999 | 17.981 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97973 | 0.79761 | 18.212 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97877 | 0.7991 | 17.967 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98023 | 0.78927 | 19.096 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97877 | 0.88131 | 9.746 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95804 | 0.73523 | 22.281 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95804 | 0.75139 | 20.665 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95804 | 0.75991 | 19.813 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95804 | 0.7673 | 19.074 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95804 | 0.78226 | 17.579 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98437 | 0.7635 | 22.086 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98355 | 0.90169 | 8.186 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97897 | 0.89765 | 8.132 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9783 | 0.79167 | 18.663 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97877 | 0.79207 | 18.671 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98161 | 0.89651 | 8.51 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.90025 | 8.191 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98224 | 0.90025 | 8.199 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97983 | 0.80022 | 17.961 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97621 | 0.79334 | 18.288 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97621 | 0.88807 | 8.815 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97987 | 0.89455 | 8.532 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98315 | 0.90097 | 8.218 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97784 | 0.79221 | 18.563 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97457 | 0.78148 | 19.309 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97457 | 0.79359 | 18.098 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98405 | 0.76372 | 22.033 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96366 | 0.73502 | 22.863 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96366 | 0.75801 | 20.565 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96366 | 0.76813 | 19.553 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96366 | 0.79495 | 16.871 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97612 | 0.86386 | 11.225 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97606 | 0.74839 | 22.767 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98383 | 0.79143 | 19.24 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97861 | 0.79665 | 18.196 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97611 | 0.75915 | 21.696 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97611 | 0.7604 | 21.571 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.7918 | 19.532 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98712 | 0.89716 | 8.996 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9718 | 0.77808 | 19.372 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9718 | 0.78917 | 18.262 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98255 | 0.87802 | 10.453 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98205 | 0.89909 | 8.297 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97877 | 0.88131 | 9.746 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97874 | 0.88634 | 9.24 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97859 | 0.8869 | 9.169 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97807 | 0.78784 | 19.022 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97807 | 0.88846 | 8.961 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97974 | 0.79351 | 18.624 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97937 | 0.79701 | 18.236 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98129 | 0.88524 | 9.605 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98058 | 0.89317 | 8.741 | Yes
Active | 2025W1-N11-WVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97918 | 0.79597 | 18.321 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99652 | 0.91438 | 8.214 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.90177 | 9.161 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99295 | 0.80846 | 18.449 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.8056 | 18.782 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.80802 | 18.429 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.79553 | 20.003 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98725 | 0.88749 | 9.977 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97586 | 0.74469 | 23.117 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97586 | 0.75909 | 21.677 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97586 | 0.76844 | 20.742 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97586 | 0.777 | 19.885 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97586 | 0.78978 | 18.608 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97586 | 0.79986 | 17.6 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97586 | 0.88228 | 9.357 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97586 | 0.88771 | 8.815 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99737 | 0.77377 | 22.36 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99668 | 0.91597 | 8.071 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9909 | 0.91015 | 8.075 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.79611 | 19.511 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.79669 | 19.516 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.91113 | 8.41 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99576 | 0.91497 | 8.079 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.91497 | 8.086 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99313 | 0.80981 | 18.332 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98964 | 0.80237 | 18.727 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98964 | 0.90223 | 8.741 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.90892 | 8.45 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99628 | 0.91523 | 8.105 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.79979 | 19.118 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98849 | 0.78834 | 20.016 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98849 | 0.80095 | 18.754 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.77197 | 22.496 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98164 | 0.74431 | 23.733 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98164 | 0.76618 | 21.546 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98164 | 0.77976 | 20.188 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98164 | 0.80272 | 17.892 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99042 | 0.87842 | 11.2 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98921 | 0.7549 | 23.431 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.79893 | 19.766 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.80483 | 18.688 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99071 | 0.76615 | 22.457 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99071 | 0.76758 | 22.313 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.79936 | 20.065 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1 | 0.91024 | 8.977 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98644 | 0.78433 | 20.211 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98644 | 0.79559 | 19.085 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99578 | 0.89246 | 10.332 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99565 | 0.91377 | 8.188 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98725 | 0.88749 | 9.977 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.90533 | 8.938 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.90589 | 8.878 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.79326 | 19.916 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99242 | 0.90166 | 9.077 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.79856 | 19.464 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9931 | 0.80517 | 18.793 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.995 | 0.89919 | 9.581 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99417 | 0.90756 | 8.661 | Yes
Active | 2025W1-N11-WVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99286 | 0.80385 | 18.901 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.91647 | 8.045 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.90235 | 9.062 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.81169 | 18.178 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.80781 | 18.588 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99255 | 0.8106 | 18.195 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.79738 | 19.88 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98732 | 0.88909 | 9.823 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97834 | 0.7495 | 22.884 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97834 | 0.76379 | 21.456 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97834 | 0.77149 | 20.686 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97834 | 0.78126 | 19.709 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97834 | 0.79208 | 18.626 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97834 | 0.79814 | 18.02 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97834 | 0.80303 | 17.532 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97834 | 0.88629 | 9.205 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97834 | 0.89103 | 8.731 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99774 | 0.77778 | 21.996 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.79756 | 19.373 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.7982 | 19.377 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.91322 | 8.242 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.81277 | 18.083 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99014 | 0.80542 | 18.473 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99014 | 0.90399 | 8.616 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99385 | 0.91101 | 8.284 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9913 | 0.80252 | 18.878 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.79075 | 19.806 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98881 | 0.80275 | 18.606 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.77546 | 22.178 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98374 | 0.74912 | 23.462 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98374 | 0.76861 | 21.513 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98374 | 0.78449 | 19.925 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98374 | 0.80438 | 17.936 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99079 | 0.88052 | 11.027 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98928 | 0.75886 | 23.042 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.80282 | 19.424 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.80814 | 18.415 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99065 | 0.76778 | 22.287 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99065 | 0.76985 | 22.08 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.8017 | 19.832 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1 | 0.91125 | 8.877 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.78581 | 20.052 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98633 | 0.79643 | 18.99 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99623 | 0.89491 | 10.131 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.91584 | 8.022 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98732 | 0.88909 | 9.823 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.90715 | 8.787 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99497 | 0.90771 | 8.726 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.79486 | 19.791 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99276 | 0.90264 | 9.013 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.80019 | 19.324 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.80743 | 18.593 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.90106 | 9.426 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99448 | 0.90951 | 8.497 | Yes
Active | 2025W1-N11-WVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99311 | 0.80603 | 18.708 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.86971 | 13.544 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.86848 | 13.737 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.86824 | 13.683 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.85898 | 14.715 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99147 | 0.81746 | 17.401 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99147 | 0.82581 | 16.567 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99147 | 0.82905 | 16.242 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99147 | 0.84268 | 14.879 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99147 | 0.84564 | 14.583 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99147 | 0.85283 | 13.865 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99147 | 0.85505 | 13.642 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0082 | 0.85121 | 15.7 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.86107 | 14.343 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.86146 | 14.338 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.86972 | 13.553 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.85946 | 14.206 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.87157 | 13.444 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99761 | 0.84116 | 15.645 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99761 | 0.84958 | 14.803 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.83987 | 16.579 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.81686 | 17.675 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99361 | 0.82426 | 16.935 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99361 | 0.85426 | 13.935 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99361 | 0.86099 | 13.262 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.92738 | 8.06 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.82394 | 17.666 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.86232 | 14.626 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.86699 | 13.73 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9997 | 0.82691 | 17.28 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9997 | 0.83061 | 16.91 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.85617 | 15.082 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99965 | 0.84935 | 15.03 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99965 | 0.85678 | 14.287 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.85763 | 14.693 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86285 | 14.272 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.86742 | 13.802 | Yes
Active | 2025W1-N11-WVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86672 | 13.861 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99924 | 0.91694 | 8.23 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99736 | 0.90845 | 8.89 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.8142 | 18.123 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.81382 | 18.236 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.81536 | 17.98 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99753 | 0.80417 | 19.336 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.89772 | 9.638 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97539 | 0.75052 | 22.486 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97539 | 0.76324 | 21.215 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97539 | 0.77399 | 20.14 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97539 | 0.78272 | 19.266 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97539 | 0.79786 | 17.753 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97539 | 0.80125 | 17.414 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97539 | 0.80526 | 17.013 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97539 | 0.88407 | 9.131 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97539 | 0.88922 | 8.616 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99962 | 0.78424 | 21.538 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.91913 | 8.001 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.91117 | 8.094 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.80548 | 18.892 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.80598 | 18.892 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99797 | 0.91425 | 8.372 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99852 | 0.91805 | 8.047 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99856 | 0.91801 | 8.054 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.81628 | 17.92 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99222 | 0.80858 | 18.364 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99222 | 0.90559 | 8.663 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99639 | 0.91254 | 8.385 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99882 | 0.91846 | 8.036 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.80655 | 18.748 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.79571 | 19.624 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99195 | 0.80962 | 18.233 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99881 | 0.77877 | 22.004 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98138 | 0.74988 | 23.149 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98138 | 0.77272 | 20.866 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98138 | 0.78877 | 19.261 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98138 | 0.81168 | 16.97 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99443 | 0.88524 | 10.919 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.76013 | 23.203 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9994 | 0.80418 | 19.523 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99403 | 0.81026 | 18.377 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99228 | 0.7741 | 21.819 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99228 | 0.7742 | 21.808 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.80566 | 19.599 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.91339 | 8.826 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98912 | 0.79342 | 19.569 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98912 | 0.80601 | 18.31 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99813 | 0.8959 | 10.224 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99842 | 0.9169 | 8.152 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.89772 | 9.638 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.90965 | 8.799 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99761 | 0.91018 | 8.743 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.80232 | 19.275 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99507 | 0.90699 | 8.809 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.80767 | 18.832 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99588 | 0.8133 | 18.258 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99774 | 0.90333 | 9.441 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99703 | 0.91122 | 8.581 | Yes
Active | 2025W1-N11-WVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9957 | 0.81215 | 18.355 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.92111 | 8.619 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.92044 | 8.71 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.91744 | 8.92 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91288 | 9.393 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.998 | 0.88624 | 11.176 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.998 | 0.88723 | 11.076 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.998 | 0.89156 | 10.643 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.998 | 0.90138 | 9.662 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.998 | 0.90367 | 9.433 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.998 | 0.90443 | 9.357 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.998 | 0.90927 | 8.872 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0085 | 0.91024 | 9.826 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.9151 | 9.137 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.91529 | 9.137 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.92073 | 8.617 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.91299 | 9.192 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99782 | 0.89859 | 9.922 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99782 | 0.90234 | 9.548 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.90181 | 10.457 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99777 | 0.88276 | 11.5 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99777 | 0.88668 | 11.108 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99777 | 0.91223 | 8.553 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99777 | 0.91337 | 8.44 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.89065 | 11.196 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.91537 | 9.328 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91967 | 8.717 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0003 | 0.88637 | 11.39 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.88904 | 11.123 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.9064 | 9.974 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.90713 | 9.53 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.91091 | 9.151 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.91219 | 9.377 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.91609 | 9.096 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.91874 | 8.816 | Yes
Active | 2025W1-N11-WVD243534 | 243534 | 05LICK | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91865 | 8.817 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.90768 | 8.279 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98635 | 0.89287 | 9.348 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98702 | 0.80256 | 18.446 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.79913 | 18.815 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98614 | 0.80162 | 18.451 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98948 | 0.78924 | 20.024 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.88303 | 9.968 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96933 | 0.7394 | 22.993 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96933 | 0.75459 | 21.474 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96933 | 0.76316 | 20.616 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96933 | 0.77159 | 19.773 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96933 | 0.78378 | 18.554 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96933 | 0.87693 | 9.24 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96933 | 0.88165 | 8.768 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99137 | 0.76729 | 22.408 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.9091 | 8.153 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.90439 | 8.128 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98503 | 0.78975 | 19.527 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98567 | 0.79034 | 19.533 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98914 | 0.90434 | 8.48 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.90816 | 8.152 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98975 | 0.90816 | 8.159 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98714 | 0.8036 | 18.354 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98364 | 0.79639 | 18.725 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98364 | 0.89531 | 8.834 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98733 | 0.90213 | 8.52 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.90835 | 8.187 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98488 | 0.79386 | 19.102 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98228 | 0.78265 | 19.963 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98228 | 0.79455 | 18.773 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99107 | 0.76623 | 22.484 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97487 | 0.73903 | 23.584 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97487 | 0.76047 | 21.44 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97487 | 0.77363 | 20.124 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97487 | 0.79605 | 17.881 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98408 | 0.8712 | 11.288 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98301 | 0.75009 | 23.292 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99051 | 0.79408 | 19.643 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98584 | 0.79907 | 18.677 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98422 | 0.76009 | 22.413 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98422 | 0.76199 | 22.223 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9942 | 0.79355 | 20.065 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9942 | 0.90347 | 9.073 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97957 | 0.77804 | 20.152 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97957 | 0.78871 | 19.086 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9898 | 0.88577 | 10.404 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98956 | 0.90696 | 8.26 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.88303 | 9.968 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98853 | 0.89828 | 9.025 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.89884 | 8.964 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98625 | 0.78695 | 19.931 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98625 | 0.89432 | 9.193 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98706 | 0.7922 | 19.486 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98695 | 0.79873 | 18.822 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98889 | 0.89235 | 9.655 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.90071 | 8.734 | Yes
Active | 2025W1-N11-WVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98671 | 0.79742 | 18.929 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.91296 | 8.242 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.81883 | 17.448 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99365 | 0.81495 | 17.87 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99268 | 0.8178 | 17.487 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.80398 | 19.233 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98828 | 0.89486 | 9.342 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97727 | 0.75753 | 21.974 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97727 | 0.76904 | 20.823 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97727 | 0.77505 | 20.222 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97727 | 0.78761 | 18.966 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97727 | 0.79666 | 18.062 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97727 | 0.80168 | 17.559 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97727 | 0.80641 | 17.087 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97727 | 0.88905 | 8.822 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97727 | 0.89313 | 8.414 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99727 | 0.78987 | 20.74 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99126 | 0.80402 | 18.724 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.80469 | 18.725 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99353 | 0.81993 | 17.36 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99011 | 0.81237 | 17.774 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99011 | 0.90712 | 8.299 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99161 | 0.80871 | 18.29 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.79578 | 19.427 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99004 | 0.80789 | 18.216 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.78362 | 21.238 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9822 | 0.75713 | 22.507 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9822 | 0.7717 | 21.05 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9822 | 0.79457 | 18.764 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9822 | 0.80848 | 17.372 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.88722 | 10.464 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98841 | 0.76586 | 22.255 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.80997 | 18.71 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99214 | 0.81523 | 17.69 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98829 | 0.77256 | 21.573 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.77509 | 21.321 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99784 | 0.80667 | 19.116 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99784 | 0.91178 | 8.606 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9861 | 0.79204 | 19.406 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9861 | 0.80226 | 18.384 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99566 | 0.89986 | 9.581 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98828 | 0.89486 | 9.342 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.91136 | 8.37 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.91189 | 8.312 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.80132 | 19.159 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99291 | 0.9059 | 8.7 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.80678 | 18.661 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99331 | 0.8145 | 17.881 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99525 | 0.90495 | 9.03 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.91324 | 8.117 | Yes
Active | 2025W1-N11-WVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.81309 | 17.997 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97863 | 0.89602 | 8.261 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97556 | 0.88332 | 9.225 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97539 | 0.7975 | 17.789 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97566 | 0.79547 | 18.019 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97454 | 0.797 | 17.754 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9767 | 0.7865 | 19.02 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97395 | 0.87677 | 9.718 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95303 | 0.72888 | 22.414 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95303 | 0.7482 | 20.483 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95303 | 0.76107 | 19.196 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95303 | 0.76368 | 18.935 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95303 | 0.78049 | 17.254 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97976 | 0.75553 | 22.423 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97878 | 0.89705 | 8.172 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97431 | 0.8931 | 8.122 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97394 | 0.7881 | 18.584 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97443 | 0.78854 | 18.589 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97736 | 0.89278 | 8.459 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97785 | 0.89632 | 8.152 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97791 | 0.89634 | 8.158 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97548 | 0.79855 | 17.694 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97221 | 0.7917 | 18.051 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97221 | 0.88515 | 8.706 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97529 | 0.89026 | 8.503 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97837 | 0.89631 | 8.206 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97341 | 0.78981 | 18.361 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97063 | 0.77938 | 19.125 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97063 | 0.79199 | 17.864 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98015 | 0.75941 | 22.074 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95873 | 0.72857 | 23.016 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95873 | 0.75925 | 19.948 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95873 | 0.7611 | 19.763 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95873 | 0.79372 | 16.501 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9722 | 0.861 | 11.12 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97496 | 0.74474 | 23.022 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97822 | 0.79282 | 18.54 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97429 | 0.7942 | 18.009 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97526 | 0.76015 | 21.511 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97526 | 0.76118 | 21.408 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.79203 | 19.251 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98454 | 0.89605 | 8.849 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96829 | 0.77613 | 19.217 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96829 | 0.78775 | 18.054 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97808 | 0.87501 | 10.307 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97772 | 0.89519 | 8.254 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97395 | 0.87677 | 9.718 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97704 | 0.88761 | 8.943 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.977 | 0.88814 | 8.886 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97431 | 0.78484 | 18.947 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97431 | 0.88495 | 8.935 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9755 | 0.79009 | 18.541 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97535 | 0.79497 | 18.038 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97722 | 0.88195 | 9.527 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97646 | 0.88952 | 8.694 | Yes
Active | 2025W1-N11-WVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97517 | 0.79389 | 18.128 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97851 | 0.89592 | 8.26 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97545 | 0.88322 | 9.223 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97528 | 0.79744 | 17.784 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97554 | 0.7954 | 18.014 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97442 | 0.79694 | 17.748 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97658 | 0.78644 | 19.013 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97384 | 0.87668 | 9.715 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9529 | 0.7288 | 22.41 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9529 | 0.74817 | 20.472 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9529 | 0.76104 | 19.186 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9529 | 0.76361 | 18.929 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9529 | 0.78043 | 17.246 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97965 | 0.75541 | 22.423 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97866 | 0.89694 | 8.171 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9742 | 0.893 | 8.12 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97382 | 0.78804 | 18.578 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97431 | 0.78849 | 18.583 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97724 | 0.89267 | 8.457 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97773 | 0.89622 | 8.151 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97779 | 0.89623 | 8.157 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97536 | 0.79848 | 17.688 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97209 | 0.79163 | 18.046 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97209 | 0.88504 | 8.705 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97517 | 0.89015 | 8.502 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97825 | 0.8962 | 8.205 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97329 | 0.78974 | 18.355 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97051 | 0.77932 | 19.119 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97051 | 0.79193 | 17.857 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.75933 | 22.07 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9586 | 0.72848 | 23.012 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9586 | 0.75922 | 19.938 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9586 | 0.76099 | 19.761 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9586 | 0.79366 | 16.494 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97208 | 0.8609 | 11.118 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97489 | 0.74471 | 23.018 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97809 | 0.79279 | 18.53 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97418 | 0.79414 | 18.004 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97517 | 0.76012 | 21.505 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97517 | 0.76116 | 21.401 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98444 | 0.79199 | 19.245 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98444 | 0.89598 | 8.846 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96817 | 0.77607 | 19.21 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96817 | 0.7877 | 18.047 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97796 | 0.87491 | 10.305 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9776 | 0.89508 | 8.253 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97384 | 0.87668 | 9.715 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97692 | 0.88751 | 8.941 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97689 | 0.88804 | 8.884 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97419 | 0.78479 | 18.94 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97419 | 0.88485 | 8.933 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97538 | 0.79003 | 18.535 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97523 | 0.79491 | 18.032 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9771 | 0.88185 | 9.525 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97634 | 0.88941 | 8.693 | Yes
Active | 2025W1-N11-WVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97505 | 0.79382 | 18.122 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99738 | 0.91371 | 8.367 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.81858 | 17.718 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.8143 | 18.176 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.81734 | 17.773 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99891 | 0.8032 | 19.571 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.8942 | 9.518 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98033 | 0.75688 | 22.346 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98033 | 0.76858 | 21.175 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98033 | 0.77434 | 20.599 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98033 | 0.78706 | 19.327 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98033 | 0.79596 | 18.438 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98033 | 0.80122 | 17.912 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98033 | 0.80593 | 17.44 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98033 | 0.89051 | 8.982 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98033 | 0.89479 | 8.554 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99974 | 0.78878 | 21.096 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.80309 | 19.05 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.80378 | 19.052 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99594 | 0.81964 | 17.63 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99254 | 0.81203 | 18.051 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99254 | 0.90866 | 8.388 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99385 | 0.8093 | 18.454 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.79512 | 19.699 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99211 | 0.80704 | 18.507 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99848 | 0.78289 | 21.559 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98525 | 0.75649 | 22.876 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98525 | 0.77078 | 21.447 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98525 | 0.79369 | 19.156 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98525 | 0.80766 | 17.759 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.88786 | 10.617 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99061 | 0.76522 | 22.54 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99949 | 0.80962 | 18.987 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.81496 | 17.962 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99085 | 0.77143 | 21.942 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99085 | 0.7742 | 21.665 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.80604 | 19.431 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.9132 | 8.715 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98869 | 0.79115 | 19.754 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98869 | 0.8012 | 18.749 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99818 | 0.90102 | 9.716 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.8942 | 9.518 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99738 | 0.91261 | 8.477 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99734 | 0.91316 | 8.418 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99536 | 0.80044 | 19.491 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99536 | 0.90711 | 8.824 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9958 | 0.8059 | 18.99 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99572 | 0.81386 | 18.186 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99766 | 0.90626 | 9.14 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.91474 | 8.203 | Yes
Active | 2025W1-N11-WVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99545 | 0.8124 | 18.305 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.92376 | 8.123 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.82781 | 17.458 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.82208 | 18.038 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.82584 | 17.556 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.81062 | 19.544 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.90401 | 9.345 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98674 | 0.76683 | 21.991 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98674 | 0.77854 | 20.82 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98674 | 0.78291 | 20.383 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98674 | 0.79673 | 19.001 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98674 | 0.80292 | 18.382 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98674 | 0.81097 | 17.577 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98674 | 0.8149 | 17.184 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98674 | 0.89877 | 8.798 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98674 | 0.90292 | 8.382 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0063 | 0.79802 | 20.824 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99967 | 0.80964 | 19.003 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.81042 | 19.005 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.82871 | 17.383 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99925 | 0.82139 | 17.787 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99925 | 0.91619 | 8.306 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.81785 | 18.234 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.80479 | 19.366 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99845 | 0.81626 | 18.22 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.79242 | 21.266 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.76644 | 22.492 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99135 | 0.77903 | 21.232 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99135 | 0.80304 | 18.832 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99135 | 0.81435 | 17.7 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.89457 | 10.552 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9971 | 0.77505 | 22.206 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.81923 | 18.675 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.82431 | 17.696 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99648 | 0.77953 | 21.696 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.78261 | 21.388 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.81491 | 19.178 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0067 | 0.92021 | 8.648 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.79795 | 19.602 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99397 | 0.80772 | 18.625 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.90864 | 9.615 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.90401 | 9.345 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.91887 | 8.464 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.91942 | 8.403 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.80736 | 19.463 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.91349 | 8.85 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.81278 | 18.938 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.8218 | 18.033 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91338 | 9.068 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.92188 | 8.125 | Yes
Active | 2025W1-N11-WVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.82018 | 18.165 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99901 | 0.9175 | 8.152 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99621 | 0.9058 | 9.041 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.81143 | 18.4 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99584 | 0.80865 | 18.719 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.81098 | 18.373 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.79845 | 19.938 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.88909 | 9.963 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97864 | 0.74715 | 23.149 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97864 | 0.76176 | 21.689 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97864 | 0.77122 | 20.743 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97864 | 0.77951 | 19.913 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97864 | 0.79231 | 18.634 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97864 | 0.79725 | 18.139 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97864 | 0.80254 | 17.611 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97864 | 0.88487 | 9.378 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97864 | 0.89033 | 8.831 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99986 | 0.77668 | 22.319 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99916 | 0.91915 | 8.001 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.91301 | 8.017 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99366 | 0.79916 | 19.449 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.79974 | 19.453 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.91429 | 8.344 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99827 | 0.91814 | 8.013 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99834 | 0.91813 | 8.02 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.8128 | 18.276 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.80529 | 18.682 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99211 | 0.90538 | 8.673 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99591 | 0.91207 | 8.384 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99878 | 0.91842 | 8.036 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99346 | 0.80268 | 19.078 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99095 | 0.79101 | 19.993 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99095 | 0.80387 | 18.708 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99941 | 0.77483 | 22.458 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98447 | 0.74677 | 23.77 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98447 | 0.76909 | 21.537 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98447 | 0.78232 | 20.215 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98447 | 0.80546 | 17.9 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.88181 | 11.126 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.75791 | 23.421 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99912 | 0.80165 | 19.748 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.80775 | 18.643 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99384 | 0.76944 | 22.44 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99384 | 0.77072 | 22.312 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.8024 | 20.015 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.91352 | 8.903 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.7872 | 20.2 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9892 | 0.79865 | 19.055 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99827 | 0.89563 | 10.263 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.91694 | 8.122 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.88909 | 9.963 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99725 | 0.9086 | 8.865 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9972 | 0.90916 | 8.805 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99476 | 0.79622 | 19.854 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99476 | 0.90481 | 8.995 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99561 | 0.80161 | 19.399 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99551 | 0.8082 | 18.731 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99747 | 0.90234 | 9.513 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99666 | 0.91072 | 8.594 | Yes
Active | 2025W1-N11-WVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.80688 | 18.84 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0116 | 0.91145 | 10.013 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0116 | 0.91704 | 9.454 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0116 | 0.92056 | 9.101 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0116 | 0.92777 | 8.38 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0116 | 0.93087 | 8.071 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0206 | 0.93597 | 8.459 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0132 | 0.9323 | 8.092 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0188 | 0.92904 | 8.971 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0117 | 0.90918 | 10.252 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0117 | 0.91654 | 9.516 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0151 | 0.91967 | 9.54 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0207 | 0.94033 | 8.039 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0111 | 0.91293 | 9.82 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0111 | 0.91454 | 9.658 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.017 | 0.9301 | 8.694 | Yes
Active | 2025W1-N11-WVD243544 | 243544 | 05MILPRD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0148 | 0.93432 | 8.044 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.90997 | 9.336 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.90911 | 9.444 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.90649 | 9.622 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.90116 | 10.177 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99328 | 0.8732 | 12.008 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99328 | 0.87379 | 11.949 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99328 | 0.87807 | 11.521 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99328 | 0.8877 | 10.559 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99328 | 0.89096 | 10.232 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99328 | 0.89321 | 10.007 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99328 | 0.89708 | 9.62 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0048 | 0.89798 | 10.685 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.90343 | 9.902 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.90365 | 9.901 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.90952 | 9.342 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.90138 | 9.93 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.9235 | 8.327 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.88468 | 10.874 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99342 | 0.88885 | 10.457 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.88899 | 11.351 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99325 | 0.86981 | 12.344 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99325 | 0.87265 | 12.06 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99325 | 0.9001 | 9.315 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99325 | 0.90153 | 9.172 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.87705 | 12.141 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.90394 | 10.107 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.90835 | 9.447 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99622 | 0.87333 | 12.289 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99622 | 0.87647 | 11.975 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.89511 | 10.733 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.89478 | 10.334 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99812 | 0.89885 | 9.927 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.90039 | 10.16 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.90453 | 9.857 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.90744 | 9.55 | Yes
Active | 2025W1-N11-WVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.90729 | 9.556 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99768 | 0.91483 | 8.286 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.90287 | 9.195 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99408 | 0.80903 | 18.505 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99455 | 0.80663 | 18.792 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.80878 | 18.464 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99636 | 0.79666 | 19.97 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98914 | 0.88913 | 10.001 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97574 | 0.74431 | 23.143 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97574 | 0.75935 | 21.639 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97574 | 0.76949 | 20.625 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97574 | 0.77699 | 19.875 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97574 | 0.79061 | 18.513 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97574 | 0.80067 | 17.507 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97574 | 0.88194 | 9.38 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97574 | 0.88763 | 8.812 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99857 | 0.7736 | 22.497 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.91643 | 8.14 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.91007 | 8.155 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99246 | 0.79755 | 19.491 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99305 | 0.79811 | 19.494 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.91161 | 8.478 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.91544 | 8.148 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.91544 | 8.155 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99423 | 0.81048 | 18.375 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99078 | 0.80301 | 18.777 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99078 | 0.90295 | 8.784 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99456 | 0.90939 | 8.517 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.9157 | 8.174 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.80058 | 19.158 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98962 | 0.78923 | 20.039 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98962 | 0.80225 | 18.737 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99821 | 0.77237 | 22.584 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98169 | 0.74392 | 23.777 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98169 | 0.76763 | 21.406 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98169 | 0.77922 | 20.247 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98169 | 0.80399 | 17.77 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.87918 | 11.252 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.75556 | 23.553 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99776 | 0.79909 | 19.867 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.80536 | 18.747 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99242 | 0.76806 | 22.436 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.76908 | 22.334 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.80063 | 20.091 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.91157 | 8.997 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98755 | 0.78561 | 20.195 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98755 | 0.79731 | 19.025 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99696 | 0.89289 | 10.407 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99681 | 0.91425 | 8.257 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98914 | 0.88913 | 10.001 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.90604 | 8.991 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99591 | 0.9066 | 8.931 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.79455 | 19.887 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99342 | 0.90264 | 9.078 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.79991 | 19.442 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99422 | 0.80616 | 18.807 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99617 | 0.89983 | 9.633 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.90812 | 8.725 | Yes
Active | 2025W1-N11-WVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.80489 | 18.911 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99868 | 0.91474 | 8.395 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99721 | 0.81967 | 17.754 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99753 | 0.8154 | 18.213 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99651 | 0.81848 | 17.803 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.80436 | 19.607 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.89446 | 9.559 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98226 | 0.7577 | 22.457 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98226 | 0.76972 | 21.254 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98226 | 0.77572 | 20.654 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98226 | 0.78817 | 19.41 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98226 | 0.79726 | 18.5 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98226 | 0.8029 | 17.936 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98226 | 0.80747 | 17.479 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98226 | 0.89198 | 9.028 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98226 | 0.89634 | 8.592 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0012 | 0.78928 | 21.196 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99504 | 0.80418 | 19.086 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.80487 | 19.088 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.82075 | 17.664 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.81318 | 18.079 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99397 | 0.91025 | 8.372 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.81018 | 18.516 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.7967 | 19.671 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99341 | 0.80871 | 18.47 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.78384 | 21.625 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.75731 | 22.997 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98728 | 0.77229 | 21.499 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98728 | 0.79436 | 19.292 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98728 | 0.80915 | 17.813 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.88891 | 10.637 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.76621 | 22.599 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.8107 | 19.023 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.81605 | 17.998 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99281 | 0.77281 | 22 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99281 | 0.77544 | 21.737 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.80746 | 19.46 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0021 | 0.91517 | 8.689 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99041 | 0.79232 | 19.809 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99041 | 0.80253 | 18.788 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99966 | 0.90234 | 9.732 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.89446 | 9.559 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99881 | 0.91402 | 8.479 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99876 | 0.91457 | 8.419 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99684 | 0.80157 | 19.527 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99684 | 0.90874 | 8.81 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99727 | 0.80701 | 19.026 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.81499 | 18.22 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99911 | 0.90774 | 9.137 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.91623 | 8.2 | Yes
Active | 2025W1-N11-WVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.81352 | 18.341 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.88334 | 11.365 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.88183 | 11.492 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.87981 | 11.617 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99635 | 0.87182 | 12.453 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98478 | 0.84022 | 14.456 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98478 | 0.84033 | 14.445 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98478 | 0.84161 | 14.317 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98478 | 0.84599 | 13.879 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98478 | 0.86093 | 12.385 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98478 | 0.86498 | 11.98 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98478 | 0.86608 | 11.87 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99923 | 0.8682 | 13.103 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99524 | 0.87421 | 12.102 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99556 | 0.87454 | 12.102 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99673 | 0.88313 | 11.36 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99463 | 0.87636 | 11.827 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.91032 | 9.287 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98447 | 0.83636 | 14.81 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98447 | 0.84272 | 14.175 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99667 | 0.85863 | 13.804 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98578 | 0.83673 | 14.905 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98578 | 0.83976 | 14.602 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98578 | 0.87078 | 11.5 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98578 | 0.87159 | 11.419 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.84464 | 14.659 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99948 | 0.877 | 12.248 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99635 | 0.8812 | 11.515 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98752 | 0.83997 | 14.755 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98752 | 0.8441 | 14.341 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99586 | 0.86694 | 12.892 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98926 | 0.8634 | 12.586 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98926 | 0.86819 | 12.107 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.87063 | 12.423 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99622 | 0.87573 | 12.05 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.87969 | 11.627 | Yes
Active | 2025W1-N11-WVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.87956 | 11.628 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99796 | 0.82852 | 16.944 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.824 | 17.423 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99729 | 0.82679 | 17.051 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.81273 | 18.823 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.90285 | 9.053 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98267 | 0.76863 | 21.405 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98267 | 0.77937 | 20.331 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98267 | 0.78346 | 19.921 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98267 | 0.79768 | 18.499 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98267 | 0.80517 | 17.751 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98267 | 0.80633 | 17.634 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98267 | 0.81454 | 16.813 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98267 | 0.89706 | 8.562 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98267 | 0.90084 | 8.183 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.80068 | 20.097 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99582 | 0.8127 | 18.312 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9965 | 0.81338 | 18.312 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99808 | 0.82932 | 16.876 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99487 | 0.8218 | 17.307 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99487 | 0.91371 | 8.116 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99683 | 0.82375 | 17.307 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.8004 | 19.264 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99304 | 0.81169 | 18.135 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.79379 | 20.643 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98692 | 0.76823 | 21.869 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98692 | 0.77928 | 20.764 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98692 | 0.80527 | 18.165 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98692 | 0.81594 | 17.098 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.89487 | 10.16 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99263 | 0.77631 | 21.632 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.81993 | 18.153 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99688 | 0.82509 | 17.179 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9919 | 0.78028 | 21.162 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9919 | 0.78367 | 20.823 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.81491 | 18.668 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.91678 | 8.481 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9905 | 0.80061 | 18.989 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9905 | 0.80984 | 18.066 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90746 | 9.288 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.90285 | 9.053 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99944 | 0.91794 | 8.15 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99939 | 0.91847 | 8.093 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99753 | 0.80998 | 18.755 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99753 | 0.91186 | 8.566 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99795 | 0.8155 | 18.245 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99785 | 0.8234 | 17.446 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99962 | 0.91155 | 8.806 | Yes
Active | 2025W1-N11-WVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.82205 | 17.555 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99709 | 0.90749 | 8.96 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99735 | 0.81576 | 18.159 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.81158 | 18.602 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.81459 | 18.189 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.80093 | 19.946 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.89258 | 9.809 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98271 | 0.75375 | 22.896 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98271 | 0.76744 | 21.527 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98271 | 0.77444 | 20.826 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98271 | 0.78522 | 19.749 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98271 | 0.79538 | 18.733 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98271 | 0.80165 | 18.106 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98271 | 0.80629 | 17.642 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98271 | 0.89062 | 9.209 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98271 | 0.89524 | 8.747 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.78263 | 21.894 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.80084 | 19.427 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99582 | 0.80151 | 19.431 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99952 | 0.91758 | 8.195 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99748 | 0.8168 | 18.068 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.8094 | 18.461 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99402 | 0.90812 | 8.589 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.91535 | 8.238 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99513 | 0.80632 | 18.881 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.79427 | 19.85 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99277 | 0.80619 | 18.658 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.77952 | 22.138 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.988 | 0.75338 | 23.463 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.988 | 0.77131 | 21.669 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.988 | 0.7892 | 19.88 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.988 | 0.80755 | 18.045 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.88481 | 10.988 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99273 | 0.7626 | 23.013 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.80694 | 19.402 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99616 | 0.8122 | 18.397 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99396 | 0.77053 | 22.343 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99396 | 0.77287 | 22.109 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.80502 | 19.841 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0034 | 0.91472 | 8.872 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99026 | 0.78915 | 20.111 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99026 | 0.79959 | 19.067 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.8993 | 10.075 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.89258 | 9.809 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99885 | 0.91132 | 8.753 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9988 | 0.91188 | 8.691 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.79824 | 19.856 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9968 | 0.90663 | 9.017 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99734 | 0.80358 | 19.376 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99728 | 0.81122 | 18.605 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9992 | 0.90526 | 9.394 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99833 | 0.91379 | 8.454 | Yes
Active | 2025W1-N11-WVD243551 | 243551 | 05OSU | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99701 | 0.80977 | 18.724 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.91536 | 8.142 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99385 | 0.82194 | 17.191 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.82062 | 17.41 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99378 | 0.82235 | 17.143 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.80989 | 18.647 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99218 | 0.90146 | 9.072 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97711 | 0.76164 | 21.547 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97711 | 0.77239 | 20.472 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97711 | 0.77948 | 19.764 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97711 | 0.79111 | 18.6 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97711 | 0.80272 | 17.439 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97711 | 0.80465 | 17.246 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97711 | 0.81024 | 16.687 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97711 | 0.89059 | 8.653 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97711 | 0.89272 | 8.439 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9979 | 0.79604 | 20.186 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.81099 | 18.181 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.81156 | 18.176 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.82381 | 17.044 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99041 | 0.81459 | 17.583 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99041 | 0.90741 | 8.3 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.81352 | 17.919 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.79895 | 19.127 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99022 | 0.81186 | 17.837 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.78746 | 20.9 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98205 | 0.76111 | 22.094 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98205 | 0.77673 | 20.532 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98205 | 0.80025 | 18.18 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98205 | 0.81525 | 16.68 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99407 | 0.89202 | 10.205 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.76963 | 22.023 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99793 | 0.81359 | 18.434 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.81812 | 17.447 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98944 | 0.77824 | 21.12 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98944 | 0.77995 | 20.949 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99837 | 0.81074 | 18.763 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99837 | 0.91365 | 8.472 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98759 | 0.79822 | 18.937 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98759 | 0.80949 | 17.809 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.90253 | 9.396 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99218 | 0.90146 | 9.072 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99628 | 0.91408 | 8.221 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99626 | 0.91459 | 8.167 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99374 | 0.80773 | 18.601 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99374 | 0.90921 | 8.453 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99448 | 0.81345 | 18.103 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.82002 | 17.438 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99627 | 0.90737 | 8.89 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99562 | 0.91536 | 8.025 | Yes
Active | 2025W1-N11-WVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9942 | 0.8188 | 17.54 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98083 | 0.89745 | 8.338 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97785 | 0.88489 | 9.296 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97747 | 0.79682 | 18.065 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97781 | 0.79486 | 18.295 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97668 | 0.79646 | 18.022 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97894 | 0.78576 | 19.318 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9757 | 0.87732 | 9.838 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9555 | 0.72925 | 22.626 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9555 | 0.74791 | 20.759 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9555 | 0.76028 | 19.522 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9555 | 0.76354 | 19.196 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9555 | 0.77975 | 17.575 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98195 | 0.75612 | 22.583 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98099 | 0.89861 | 8.238 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97593 | 0.8939 | 8.203 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97603 | 0.78728 | 18.875 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97654 | 0.78774 | 18.88 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97954 | 0.89418 | 8.536 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.8978 | 8.223 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98011 | 0.89781 | 8.229 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97759 | 0.798 | 17.959 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97425 | 0.79103 | 18.322 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97425 | 0.88638 | 8.788 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97751 | 0.89172 | 8.58 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98058 | 0.89786 | 8.272 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9755 | 0.78907 | 18.643 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97272 | 0.77853 | 19.419 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97272 | 0.79129 | 18.143 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98225 | 0.75926 | 22.299 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96135 | 0.72892 | 23.243 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96135 | 0.75861 | 20.274 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96135 | 0.76166 | 19.969 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96135 | 0.79308 | 16.826 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97444 | 0.86206 | 11.237 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97682 | 0.74444 | 23.237 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98041 | 0.79033 | 19.008 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97633 | 0.79345 | 18.288 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97724 | 0.75947 | 21.777 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97724 | 0.76035 | 21.689 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98653 | 0.79111 | 19.542 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98653 | 0.89717 | 8.936 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97041 | 0.77533 | 19.508 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97041 | 0.78706 | 18.335 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98025 | 0.87608 | 10.417 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9765 | 0.89603 | 8.047 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9765 | 0.89603 | 8.047 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97992 | 0.89665 | 8.327 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9757 | 0.87732 | 9.838 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97922 | 0.88896 | 9.026 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97919 | 0.8895 | 8.969 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97647 | 0.78406 | 19.241 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97647 | 0.88624 | 9.023 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97764 | 0.78932 | 18.832 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9775 | 0.79436 | 18.313 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97939 | 0.88314 | 9.625 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97863 | 0.89089 | 8.775 | Yes
Active | 2025W1-N11-WVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97731 | 0.79326 | 18.405 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0058 | 0.91643 | 8.941 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0058 | 0.921 | 8.484 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0058 | 0.92334 | 8.25 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0055 | 0.91551 | 9.003 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.92035 | 8.518 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.92255 | 8.615 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0069 | 0.91894 | 8.793 | Yes
Active | 2025W1-N11-WVD243558 | 243558 | 05RIO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.919 | 8.786 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0065 | 0.9167 | 8.979 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0065 | 0.92119 | 8.53 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0065 | 0.92357 | 8.292 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0062 | 0.91573 | 9.046 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92055 | 8.564 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.92278 | 8.661 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0076 | 0.91916 | 8.84 | Yes
Active | 2025W1-N11-WVD243559 | 243559 | 05RIO Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.91928 | 8.828 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99432 | 0.91405 | 8.027 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98957 | 0.89819 | 9.138 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.8109 | 18.007 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.80664 | 18.449 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99 | 0.80959 | 18.041 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99383 | 0.79625 | 19.758 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.88923 | 9.71 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97599 | 0.74972 | 22.627 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97599 | 0.76403 | 21.196 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97599 | 0.7711 | 20.488 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97599 | 0.78137 | 19.462 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97599 | 0.79164 | 18.435 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97599 | 0.80277 | 17.322 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97599 | 0.88548 | 9.051 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97599 | 0.88993 | 8.606 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99513 | 0.77716 | 21.796 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98867 | 0.79619 | 19.247 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.79684 | 19.253 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.91079 | 8.225 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99108 | 0.81184 | 17.924 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98766 | 0.80465 | 18.302 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98766 | 0.90161 | 8.606 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.90861 | 8.267 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98874 | 0.80172 | 18.701 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9863 | 0.79015 | 19.615 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9863 | 0.80177 | 18.453 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.77482 | 21.98 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98121 | 0.74934 | 23.186 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98121 | 0.76794 | 21.326 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98121 | 0.78462 | 19.659 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98121 | 0.8036 | 17.761 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98809 | 0.87822 | 10.987 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98638 | 0.75837 | 22.801 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99447 | 0.80246 | 19.201 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98982 | 0.80743 | 18.239 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98723 | 0.76635 | 22.088 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98723 | 0.76871 | 21.852 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99727 | 0.80068 | 19.659 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99727 | 0.90849 | 8.878 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98317 | 0.78461 | 19.856 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98317 | 0.79493 | 18.825 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99365 | 0.89273 | 10.092 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.91337 | 8.008 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.88923 | 9.71 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99238 | 0.90463 | 8.774 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99233 | 0.90519 | 8.714 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.79362 | 19.668 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9903 | 0.9 | 9.03 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99087 | 0.79887 | 19.2 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99081 | 0.8063 | 18.451 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99273 | 0.89871 | 9.402 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99187 | 0.90707 | 8.48 | Yes
Active | 2025W1-N11-WVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.80487 | 18.568 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0052 | 0.91638 | 8.883 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.92107 | 8.414 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0052 | 0.92335 | 8.186 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.91554 | 8.938 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.92042 | 8.45 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.92257 | 8.546 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.91896 | 8.724 | Yes
Active | 2025W1-N11-WVD243561 | 243561 | 05RODNEY SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0062 | 0.91897 | 8.723 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99896 | 0.87546 | 12.349 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99862 | 0.87329 | 12.533 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99799 | 0.8721 | 12.589 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99852 | 0.86274 | 13.579 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98579 | 0.82865 | 15.714 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98579 | 0.82905 | 15.674 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98579 | 0.83231 | 15.349 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98579 | 0.83513 | 15.066 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98579 | 0.85107 | 13.472 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98579 | 0.85632 | 12.947 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98579 | 0.85727 | 12.853 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.85857 | 14.284 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99703 | 0.86502 | 13.201 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.8654 | 13.2 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99872 | 0.87528 | 12.344 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99642 | 0.86822 | 12.82 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.9031 | 10.161 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98795 | 0.82461 | 16.335 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98795 | 0.83222 | 15.573 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99881 | 0.84861 | 15.02 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98713 | 0.82702 | 16.011 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98713 | 0.8282 | 15.893 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98713 | 0.86136 | 12.577 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98713 | 0.86247 | 12.467 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99303 | 0.83361 | 15.942 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.86869 | 13.298 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99825 | 0.8731 | 12.516 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98961 | 0.83004 | 15.957 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98961 | 0.83455 | 15.507 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99833 | 0.85905 | 13.928 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99073 | 0.85341 | 13.732 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99073 | 0.85872 | 13.201 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99683 | 0.86136 | 13.547 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.86674 | 13.141 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99791 | 0.87126 | 12.665 | Yes
Active | 2025W1-N11-WVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99777 | 0.87103 | 12.674 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.90561 | 9.886 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.90514 | 9.933 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90193 | 10.152 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.89608 | 10.765 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99385 | 0.86673 | 12.712 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99385 | 0.8682 | 12.565 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99385 | 0.87201 | 12.183 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99385 | 0.87304 | 12.08 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99385 | 0.8863 | 10.754 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99385 | 0.88751 | 10.634 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99385 | 0.89145 | 10.239 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0064 | 0.89293 | 11.344 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.89849 | 10.458 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.89874 | 10.459 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.90539 | 9.88 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.89912 | 10.329 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0108 | 0.93065 | 8.015 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.86868 | 12.376 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99244 | 0.87361 | 11.883 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.88422 | 11.98 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99445 | 0.86267 | 13.178 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99445 | 0.86773 | 12.672 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99445 | 0.89524 | 9.921 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99445 | 0.89617 | 9.828 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99916 | 0.8719 | 12.726 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.89995 | 10.665 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.9038 | 10.013 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99524 | 0.86613 | 12.911 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99524 | 0.86949 | 12.575 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.88964 | 11.317 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99776 | 0.88908 | 10.868 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99776 | 0.89325 | 10.452 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.89513 | 10.739 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.89971 | 10.415 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.9029 | 10.066 | Yes
Active | 2025W1-N11-WVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.9029 | 10.058 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98504 | 0.90233 | 8.271 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98086 | 0.88727 | 9.359 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98169 | 0.79986 | 18.184 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98187 | 0.79669 | 18.518 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98073 | 0.79887 | 18.186 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9837 | 0.78717 | 19.653 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.88055 | 9.844 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96229 | 0.7356 | 22.669 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96229 | 0.75208 | 21.021 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96229 | 0.76123 | 20.106 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96229 | 0.76832 | 19.397 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96229 | 0.78146 | 18.083 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96229 | 0.87642 | 8.587 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98601 | 0.76298 | 22.303 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98521 | 0.90358 | 8.163 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98065 | 0.89947 | 8.117 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97979 | 0.78805 | 19.174 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98039 | 0.78859 | 19.181 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98369 | 0.89896 | 8.472 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98422 | 0.9027 | 8.152 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98429 | 0.90271 | 8.159 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98178 | 0.80073 | 18.105 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97832 | 0.79376 | 18.456 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97832 | 0.89026 | 8.806 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9819 | 0.89681 | 8.509 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98479 | 0.90283 | 8.196 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97955 | 0.79149 | 18.806 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97683 | 0.78061 | 19.622 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97683 | 0.79236 | 18.447 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98598 | 0.76333 | 22.265 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96775 | 0.73524 | 23.251 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96775 | 0.75861 | 20.914 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96775 | 0.76902 | 19.873 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96775 | 0.79365 | 17.409 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97853 | 0.86622 | 11.232 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97808 | 0.74796 | 23.012 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98499 | 0.792 | 19.299 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98055 | 0.7965 | 18.405 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97922 | 0.75867 | 22.055 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97922 | 0.7605 | 21.873 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9894 | 0.79185 | 19.755 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9894 | 0.89922 | 9.018 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97395 | 0.77619 | 19.776 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97395 | 0.78682 | 18.713 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98446 | 0.88071 | 10.376 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9841 | 0.90152 | 8.258 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.88055 | 9.844 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98307 | 0.89299 | 9.008 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98302 | 0.89354 | 8.948 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98072 | 0.78508 | 19.564 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98072 | 0.88944 | 9.128 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98168 | 0.79034 | 19.134 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98155 | 0.79627 | 18.528 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98348 | 0.88737 | 9.611 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98266 | 0.89547 | 8.719 | Yes
Active | 2025W1-N11-WVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98133 | 0.79503 | 18.629 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.85083 | 14.454 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99506 | 0.84703 | 14.803 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99444 | 0.84777 | 14.667 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.83562 | 16.044 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.981 | 0.79723 | 18.376 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.981 | 0.80514 | 17.585 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.981 | 0.80538 | 17.562 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.981 | 0.81224 | 16.875 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.981 | 0.82281 | 15.818 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.981 | 0.82793 | 15.307 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.981 | 0.83331 | 14.768 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99822 | 0.82939 | 16.883 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99319 | 0.83714 | 15.605 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99368 | 0.83767 | 15.601 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.85098 | 14.428 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.84382 | 14.895 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99755 | 0.86798 | 12.958 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98925 | 0.80697 | 18.228 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98925 | 0.81664 | 17.261 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.81986 | 17.612 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98339 | 0.79683 | 18.656 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98339 | 0.79967 | 18.372 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98339 | 0.83283 | 15.056 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98339 | 0.83576 | 14.763 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9957 | 0.90908 | 8.661 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98957 | 0.80333 | 18.625 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99834 | 0.84325 | 15.508 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99455 | 0.84798 | 14.657 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98685 | 0.80196 | 18.489 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98685 | 0.80668 | 18.018 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.83466 | 16.145 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98693 | 0.8244 | 16.252 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98693 | 0.83107 | 15.585 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.83364 | 16.007 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.8394 | 15.53 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.84556 | 14.896 | Yes
Active | 2025W1-N11-WVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.84486 | 14.947 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99722 | 0.8512 | 14.603 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.84729 | 14.965 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.84818 | 14.813 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99805 | 0.83586 | 16.219 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98281 | 0.79719 | 18.562 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98281 | 0.80547 | 17.734 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98281 | 0.80548 | 17.733 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98281 | 0.81364 | 16.918 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98281 | 0.82298 | 15.984 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98281 | 0.82811 | 15.47 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98281 | 0.83383 | 14.898 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.82939 | 17.071 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99504 | 0.83728 | 15.776 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99554 | 0.83782 | 15.773 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99713 | 0.85137 | 14.575 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.84421 | 15.041 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99907 | 0.8671 | 13.198 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99148 | 0.80832 | 18.316 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99148 | 0.81812 | 17.336 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99792 | 0.81998 | 17.795 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9853 | 0.79679 | 18.852 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9853 | 0.80004 | 18.527 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9853 | 0.83288 | 15.242 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9853 | 0.83609 | 14.922 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.90996 | 8.749 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99148 | 0.80338 | 18.81 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.84357 | 15.664 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.84831 | 14.809 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98885 | 0.80225 | 18.66 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98885 | 0.80694 | 18.191 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9981 | 0.83512 | 16.298 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98883 | 0.82453 | 16.431 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98883 | 0.83132 | 15.752 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.83382 | 16.182 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.83958 | 15.701 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99642 | 0.84587 | 15.054 | Yes
Active | 2025W1-N11-WVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99622 | 0.84513 | 15.109 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99825 | 0.8718 | 12.645 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99787 | 0.86937 | 12.851 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.86847 | 12.879 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99792 | 0.85866 | 13.926 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98482 | 0.824 | 16.082 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98482 | 0.82489 | 15.993 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98482 | 0.82822 | 15.66 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98482 | 0.83069 | 15.413 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98482 | 0.84688 | 13.794 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98482 | 0.852 | 13.282 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98482 | 0.85365 | 13.117 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.85432 | 14.645 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99624 | 0.86085 | 13.539 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99663 | 0.86125 | 13.538 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99803 | 0.87166 | 12.636 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99574 | 0.8647 | 13.104 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90044 | 10.347 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98861 | 0.82026 | 16.835 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98861 | 0.82841 | 16.02 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.84437 | 15.382 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98632 | 0.82288 | 16.344 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98632 | 0.82356 | 16.275 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98632 | 0.85717 | 12.914 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98632 | 0.85836 | 12.795 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.82911 | 16.319 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.86493 | 13.608 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99753 | 0.86936 | 12.816 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98892 | 0.8258 | 16.311 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.83038 | 15.854 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99776 | 0.85539 | 14.237 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98987 | 0.84902 | 14.084 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98987 | 0.8545 | 13.537 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.8572 | 13.893 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99742 | 0.86265 | 13.477 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.86741 | 12.978 | Yes
Active | 2025W1-N11-WVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99704 | 0.86712 | 12.992 | Yes
Active | 2025W1-N11-WVD243571 | 243571 | 05SEAMAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0047 | 0.92199 | 8.271 | Yes
Active | 2025W1-N11-WVD243571 | 243571 | 05SEAMAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0048 | 0.9197 | 8.514 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99456 | 0.91156 | 8.3 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9922 | 0.81756 | 17.464 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99268 | 0.81461 | 17.807 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.81714 | 17.457 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.80393 | 19.109 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98835 | 0.89513 | 9.322 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9753 | 0.75615 | 21.915 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9753 | 0.7677 | 20.759 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9753 | 0.77473 | 20.057 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9753 | 0.78652 | 18.878 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9753 | 0.79677 | 17.853 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9753 | 0.80131 | 17.399 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9753 | 0.80595 | 16.935 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9753 | 0.88703 | 8.827 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9753 | 0.89124 | 8.406 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99624 | 0.78885 | 20.739 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.80426 | 18.617 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99107 | 0.8049 | 18.617 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.81887 | 17.356 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.81127 | 17.771 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98898 | 0.90573 | 8.325 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99052 | 0.8069 | 18.361 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98912 | 0.79556 | 19.356 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98912 | 0.80811 | 18.101 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.78262 | 21.244 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98043 | 0.75571 | 22.472 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98043 | 0.77186 | 20.858 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98043 | 0.79342 | 18.701 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98043 | 0.80903 | 17.14 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99098 | 0.8862 | 10.477 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98775 | 0.76462 | 22.312 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.8085 | 18.753 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.8139 | 17.707 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98758 | 0.77289 | 21.469 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98758 | 0.77487 | 21.271 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99707 | 0.80632 | 19.075 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99707 | 0.91114 | 8.593 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98519 | 0.79228 | 19.291 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98519 | 0.803 | 18.219 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.89834 | 9.628 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98835 | 0.89513 | 9.322 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99414 | 0.9102 | 8.393 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.91073 | 8.337 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.80145 | 19.04 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99185 | 0.90525 | 8.66 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.8069 | 18.553 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.81415 | 17.82 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.90374 | 9.053 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99347 | 0.91188 | 8.159 | Yes
Active | 2025W1-N11-WVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.8128 | 17.932 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.9088 | 8.369 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98918 | 0.89766 | 9.153 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98853 | 0.80873 | 17.98 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.80677 | 18.196 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9878 | 0.80796 | 17.984 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.79869 | 19.045 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.8911 | 9.694 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96726 | 0.74413 | 22.313 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96726 | 0.75922 | 20.804 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96726 | 0.76741 | 19.985 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96726 | 0.7757 | 19.156 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96726 | 0.7915 | 17.575 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96726 | 0.87739 | 8.987 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96726 | 0.88023 | 8.702 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99305 | 0.77446 | 21.859 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.91105 | 8.131 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98797 | 0.90692 | 8.105 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98755 | 0.80126 | 18.629 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98798 | 0.80163 | 18.635 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.90547 | 8.501 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.90938 | 8.171 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99116 | 0.90935 | 8.181 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.80831 | 18.061 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98447 | 0.80087 | 18.361 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98447 | 0.89623 | 8.825 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98888 | 0.90391 | 8.497 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.992 | 0.91035 | 8.164 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98697 | 0.80102 | 18.594 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98384 | 0.79029 | 19.355 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98384 | 0.80296 | 18.088 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99254 | 0.77234 | 22.02 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97301 | 0.74387 | 22.914 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97301 | 0.76603 | 20.697 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97301 | 0.77873 | 19.428 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97301 | 0.80468 | 16.832 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98546 | 0.87384 | 11.162 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98483 | 0.7564 | 22.843 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.79916 | 19.354 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98747 | 0.80548 | 18.199 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98454 | 0.76742 | 21.712 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.76808 | 21.646 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99508 | 0.79951 | 19.557 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99508 | 0.90585 | 8.924 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98125 | 0.78742 | 19.383 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98125 | 0.79906 | 18.219 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99158 | 0.88611 | 10.547 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.991 | 0.90819 | 8.28 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.8911 | 9.694 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98725 | 0.89505 | 9.22 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98711 | 0.89562 | 9.148 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98721 | 0.79736 | 18.984 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98721 | 0.89861 | 8.859 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98885 | 0.80302 | 18.582 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98837 | 0.80612 | 18.225 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99017 | 0.89452 | 9.565 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98942 | 0.90234 | 8.709 | Yes
Active | 2025W1-N11-WVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9882 | 0.80511 | 18.309 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.9187 | 8.549 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.82333 | 17.994 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.81951 | 18.402 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.82232 | 18.01 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.80868 | 19.737 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.89343 | 9.804 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99107 | 0.76015 | 23.091 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99107 | 0.77366 | 21.74 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99107 | 0.78113 | 20.993 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99107 | 0.79174 | 19.932 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99107 | 0.80225 | 18.882 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99107 | 0.80786 | 18.321 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99107 | 0.81298 | 17.808 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.99107 | 0.89786 | 9.321 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99107 | 0.90263 | 8.844 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0075 | 0.7905 | 21.704 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.80888 | 19.222 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.80953 | 19.225 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.82449 | 17.891 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99992 | 0.81691 | 18.301 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99992 | 0.9168 | 8.311 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.81379 | 18.741 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99881 | 0.80122 | 19.759 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99881 | 0.81363 | 18.518 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.78686 | 21.993 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.75976 | 23.673 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99649 | 0.77822 | 21.827 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99649 | 0.79624 | 20.025 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99649 | 0.81478 | 18.171 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.89395 | 10.705 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99903 | 0.76962 | 22.941 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.81409 | 19.29 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.81966 | 18.239 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.77832 | 22.357 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.7804 | 22.149 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.81256 | 19.68 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0094 | 0.92351 | 8.585 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.998 | 0.79682 | 20.119 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.998 | 0.80762 | 19.038 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.90802 | 9.796 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.89343 | 9.804 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.92037 | 8.457 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.92093 | 8.396 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.80609 | 19.653 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.91553 | 8.709 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.81159 | 19.167 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.81909 | 18.41 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.91401 | 9.118 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.92262 | 8.173 | Yes
Active | 2025W1-N11-WVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.81766 | 18.527 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99962 | 0.91222 | 8.74 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99859 | 0.81776 | 18.083 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.81403 | 18.483 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99771 | 0.81677 | 18.094 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.80333 | 19.795 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.89152 | 9.799 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98511 | 0.75536 | 22.975 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98511 | 0.76915 | 21.596 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98511 | 0.77693 | 20.818 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98511 | 0.78688 | 19.823 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98511 | 0.79735 | 18.776 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98511 | 0.80261 | 18.25 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98511 | 0.80842 | 17.67 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98511 | 0.89214 | 9.298 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98511 | 0.89704 | 8.807 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.78441 | 21.854 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99644 | 0.80359 | 19.285 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.80423 | 19.289 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.92027 | 8.057 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99872 | 0.81892 | 17.98 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99522 | 0.81139 | 18.383 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99522 | 0.91084 | 8.438 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99909 | 0.91812 | 8.097 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.80819 | 18.812 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99366 | 0.79572 | 19.794 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99366 | 0.80803 | 18.563 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.78167 | 22.075 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99056 | 0.75498 | 23.558 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99056 | 0.77419 | 21.636 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99056 | 0.79051 | 20.005 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99056 | 0.80987 | 18.069 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.88767 | 10.845 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99465 | 0.7648 | 22.985 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.80849 | 19.374 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99737 | 0.81413 | 18.325 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.77397 | 22.302 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99699 | 0.77589 | 22.11 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.80768 | 19.747 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0051 | 0.91821 | 8.694 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99248 | 0.79164 | 20.084 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99248 | 0.80243 | 19.005 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.90209 | 9.937 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.89152 | 9.799 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.91429 | 8.597 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.91485 | 8.536 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99789 | 0.8008 | 19.709 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99789 | 0.9096 | 8.829 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99857 | 0.80625 | 19.232 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99852 | 0.81361 | 18.491 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.90801 | 9.249 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9997 | 0.91658 | 8.312 | Yes
Active | 2025W1-N11-WVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99827 | 0.8122 | 18.606 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99808 | 0.9156 | 8.249 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.90371 | 9.152 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.80971 | 18.477 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.8072 | 18.773 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99381 | 0.80941 | 18.44 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.79717 | 19.963 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98905 | 0.88914 | 9.991 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97658 | 0.74512 | 23.147 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97658 | 0.76004 | 21.655 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97658 | 0.76999 | 20.659 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97658 | 0.77771 | 19.887 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97658 | 0.79109 | 18.549 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97658 | 0.8012 | 17.538 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97658 | 0.88278 | 9.38 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97658 | 0.8884 | 8.818 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99896 | 0.77447 | 22.449 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.91721 | 8.101 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.91092 | 8.117 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99282 | 0.79801 | 19.481 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.79857 | 19.485 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.91238 | 8.441 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99733 | 0.91622 | 8.111 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.91622 | 8.118 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99463 | 0.81114 | 18.349 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99118 | 0.80366 | 18.752 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99118 | 0.90365 | 8.753 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99496 | 0.91016 | 8.48 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99784 | 0.91648 | 8.136 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99255 | 0.80117 | 19.138 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.78973 | 20.028 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99001 | 0.80271 | 18.731 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99857 | 0.77307 | 22.551 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98249 | 0.74473 | 23.776 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98249 | 0.76805 | 21.444 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98249 | 0.7801 | 20.24 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98249 | 0.80441 | 17.809 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.87994 | 11.218 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99141 | 0.75623 | 23.518 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99817 | 0.79982 | 19.835 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99323 | 0.80604 | 18.719 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99284 | 0.76846 | 22.439 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99284 | 0.76955 | 22.329 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.80113 | 20.072 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.91214 | 8.971 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.78606 | 20.198 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98804 | 0.79769 | 19.035 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99735 | 0.89368 | 10.367 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99722 | 0.91502 | 8.219 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98905 | 0.88914 | 9.991 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99634 | 0.90678 | 8.956 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.90734 | 8.896 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.79503 | 19.879 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99382 | 0.90326 | 9.056 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.8004 | 19.432 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99461 | 0.80674 | 18.787 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99656 | 0.90056 | 9.6 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99576 | 0.90887 | 8.689 | Yes
Active | 2025W1-N11-WVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.80546 | 18.893 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87754 | 12.852 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87596 | 13.067 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.87544 | 13.042 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.86671 | 14.008 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99302 | 0.82707 | 16.595 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99302 | 0.83506 | 15.796 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99302 | 0.83734 | 15.568 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99302 | 0.85134 | 14.169 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99302 | 0.85234 | 14.069 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99302 | 0.86081 | 13.221 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99302 | 0.86231 | 13.071 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0089 | 0.85988 | 14.898 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86883 | 13.652 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.8692 | 13.646 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.87706 | 12.893 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.86678 | 13.558 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88105 | 12.633 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.84805 | 14.978 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99783 | 0.85565 | 14.218 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.84865 | 15.757 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.82646 | 16.819 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99466 | 0.83237 | 16.229 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99466 | 0.86279 | 13.187 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99466 | 0.86821 | 12.645 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.83333 | 16.809 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0092 | 0.87016 | 13.909 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87505 | 13.024 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.83517 | 16.534 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.83906 | 16.145 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.86352 | 14.395 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.85751 | 14.312 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.86424 | 13.639 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.86544 | 13.989 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.87052 | 13.583 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.87484 | 13.138 | Yes
Active | 2025W1-N11-WVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87421 | 13.189 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99895 | 0.91525 | 8.37 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99741 | 0.82018 | 17.722 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99772 | 0.81566 | 18.207 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.8189 | 17.779 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.80457 | 19.627 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99085 | 0.89555 | 9.53 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98218 | 0.75839 | 22.379 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98218 | 0.77034 | 21.184 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98218 | 0.77603 | 20.615 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98218 | 0.78877 | 19.341 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98218 | 0.7974 | 18.478 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98218 | 0.80364 | 17.854 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98218 | 0.8079 | 17.428 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98218 | 0.8923 | 8.988 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98218 | 0.89663 | 8.555 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.78987 | 21.154 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.80416 | 19.101 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9959 | 0.80487 | 19.103 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.82125 | 17.635 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.81373 | 18.045 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99419 | 0.91042 | 8.377 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99555 | 0.81052 | 18.502 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99362 | 0.79742 | 19.62 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99362 | 0.80934 | 18.428 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.78443 | 21.583 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98715 | 0.75801 | 22.914 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98715 | 0.77253 | 21.462 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98715 | 0.79496 | 19.219 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98715 | 0.80924 | 17.79 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.88888 | 10.647 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.76681 | 22.55 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.81132 | 18.979 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99624 | 0.8166 | 17.964 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99259 | 0.773 | 21.959 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99259 | 0.77571 | 21.689 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.80786 | 19.429 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.91518 | 8.698 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.79242 | 19.788 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9903 | 0.80257 | 18.773 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.9025 | 9.734 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99085 | 0.89555 | 9.53 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99891 | 0.91393 | 8.498 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.91448 | 8.438 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.80166 | 19.546 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99712 | 0.90874 | 8.839 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99746 | 0.80706 | 19.04 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.81529 | 18.211 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99928 | 0.90783 | 9.145 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99838 | 0.91632 | 8.206 | Yes
Active | 2025W1-N11-WVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.81378 | 18.334 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99993 | 0.91759 | 8.234 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.90831 | 8.959 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99617 | 0.81275 | 18.342 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.81131 | 18.549 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.81322 | 18.251 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.80122 | 19.724 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99278 | 0.8947 | 9.808 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97735 | 0.74894 | 22.84 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97735 | 0.76212 | 21.523 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97735 | 0.7721 | 20.525 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97735 | 0.78097 | 19.638 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97735 | 0.79481 | 18.254 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97735 | 0.79874 | 17.861 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97735 | 0.80339 | 17.395 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97735 | 0.88458 | 9.277 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97735 | 0.8898 | 8.755 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.78124 | 21.925 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99994 | 0.91962 | 8.032 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.91241 | 8.095 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99482 | 0.80227 | 19.255 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.80282 | 19.256 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99866 | 0.9147 | 8.397 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9992 | 0.91854 | 8.067 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99926 | 0.91851 | 8.074 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99627 | 0.81456 | 18.17 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.80685 | 18.606 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99291 | 0.90578 | 8.713 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.91278 | 8.42 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99959 | 0.91893 | 8.066 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99448 | 0.80426 | 19.023 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.79299 | 19.931 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99231 | 0.80653 | 18.577 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99975 | 0.77683 | 22.292 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98327 | 0.74841 | 23.486 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98327 | 0.77043 | 21.284 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98327 | 0.78609 | 19.718 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98327 | 0.8084 | 17.487 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.88425 | 11.047 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99278 | 0.75882 | 23.396 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.80277 | 19.733 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.80886 | 18.595 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99343 | 0.77147 | 22.196 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.77212 | 22.131 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.80366 | 19.897 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.91352 | 8.911 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98978 | 0.79019 | 19.958 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98978 | 0.80228 | 18.75 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99895 | 0.89624 | 10.271 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9991 | 0.91736 | 8.174 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99278 | 0.8947 | 9.808 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99827 | 0.90965 | 8.862 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99824 | 0.9102 | 8.804 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99571 | 0.79917 | 19.653 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99571 | 0.90632 | 8.938 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99658 | 0.80462 | 19.196 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.81081 | 18.568 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.90325 | 9.515 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99765 | 0.91141 | 8.624 | Yes
Active | 2025W1-N11-WVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99628 | 0.80957 | 18.671 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.89755 | 8.957 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98778 | 0.80871 | 17.907 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98789 | 0.80392 | 18.398 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98678 | 0.80717 | 17.961 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99095 | 0.79336 | 19.759 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98351 | 0.88706 | 9.645 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97228 | 0.74804 | 22.423 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97228 | 0.7616 | 21.068 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97228 | 0.76769 | 20.459 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97228 | 0.779 | 19.328 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97228 | 0.78795 | 18.432 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97228 | 0.79926 | 17.301 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97228 | 0.88231 | 8.996 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97228 | 0.88666 | 8.562 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99186 | 0.77624 | 21.562 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9853 | 0.79294 | 19.236 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98604 | 0.79362 | 19.242 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98985 | 0.90808 | 8.177 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98789 | 0.8096 | 17.829 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98452 | 0.80245 | 18.207 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98452 | 0.89872 | 8.58 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98806 | 0.90583 | 8.223 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98547 | 0.79937 | 18.61 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98326 | 0.78771 | 19.555 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98326 | 0.79905 | 18.421 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.77308 | 21.809 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9773 | 0.74767 | 22.963 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9773 | 0.76426 | 21.304 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9773 | 0.783 | 19.43 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9773 | 0.79956 | 17.775 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98495 | 0.87554 | 10.941 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98291 | 0.75655 | 22.636 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9913 | 0.80037 | 19.092 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98664 | 0.80527 | 18.137 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98315 | 0.7632 | 21.994 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98315 | 0.76585 | 21.73 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.79773 | 19.579 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99352 | 0.90475 | 8.877 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97954 | 0.78151 | 19.803 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97954 | 0.79152 | 18.802 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99039 | 0.89013 | 10.026 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98351 | 0.88706 | 9.645 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98905 | 0.90151 | 8.754 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98899 | 0.90206 | 8.693 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98719 | 0.79053 | 19.666 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98719 | 0.8967 | 9.05 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98763 | 0.79573 | 19.189 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98758 | 0.80362 | 18.396 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98949 | 0.89579 | 9.37 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9886 | 0.90422 | 8.438 | Yes
Active | 2025W1-N11-WVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9873 | 0.80212 | 18.517 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.91153 | 8.356 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9918 | 0.90059 | 9.121 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.81172 | 17.939 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.80979 | 18.155 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99041 | 0.81095 | 17.946 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99178 | 0.8017 | 19.008 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.89402 | 9.665 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97 | 0.747 | 22.3 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97 | 0.76198 | 20.802 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97 | 0.7702 | 19.98 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97 | 0.7786 | 19.14 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97 | 0.79454 | 17.546 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97 | 0.80132 | 16.868 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97 | 0.88023 | 8.976 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97 | 0.88287 | 8.713 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99558 | 0.77772 | 21.785 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.91388 | 8.103 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.90975 | 8.082 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99017 | 0.80424 | 18.593 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9906 | 0.80462 | 18.598 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.90828 | 8.48 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.91221 | 8.149 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.91217 | 8.16 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99157 | 0.81119 | 18.038 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98698 | 0.80366 | 18.333 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98698 | 0.89891 | 8.807 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99151 | 0.90679 | 8.472 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99455 | 0.91319 | 8.137 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.804 | 18.56 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98652 | 0.79325 | 19.327 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98652 | 0.80602 | 18.05 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99506 | 0.77522 | 21.983 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97575 | 0.74671 | 22.903 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97575 | 0.76887 | 20.688 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97575 | 0.78199 | 19.376 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97575 | 0.80779 | 16.796 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98817 | 0.87693 | 11.124 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98743 | 0.75916 | 22.828 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99525 | 0.80207 | 19.318 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99006 | 0.80847 | 18.159 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98712 | 0.77028 | 21.684 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.77086 | 21.626 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.80234 | 19.518 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99752 | 0.90862 | 8.89 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98396 | 0.79044 | 19.352 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98396 | 0.80217 | 18.179 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.88883 | 10.538 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.91102 | 8.258 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.89402 | 9.665 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.89811 | 9.183 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9898 | 0.89868 | 9.112 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98985 | 0.80037 | 18.949 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98985 | 0.90158 | 8.827 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.80602 | 18.545 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.991 | 0.80915 | 18.185 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.89742 | 9.535 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99203 | 0.9052 | 8.683 | Yes
Active | 2025W1-N11-WVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.80813 | 18.269 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.91494 | 8.702 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.8199 | 18.134 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.81582 | 18.565 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.81875 | 18.16 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.80497 | 19.919 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99164 | 0.89327 | 9.837 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98779 | 0.7573 | 23.049 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98779 | 0.77064 | 21.715 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98779 | 0.77765 | 21.013 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98779 | 0.78861 | 19.917 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98779 | 0.79862 | 18.916 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98779 | 0.80453 | 18.326 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98779 | 0.80945 | 17.834 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98779 | 0.89471 | 9.308 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98779 | 0.89938 | 8.841 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.78738 | 21.809 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99898 | 0.805 | 19.397 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99968 | 0.80567 | 19.401 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.92291 | 8.058 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.82099 | 18.037 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99788 | 0.81347 | 18.44 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99788 | 0.91324 | 8.463 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.92067 | 8.101 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99912 | 0.81034 | 18.878 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.79777 | 19.898 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99676 | 0.80996 | 18.679 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.78363 | 22.106 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.75693 | 23.621 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99314 | 0.7746 | 21.854 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99314 | 0.79322 | 19.992 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99314 | 0.81095 | 18.219 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99887 | 0.89029 | 10.858 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.76649 | 23.027 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.81084 | 19.41 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.81627 | 18.375 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99876 | 0.77451 | 22.424 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99876 | 0.77677 | 22.199 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.80889 | 19.828 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0072 | 0.91968 | 8.748 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.79306 | 20.199 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99505 | 0.80363 | 19.141 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90454 | 9.938 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99164 | 0.89327 | 9.837 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.91674 | 8.609 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.9173 | 8.548 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.80231 | 19.831 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.91178 | 8.883 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.80776 | 19.344 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.81542 | 18.571 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.91044 | 9.268 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.91908 | 8.318 | Yes
Active | 2025W1-N11-WVD243584 | 243584 | 05VINE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.81398 | 18.689 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0181 | 0.93635 | 8.174 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0108 | 0.90869 | 10.209 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0108 | 0.91399 | 9.679 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0108 | 0.91765 | 9.313 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0108 | 0.92534 | 8.543 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0108 | 0.92814 | 8.264 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0108 | 0.93023 | 8.055 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.02 | 0.93336 | 8.667 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0171 | 0.93689 | 8.025 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0119 | 0.9277 | 8.422 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0119 | 0.93118 | 8.075 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0182 | 0.92628 | 9.188 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0109 | 0.90625 | 10.468 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0109 | 0.9135 | 9.743 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0144 | 0.91674 | 9.767 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0202 | 0.93793 | 8.226 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0105 | 0.90998 | 10.048 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0105 | 0.91177 | 9.869 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0165 | 0.92766 | 8.884 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.014 | 0.93166 | 8.237 | Yes
Active | 2025W1-N11-WVD243585 | 243585 | 05WAVERL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0173 | 0.93572 | 8.155 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99023 | 0.82306 | 16.717 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99019 | 0.81663 | 17.357 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98917 | 0.82067 | 16.85 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99412 | 0.80511 | 18.901 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98716 | 0.89812 | 8.904 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97425 | 0.76389 | 21.036 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97425 | 0.77503 | 19.922 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97425 | 0.77837 | 19.588 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97425 | 0.79287 | 18.138 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97425 | 0.79698 | 17.726 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97425 | 0.80604 | 16.82 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97425 | 0.80981 | 16.443 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97425 | 0.89052 | 8.373 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9939 | 0.79481 | 19.909 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.8037 | 18.361 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98813 | 0.80452 | 18.361 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99037 | 0.82379 | 16.658 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98722 | 0.81681 | 17.041 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98722 | 0.90706 | 8.016 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98793 | 0.81237 | 17.556 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98649 | 0.80015 | 18.634 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98649 | 0.81116 | 17.533 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99266 | 0.78884 | 20.382 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97852 | 0.7635 | 21.502 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97852 | 0.77433 | 20.419 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97852 | 0.7995 | 17.902 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97852 | 0.80793 | 17.059 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98796 | 0.88647 | 10.149 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98492 | 0.7718 | 21.313 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99368 | 0.8149 | 17.878 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98916 | 0.81971 | 16.945 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9834 | 0.775 | 20.839 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9834 | 0.77826 | 20.514 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99395 | 0.81005 | 18.39 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99395 | 0.91033 | 8.362 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98104 | 0.79228 | 18.876 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98104 | 0.80167 | 17.937 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.90027 | 9.223 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98716 | 0.89812 | 8.904 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.90965 | 8.158 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.91017 | 8.099 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9899 | 0.80164 | 18.826 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9899 | 0.9038 | 8.61 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98988 | 0.80696 | 18.293 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.81643 | 17.346 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.90428 | 8.748 | Yes
Active | 2025W1-N11-WVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98958 | 0.81476 | 17.481 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99261 | 0.90443 | 8.817 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99263 | 0.81368 | 17.895 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99281 | 0.80905 | 18.376 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.81227 | 17.943 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99582 | 0.79834 | 19.748 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98727 | 0.8909 | 9.636 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97763 | 0.75246 | 22.516 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97763 | 0.76583 | 21.18 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97763 | 0.77208 | 20.554 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97763 | 0.78351 | 19.412 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97763 | 0.79265 | 18.498 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97763 | 0.79959 | 17.803 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97763 | 0.80386 | 17.377 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97763 | 0.88737 | 9.026 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97763 | 0.89181 | 8.582 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99673 | 0.78124 | 21.549 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99023 | 0.79796 | 19.227 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.79865 | 19.232 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.91365 | 8.11 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.81464 | 17.811 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.80737 | 18.2 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98937 | 0.90425 | 8.512 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99296 | 0.91141 | 8.155 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99035 | 0.8042 | 18.614 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98813 | 0.79225 | 19.588 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98813 | 0.80384 | 18.429 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99601 | 0.77783 | 21.818 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98269 | 0.75209 | 23.06 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98269 | 0.76872 | 21.397 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98269 | 0.78776 | 19.493 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98269 | 0.80448 | 17.821 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.88125 | 10.867 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98784 | 0.76101 | 22.683 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.80511 | 19.107 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99148 | 0.81019 | 18.13 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9884 | 0.76792 | 22.048 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9884 | 0.77049 | 21.791 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99834 | 0.80257 | 19.576 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99834 | 0.91025 | 8.808 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9849 | 0.78643 | 19.847 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9849 | 0.79658 | 18.831 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.89572 | 9.954 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98727 | 0.8909 | 9.636 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.90715 | 8.682 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99391 | 0.9077 | 8.621 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.79551 | 19.659 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9921 | 0.90238 | 8.972 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99254 | 0.80078 | 19.176 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99248 | 0.80873 | 18.376 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.90137 | 9.303 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99351 | 0.90981 | 8.369 | Yes
Active | 2025W1-N11-WVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.80723 | 18.498 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98758 | 0.90357 | 8.401 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98468 | 0.89118 | 9.349 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98413 | 0.80108 | 18.305 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.79917 | 18.537 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98341 | 0.80086 | 18.255 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98578 | 0.7899 | 19.589 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98194 | 0.88251 | 9.943 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96258 | 0.73403 | 22.855 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96258 | 0.75186 | 21.072 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96258 | 0.76391 | 19.867 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96258 | 0.76803 | 19.455 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96258 | 0.78385 | 17.873 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96258 | 0.87675 | 8.583 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98867 | 0.76154 | 22.712 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98775 | 0.90486 | 8.289 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9821 | 0.89939 | 8.271 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.79133 | 19.138 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98323 | 0.7918 | 19.143 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98629 | 0.9003 | 8.599 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9868 | 0.904 | 8.28 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98687 | 0.90401 | 8.286 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98427 | 0.80238 | 18.189 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98088 | 0.79526 | 18.562 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98088 | 0.89235 | 8.854 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98431 | 0.8979 | 8.641 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98734 | 0.90411 | 8.323 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98219 | 0.79324 | 18.895 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97945 | 0.78254 | 19.691 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97945 | 0.79554 | 18.391 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98883 | 0.76372 | 22.511 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96856 | 0.73368 | 23.488 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96856 | 0.76234 | 20.621 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96856 | 0.76706 | 20.15 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96856 | 0.79738 | 17.117 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98128 | 0.86797 | 11.331 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98298 | 0.74836 | 23.462 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98727 | 0.79303 | 19.425 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98294 | 0.79761 | 18.533 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98359 | 0.76317 | 22.042 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98359 | 0.76392 | 21.967 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99293 | 0.7949 | 19.804 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99293 | 0.9028 | 9.013 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97717 | 0.77935 | 19.782 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97717 | 0.79126 | 18.59 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98698 | 0.8819 | 10.508 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98291 | 0.90188 | 8.102 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98291 | 0.90188 | 8.102 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98668 | 0.90283 | 8.385 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98194 | 0.88251 | 9.943 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98596 | 0.89502 | 9.094 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98593 | 0.89557 | 9.036 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98323 | 0.78813 | 19.51 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98323 | 0.89228 | 9.095 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98436 | 0.79342 | 19.094 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98423 | 0.79867 | 18.555 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98614 | 0.88908 | 9.706 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98537 | 0.89698 | 8.839 | Yes
Active | 2025W1-N11-WVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98403 | 0.79754 | 18.649 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99329 | 0.90955 | 8.374 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99044 | 0.8974 | 9.304 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.80501 | 18.473 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99019 | 0.8029 | 18.73 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98906 | 0.80481 | 18.425 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.79326 | 19.843 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98629 | 0.88627 | 10.003 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96969 | 0.7392 | 23.049 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96969 | 0.75563 | 21.406 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96969 | 0.76675 | 20.294 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96969 | 0.77252 | 19.717 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96969 | 0.78721 | 18.248 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96969 | 0.87678 | 9.291 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96969 | 0.88241 | 8.728 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99429 | 0.76757 | 22.672 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99346 | 0.91102 | 8.244 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98738 | 0.90493 | 8.246 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98823 | 0.79446 | 19.377 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98879 | 0.79496 | 19.382 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.992 | 0.9063 | 8.57 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.91008 | 8.244 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99259 | 0.91008 | 8.251 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.80642 | 18.348 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98646 | 0.7991 | 18.737 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98646 | 0.89799 | 8.848 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.904 | 8.61 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.91028 | 8.278 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98781 | 0.79686 | 19.095 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98514 | 0.78583 | 19.931 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98514 | 0.7989 | 18.625 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.76807 | 22.614 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97569 | 0.73884 | 23.686 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97569 | 0.76511 | 21.059 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97569 | 0.77312 | 20.258 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97569 | 0.80072 | 17.498 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98715 | 0.87384 | 11.332 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98775 | 0.75201 | 23.573 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.79563 | 19.754 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98852 | 0.80142 | 18.709 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9887 | 0.76576 | 22.294 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9887 | 0.76657 | 22.212 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99795 | 0.79779 | 20.016 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99795 | 0.90762 | 9.032 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98296 | 0.78247 | 20.049 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98296 | 0.79434 | 18.863 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99264 | 0.88767 | 10.497 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98839 | 0.90776 | 8.062 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98839 | 0.90776 | 8.062 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99241 | 0.90889 | 8.352 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98629 | 0.88627 | 10.003 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99163 | 0.90088 | 9.074 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.90144 | 9.015 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98896 | 0.79134 | 19.762 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98896 | 0.89782 | 9.113 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98999 | 0.79667 | 19.332 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98987 | 0.80241 | 18.746 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99181 | 0.89477 | 9.704 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.9029 | 8.814 | Yes
Active | 2025W1-N11-WVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.80121 | 18.846 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.91405 | 8.64 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.81853 | 18.018 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.81568 | 18.349 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9981 | 0.81814 | 17.996 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.80507 | 19.63 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99202 | 0.89507 | 9.695 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98297 | 0.75561 | 22.737 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98297 | 0.76852 | 21.445 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98297 | 0.77667 | 20.63 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98297 | 0.78699 | 19.598 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98297 | 0.7984 | 18.458 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98297 | 0.80305 | 17.992 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98297 | 0.80818 | 17.48 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98297 | 0.891 | 9.198 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98297 | 0.89581 | 8.717 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.78702 | 21.597 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.80558 | 19.134 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99755 | 0.80619 | 19.136 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.92007 | 8.103 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.81994 | 17.892 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99541 | 0.81228 | 18.312 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99541 | 0.91066 | 8.474 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99939 | 0.91803 | 8.135 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9967 | 0.80876 | 18.795 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.79694 | 19.773 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99467 | 0.80975 | 18.492 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.78263 | 21.954 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.75518 | 23.33 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98848 | 0.77415 | 21.432 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98848 | 0.79216 | 19.631 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98848 | 0.81122 | 17.726 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99696 | 0.88903 | 10.792 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99479 | 0.765 | 22.979 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.80905 | 19.348 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.81479 | 18.265 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99606 | 0.77481 | 22.125 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.77644 | 21.962 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.80822 | 19.649 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.91746 | 8.725 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9925 | 0.7935 | 19.9 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9925 | 0.80468 | 18.782 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.90212 | 9.931 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99202 | 0.89507 | 9.695 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91462 | 8.6 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91517 | 8.541 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99821 | 0.80267 | 19.554 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99821 | 0.91016 | 8.806 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99892 | 0.80816 | 19.075 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.81522 | 18.362 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.90818 | 9.261 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99999 | 0.91656 | 8.344 | Yes
Active | 2025W1-N11-WVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9986 | 0.81387 | 18.474 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99386 | 0.82831 | 16.555 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99385 | 0.82237 | 17.148 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99287 | 0.82581 | 16.706 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99723 | 0.81087 | 18.636 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99066 | 0.90245 | 8.821 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97842 | 0.76958 | 20.884 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97842 | 0.78037 | 19.805 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97842 | 0.78324 | 19.518 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97842 | 0.79813 | 18.029 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97842 | 0.80284 | 17.558 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97842 | 0.80722 | 17.12 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97842 | 0.81431 | 16.411 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97842 | 0.89526 | 8.316 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99743 | 0.8007 | 19.673 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.81009 | 18.108 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.81085 | 18.108 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99395 | 0.82896 | 16.499 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99088 | 0.82179 | 16.909 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99233 | 0.82252 | 16.981 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.80128 | 18.764 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98892 | 0.81207 | 17.685 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.79416 | 20.19 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98237 | 0.76918 | 21.319 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98237 | 0.77886 | 20.351 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98237 | 0.80535 | 17.702 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98237 | 0.81329 | 16.908 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99192 | 0.89177 | 10.015 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.77724 | 21.124 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99723 | 0.82016 | 17.707 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99284 | 0.82501 | 16.782 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.987 | 0.77971 | 20.729 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.987 | 0.78331 | 20.369 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99723 | 0.81461 | 18.262 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99723 | 0.91379 | 8.345 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98509 | 0.79818 | 18.691 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98509 | 0.80715 | 17.794 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.90499 | 9.119 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99066 | 0.90245 | 8.821 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99487 | 0.91413 | 8.074 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.91465 | 8.015 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.80769 | 18.565 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99335 | 0.90813 | 8.522 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.81315 | 18.039 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.82194 | 17.156 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.90861 | 8.669 | Yes
Active | 2025W1-N11-WVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99321 | 0.82044 | 17.277 | Yes
Active | 2025W1-N11-WVD243614 | 243614 | 05BAER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99515 | 0.87971 | 11.543 | Yes
Active | 2025W1-N11-WVD243614 | 243614 | 05BAER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99338 | 0.91241 | 8.097 | Yes
Active | 2025W1-N11-WVD243614 | 243614 | 05BAER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97478 | 0.89264 | 8.214 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99416 | 0.90216 | 9.199 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9938 | 0.90111 | 9.268 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.90017 | 9.303 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.90097 | 9.304 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98514 | 0.85415 | 13.099 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98514 | 0.86049 | 12.465 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98514 | 0.87743 | 10.771 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98514 | 0.88251 | 10.263 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98514 | 0.89491 | 9.023 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98514 | 0.89711 | 8.803 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98514 | 0.89927 | 8.587 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99545 | 0.87953 | 11.592 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.90398 | 9.068 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.90396 | 9.081 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.90033 | 9.344 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.89609 | 9.549 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99287 | 0.89783 | 9.504 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.89223 | 9.9 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99123 | 0.89231 | 9.892 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.87588 | 11.892 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98512 | 0.84263 | 14.249 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98512 | 0.85972 | 12.54 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98512 | 0.88613 | 9.899 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98512 | 0.89683 | 8.828 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99015 | 0.88981 | 10.034 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99567 | 0.90228 | 9.339 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99375 | 0.90063 | 9.313 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97199 | 0.84695 | 12.504 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97199 | 0.85736 | 11.463 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98982 | 0.87969 | 11.012 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9902 | 0.89088 | 9.932 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.8913 | 9.89 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.90062 | 9.27 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.90427 | 9.063 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.90041 | 9.312 | Yes
Active | 2025W1-N11-WVD243765 | 243765 | 05FORD LIMA1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99344 | 0.90004 | 9.341 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0054 | 0.91597 | 8.943 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0054 | 0.9183 | 8.711 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0054 | 0.92081 | 8.46 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.92966 | 8.093 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.91465 | 9.02 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.91763 | 8.723 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.92003 | 8.854 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0079 | 0.91779 | 9.013 | Yes
Active | 2025W1-N11-WVD243797 | 243797 | 05RUTLAND Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.91818 | 8.973 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.91778 | 8.289 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99877 | 0.82237 | 17.64 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99901 | 0.81743 | 18.158 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99797 | 0.82087 | 17.711 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.80622 | 19.609 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.89809 | 9.47 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98339 | 0.76087 | 22.251 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98339 | 0.77271 | 21.067 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98339 | 0.77794 | 20.545 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98339 | 0.79107 | 19.232 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98339 | 0.79886 | 18.453 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98339 | 0.80571 | 17.768 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98339 | 0.80985 | 17.354 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98339 | 0.89412 | 8.926 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98339 | 0.8984 | 8.499 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.79224 | 21.05 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.8056 | 19.078 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99713 | 0.80634 | 19.079 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99895 | 0.82338 | 17.557 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.81593 | 17.965 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99558 | 0.91201 | 8.357 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.81259 | 18.42 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99493 | 0.7995 | 19.543 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99493 | 0.81126 | 18.366 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.78674 | 21.483 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98823 | 0.76049 | 22.774 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98823 | 0.7743 | 21.393 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98823 | 0.7973 | 19.093 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98823 | 0.81057 | 17.766 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99663 | 0.89043 | 10.62 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.7692 | 22.44 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.8136 | 18.884 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99762 | 0.81881 | 17.881 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99356 | 0.77478 | 21.878 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99356 | 0.77762 | 21.594 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.80983 | 19.353 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0034 | 0.91651 | 8.686 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.79389 | 19.733 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99122 | 0.80391 | 18.731 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.90422 | 9.697 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.89809 | 9.47 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.91524 | 8.491 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91579 | 8.43 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.80318 | 19.528 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99846 | 0.90999 | 8.847 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99874 | 0.80859 | 19.015 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99868 | 0.8171 | 18.159 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.90935 | 9.123 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99967 | 0.91785 | 8.182 | Yes
Active | 2025W1-N11-WVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.81555 | 18.285 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98657 | 0.9024 | 8.417 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98439 | 0.89198 | 9.241 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98307 | 0.80009 | 18.298 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98345 | 0.90145 | 8.2 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98365 | 0.7995 | 18.415 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98257 | 0.80086 | 18.171 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98466 | 0.79045 | 19.42 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98256 | 0.88423 | 9.833 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96027 | 0.73392 | 22.635 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96027 | 0.74925 | 21.102 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96027 | 0.76207 | 19.82 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96027 | 0.76739 | 19.289 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96027 | 0.78417 | 17.61 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98749 | 0.76427 | 22.322 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.90399 | 8.273 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.89581 | 8.318 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98198 | 0.79205 | 18.992 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98245 | 0.7925 | 18.995 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98537 | 0.89937 | 8.601 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98588 | 0.90307 | 8.281 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98595 | 0.90307 | 8.288 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98298 | 0.80185 | 18.114 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97988 | 0.79474 | 18.515 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97988 | 0.89197 | 8.791 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98361 | 0.8973 | 8.631 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.90327 | 8.307 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98148 | 0.79294 | 18.854 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.78264 | 19.635 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97899 | 0.79685 | 18.214 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9872 | 0.76364 | 22.356 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96676 | 0.73355 | 23.321 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96676 | 0.76162 | 20.514 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96676 | 0.76908 | 19.768 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96676 | 0.79883 | 16.793 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98115 | 0.86882 | 11.233 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98089 | 0.74634 | 23.455 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98457 | 0.90418 | 8.04 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98704 | 0.78865 | 19.84 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98174 | 0.79638 | 18.536 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98141 | 0.76254 | 21.887 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98141 | 0.76297 | 21.844 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99095 | 0.79357 | 19.738 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99095 | 0.90138 | 8.957 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97632 | 0.78014 | 19.618 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97632 | 0.79332 | 18.301 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98591 | 0.88083 | 10.508 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98073 | 0.89958 | 8.115 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98073 | 0.89958 | 8.115 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98578 | 0.90192 | 8.386 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98256 | 0.88423 | 9.833 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98513 | 0.89461 | 9.053 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9851 | 0.89514 | 8.996 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98235 | 0.78882 | 19.353 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98235 | 0.89279 | 8.957 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98349 | 0.79405 | 18.944 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98335 | 0.79897 | 18.438 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98523 | 0.88853 | 9.67 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98451 | 0.89627 | 8.824 | Yes
Active | 2025W1-N11-WVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98318 | 0.7979 | 18.528 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.91555 | 8.04 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.91555 | 8.04 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99554 | 0.90644 | 8.91 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.89512 | 9.805 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.79693 | 19.489 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9931 | 0.90727 | 8.582 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99245 | 0.79613 | 19.632 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9913 | 0.79753 | 19.377 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.78705 | 20.643 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.88678 | 10.436 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96795 | 0.73145 | 23.65 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96795 | 0.74694 | 22.101 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96795 | 0.75948 | 20.847 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96795 | 0.76431 | 20.364 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96795 | 0.78089 | 18.706 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96795 | 0.87028 | 9.767 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96795 | 0.87718 | 9.077 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99655 | 0.76038 | 23.618 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99568 | 0.90811 | 8.758 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98363 | 0.89443 | 8.92 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.78866 | 20.203 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99069 | 0.90926 | 8.143 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.7891 | 20.209 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.9032 | 9.105 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99479 | 0.90713 | 8.766 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99487 | 0.90714 | 8.773 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99189 | 0.79857 | 19.332 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.91183 | 8.356 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98842 | 0.79129 | 19.714 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98842 | 0.89533 | 9.31 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99238 | 0.90097 | 9.141 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99529 | 0.90736 | 8.793 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.78958 | 20.052 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9901 | 0.90631 | 8.379 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98743 | 0.77932 | 20.811 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98743 | 0.79357 | 19.385 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.76053 | 23.58 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97476 | 0.73108 | 24.368 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97476 | 0.75912 | 21.565 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97476 | 0.76521 | 20.955 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97476 | 0.79566 | 17.91 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98969 | 0.87028 | 11.942 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.744 | 24.589 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99326 | 0.90796 | 8.53 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99608 | 0.7851 | 21.098 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.91185 | 8.233 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.79324 | 19.723 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99045 | 0.75989 | 23.056 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99045 | 0.76039 | 23.006 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.7905 | 20.988 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.90578 | 9.459 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98479 | 0.77683 | 20.796 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98479 | 0.79003 | 19.476 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.91546 | 8.057 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.88338 | 11.161 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.91122 | 8.318 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98626 | 0.90002 | 8.624 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98626 | 0.90002 | 8.624 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.90592 | 8.877 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.91045 | 8.353 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.90826 | 8.124 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.90827 | 8.123 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.88678 | 10.436 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.89811 | 9.589 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.89868 | 9.529 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.91342 | 8.148 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.78544 | 20.562 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99106 | 0.89624 | 9.482 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99228 | 0.79065 | 20.162 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.91052 | 8.376 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.79559 | 19.654 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.89165 | 10.245 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.89991 | 9.345 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.913 | 8.162 | Yes
Active | 2025W1-N11-WVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.7945 | 19.745 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.91332 | 8.507 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.81869 | 17.882 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99793 | 0.81468 | 18.325 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.81772 | 17.92 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.80381 | 19.702 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98953 | 0.8929 | 9.663 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98268 | 0.75603 | 22.665 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98268 | 0.76822 | 21.447 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98268 | 0.77464 | 20.805 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98268 | 0.7869 | 19.578 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98268 | 0.79687 | 18.582 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98268 | 0.80284 | 17.984 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98268 | 0.80666 | 17.602 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98268 | 0.89157 | 9.111 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98268 | 0.89609 | 8.659 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.78785 | 21.372 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99549 | 0.80366 | 19.182 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.80434 | 19.185 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.81986 | 17.787 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.81228 | 18.2 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99428 | 0.91013 | 8.415 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.998 | 0.91761 | 8.039 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99569 | 0.80934 | 18.636 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99406 | 0.79657 | 19.748 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99406 | 0.80869 | 18.536 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.7825 | 21.791 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98783 | 0.75565 | 23.218 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98783 | 0.77125 | 21.658 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98783 | 0.79303 | 19.48 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98783 | 0.80892 | 17.891 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99556 | 0.88844 | 10.712 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.76462 | 22.774 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.80967 | 19.16 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99632 | 0.81506 | 18.126 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99327 | 0.77168 | 22.159 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99327 | 0.77427 | 21.9 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.80658 | 19.587 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.91512 | 8.732 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.79184 | 19.935 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99119 | 0.8022 | 18.899 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99994 | 0.9018 | 9.814 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98953 | 0.8929 | 9.663 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.91382 | 8.533 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9991 | 0.91438 | 8.472 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99727 | 0.80107 | 19.62 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99727 | 0.90886 | 8.841 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9977 | 0.80645 | 19.125 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.81428 | 18.332 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9995 | 0.90758 | 9.191 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99857 | 0.91605 | 8.252 | Yes
Active | 2025W1-N11-WVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99733 | 0.81282 | 18.451 | Yes
Active | 2025W1-N11-WVD243877 | 243877 | 05DAWKNS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98417 | 0.87202 | 11.215 | Yes
Active | 2025W1-N11-WVD243877 | 243877 | 05DAWKNS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9652 | 0.88447 | 8.072 | Yes
Active | 2025W1-N11-WVD243890 | 243890 | 05WOODSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99118 | 0.8797 | 11.147 | Yes
Active | 2025W1-N11-WVD243890 | 243890 | 05WOODSR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98947 | 0.90919 | 8.028 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.87386 | 11.587 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9894 | 0.87249 | 11.691 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9887 | 0.87229 | 11.641 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98951 | 0.86925 | 12.026 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97535 | 0.81823 | 15.712 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97535 | 0.82213 | 15.322 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97535 | 0.84687 | 12.849 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97535 | 0.85425 | 12.11 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97535 | 0.86309 | 11.226 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97535 | 0.86556 | 10.98 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97535 | 0.86842 | 10.694 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99178 | 0.84215 | 14.962 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98938 | 0.87205 | 11.734 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9896 | 0.87216 | 11.745 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.87305 | 11.647 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98696 | 0.86824 | 11.873 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98807 | 0.86862 | 11.946 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98597 | 0.86178 | 12.419 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98597 | 0.86261 | 12.336 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.84087 | 15.072 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97615 | 0.80965 | 16.651 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97615 | 0.81783 | 15.833 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97615 | 0.84876 | 12.739 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97615 | 0.86658 | 10.957 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98527 | 0.85953 | 12.574 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99188 | 0.87457 | 11.731 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98914 | 0.87188 | 11.726 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97028 | 0.81203 | 15.825 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97028 | 0.82379 | 14.649 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98908 | 0.85546 | 13.363 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98579 | 0.86124 | 12.455 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98579 | 0.86143 | 12.436 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98836 | 0.86859 | 11.977 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99 | 0.87282 | 11.718 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98912 | 0.87187 | 11.725 | Yes
Active | 2025W1-N11-WVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.87132 | 11.77 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99019 | 0.86772 | 12.247 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98988 | 0.86628 | 12.359 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.86623 | 12.292 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98997 | 0.86238 | 12.759 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97433 | 0.80845 | 16.588 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97433 | 0.81552 | 15.881 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97433 | 0.83874 | 13.559 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97433 | 0.84937 | 12.496 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97433 | 0.85541 | 11.892 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97433 | 0.85837 | 11.597 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97433 | 0.8614 | 11.294 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99241 | 0.83372 | 15.869 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98968 | 0.86517 | 12.451 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.86531 | 12.462 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.86712 | 12.29 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98736 | 0.86208 | 12.528 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98845 | 0.86222 | 12.624 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98625 | 0.85501 | 13.124 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98625 | 0.85615 | 13.009 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99237 | 0.83304 | 15.933 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9753 | 0.80297 | 17.232 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9753 | 0.80805 | 16.725 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9753 | 0.84011 | 13.519 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9753 | 0.85976 | 11.554 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98509 | 0.85194 | 13.315 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99247 | 0.86844 | 12.403 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98954 | 0.8656 | 12.394 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97207 | 0.80518 | 16.689 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97207 | 0.81701 | 15.506 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99076 | 0.85062 | 14.014 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98575 | 0.85411 | 13.164 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98575 | 0.85458 | 13.117 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.86165 | 12.707 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99038 | 0.86605 | 12.433 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.86566 | 12.393 | Yes
Active | 2025W1-N11-WVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98948 | 0.86507 | 12.441 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98697 | 0.90313 | 8.384 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98363 | 0.89144 | 9.218 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98306 | 0.80262 | 18.044 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98317 | 0.80057 | 18.26 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98223 | 0.80186 | 18.037 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98355 | 0.79255 | 19.1 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98245 | 0.88494 | 9.752 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96139 | 0.73826 | 22.314 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96139 | 0.7537 | 20.769 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96139 | 0.76183 | 19.956 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96139 | 0.76981 | 19.158 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96139 | 0.78525 | 17.614 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98773 | 0.76747 | 22.026 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98698 | 0.90508 | 8.19 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98246 | 0.90097 | 8.149 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98195 | 0.79517 | 18.678 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9824 | 0.79555 | 18.685 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98497 | 0.89957 | 8.54 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98556 | 0.90341 | 8.215 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98563 | 0.90339 | 8.223 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98327 | 0.80249 | 18.078 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97924 | 0.79535 | 18.389 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97924 | 0.89072 | 8.852 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9833 | 0.8978 | 8.549 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9866 | 0.90437 | 8.223 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98137 | 0.79498 | 18.639 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97808 | 0.78424 | 19.384 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97808 | 0.79666 | 18.143 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98727 | 0.7665 | 22.078 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96712 | 0.73805 | 22.907 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96712 | 0.76029 | 20.683 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96712 | 0.77177 | 19.535 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96712 | 0.79825 | 16.887 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97964 | 0.8672 | 11.244 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97932 | 0.7509 | 22.843 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.79328 | 19.403 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98198 | 0.79937 | 18.26 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97909 | 0.76162 | 21.747 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97909 | 0.76251 | 21.658 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.79389 | 19.614 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99003 | 0.90006 | 8.997 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97543 | 0.7812 | 19.423 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97543 | 0.7926 | 18.282 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98597 | 0.88052 | 10.545 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98221 | 0.90213 | 8.007 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98221 | 0.90213 | 8.007 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.90223 | 8.322 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98245 | 0.88494 | 9.752 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98149 | 0.88846 | 9.303 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98133 | 0.88904 | 9.23 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98156 | 0.79123 | 19.033 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98156 | 0.89227 | 8.928 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98329 | 0.79693 | 18.636 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9828 | 0.79992 | 18.287 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98465 | 0.8884 | 9.625 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98389 | 0.89628 | 8.761 | Yes
Active | 2025W1-N11-WVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98262 | 0.79891 | 18.37 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91581 | 8.247 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.90686 | 8.945 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9945 | 0.81172 | 18.278 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99517 | 0.81073 | 18.444 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99412 | 0.81247 | 18.165 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99668 | 0.80081 | 19.588 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.89457 | 9.748 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97506 | 0.748 | 22.705 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97506 | 0.76096 | 21.41 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97506 | 0.77127 | 20.379 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97506 | 0.78005 | 19.5 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97506 | 0.79444 | 18.062 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97506 | 0.8025 | 17.256 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97506 | 0.88282 | 9.224 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97506 | 0.888 | 8.705 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99875 | 0.78091 | 21.784 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99824 | 0.91791 | 8.033 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99145 | 0.91036 | 8.11 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99328 | 0.80199 | 19.129 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99381 | 0.80251 | 19.13 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99701 | 0.913 | 8.401 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99756 | 0.91683 | 8.073 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.9168 | 8.08 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.81364 | 18.092 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99126 | 0.80593 | 18.533 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99126 | 0.9042 | 8.706 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.91117 | 8.42 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.91722 | 8.068 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99293 | 0.80357 | 18.936 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99079 | 0.79249 | 19.83 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99079 | 0.80621 | 18.458 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99798 | 0.77601 | 22.197 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98103 | 0.74743 | 23.36 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98103 | 0.76979 | 21.123 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98103 | 0.7856 | 19.543 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98103 | 0.80816 | 17.287 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99325 | 0.88316 | 11.009 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.75776 | 23.34 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.8017 | 19.675 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99312 | 0.8078 | 18.532 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99155 | 0.77099 | 22.057 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99155 | 0.77138 | 22.017 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.80283 | 19.801 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0009 | 0.91196 | 8.889 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98811 | 0.78992 | 19.818 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98811 | 0.80223 | 18.588 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.89456 | 10.268 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99746 | 0.91566 | 8.179 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.89457 | 9.748 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.90815 | 8.85 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99661 | 0.90869 | 8.793 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99406 | 0.79885 | 19.521 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99406 | 0.90511 | 8.896 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99497 | 0.80427 | 19.07 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.81021 | 18.465 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.90177 | 9.499 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.90982 | 8.621 | Yes
Active | 2025W1-N11-WVD244020 | 244020 | 05MINK | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.80901 | 18.565 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97927 | 0.88695 | 9.231 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98424 | 0.81718 | 16.705 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98452 | 0.81122 | 17.33 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.81521 | 16.822 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98867 | 0.80041 | 18.826 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98208 | 0.89278 | 8.93 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96692 | 0.75642 | 21.05 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96692 | 0.76902 | 19.789 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96692 | 0.77323 | 19.368 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96692 | 0.78669 | 18.023 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96692 | 0.79301 | 17.39 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96692 | 0.88417 | 8.275 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98793 | 0.78645 | 20.147 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.79872 | 18.295 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98249 | 0.79952 | 18.297 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98436 | 0.81791 | 16.645 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98119 | 0.81114 | 17.006 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98119 | 0.90063 | 8.057 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98205 | 0.80763 | 17.442 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97968 | 0.79624 | 18.344 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97968 | 0.8069 | 17.278 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98714 | 0.78242 | 20.472 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97146 | 0.75608 | 21.538 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97146 | 0.76931 | 20.215 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97146 | 0.79153 | 17.992 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97146 | 0.8041 | 16.736 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98112 | 0.87865 | 10.247 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97872 | 0.76558 | 21.314 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98753 | 0.80946 | 17.807 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9832 | 0.81395 | 16.926 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9777 | 0.76974 | 20.796 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9777 | 0.77293 | 20.477 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.80538 | 18.344 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98881 | 0.90502 | 8.379 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97553 | 0.78815 | 18.738 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97553 | 0.79776 | 17.777 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98662 | 0.89296 | 9.366 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98208 | 0.89278 | 8.93 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98542 | 0.90368 | 8.173 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98537 | 0.9042 | 8.117 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98445 | 0.79698 | 18.747 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98445 | 0.89804 | 8.64 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98423 | 0.80188 | 18.235 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98424 | 0.81111 | 17.313 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98581 | 0.89774 | 8.807 | Yes
Active | 2025W1-N11-WVD244022 | 244022 | 05COLE | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98393 | 0.80945 | 17.448 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97812 | 0.88511 | 9.301 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9821 | 0.80946 | 17.265 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9823 | 0.80429 | 17.801 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98118 | 0.80777 | 17.341 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98578 | 0.79385 | 19.192 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9798 | 0.88721 | 9.259 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96413 | 0.74788 | 21.625 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96413 | 0.76139 | 20.274 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96413 | 0.76686 | 19.727 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96413 | 0.77873 | 18.54 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96413 | 0.78694 | 17.718 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96413 | 0.87856 | 8.557 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96413 | 0.88254 | 8.159 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98599 | 0.77726 | 20.874 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97963 | 0.79289 | 18.674 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98039 | 0.79361 | 18.678 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98222 | 0.81022 | 17.201 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97895 | 0.8034 | 17.555 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97895 | 0.89559 | 8.335 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97988 | 0.80027 | 17.961 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97742 | 0.78901 | 18.841 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97742 | 0.79989 | 17.752 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98541 | 0.77427 | 21.114 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96894 | 0.74753 | 22.141 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96894 | 0.76323 | 20.571 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96894 | 0.78258 | 18.636 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96894 | 0.79824 | 17.07 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97897 | 0.87285 | 10.611 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9769 | 0.75777 | 21.913 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98544 | 0.80171 | 18.374 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98104 | 0.8062 | 17.484 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9766 | 0.76355 | 21.305 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9766 | 0.76643 | 21.017 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98757 | 0.79858 | 18.898 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98757 | 0.90123 | 8.634 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97345 | 0.78198 | 19.147 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97345 | 0.79179 | 18.166 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98463 | 0.88736 | 9.727 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9798 | 0.88721 | 9.259 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98335 | 0.89859 | 8.476 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9833 | 0.89912 | 8.418 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98187 | 0.7908 | 19.107 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98187 | 0.89343 | 8.844 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98202 | 0.79579 | 18.623 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98201 | 0.80409 | 17.792 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98373 | 0.8927 | 9.103 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98284 | 0.90082 | 8.202 | Yes
Active | 2025W1-N11-WVD244023 | 244023 | 05COLE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98172 | 0.80255 | 17.917 | Yes
Active | 2025W1-N11-WVD244183 | 244183 | 05LAFAY C SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9865 | 0.87116 | 11.533 | Yes
Active | 2025W1-N11-WVD244183 | 244183 | 05LAFAY C SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98474 | 0.90262 | 8.212 | Yes
Active | 2025W1-N11-WVD244183 | 244183 | 05LAFAY C SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96478 | 0.88376 | 8.103 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87768 | 12.944 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.87613 | 13.157 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87565 | 13.128 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.86683 | 14.105 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99404 | 0.82703 | 16.702 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99404 | 0.83507 | 15.898 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99404 | 0.83743 | 15.661 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99404 | 0.8514 | 14.265 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99404 | 0.85247 | 14.158 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99404 | 0.8609 | 13.314 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99404 | 0.86255 | 13.149 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0099 | 0.85989 | 15.006 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.86893 | 13.747 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.8693 | 13.741 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87723 | 12.986 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.867 | 13.642 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.88117 | 12.727 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.999 | 0.84814 | 15.086 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.999 | 0.85592 | 14.308 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.84868 | 15.868 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9958 | 0.82642 | 16.938 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9958 | 0.83254 | 16.326 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9958 | 0.86282 | 13.297 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9958 | 0.86844 | 12.736 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.8333 | 16.923 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0103 | 0.87031 | 14.001 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87516 | 13.118 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.8353 | 16.626 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.83911 | 16.245 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.86373 | 14.484 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.85757 | 14.41 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.86443 | 13.723 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.86554 | 14.086 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.87064 | 13.677 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.87501 | 13.227 | Yes
Active | 2025W1-N11-WVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.87437 | 13.28 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87375 | 13.253 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.87228 | 13.475 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87203 | 13.429 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.86326 | 14.403 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9941 | 0.82097 | 17.313 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9941 | 0.82973 | 16.437 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9941 | 0.83354 | 16.056 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9941 | 0.84644 | 14.766 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9941 | 0.85213 | 14.197 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9941 | 0.85764 | 13.646 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9941 | 0.85962 | 13.448 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.8549 | 15.412 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.8653 | 14.059 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.86568 | 14.051 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.87201 | 13.418 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.85982 | 14.118 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.87328 | 13.374 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.8474 | 15.285 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0003 | 0.85657 | 14.368 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.8433 | 16.368 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.82023 | 17.625 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99648 | 0.82931 | 16.718 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99648 | 0.85812 | 13.836 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99648 | 0.86632 | 13.016 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.82755 | 17.509 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.86575 | 14.364 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.87116 | 13.435 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.83188 | 17.003 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.8348 | 16.711 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.86035 | 14.783 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.85388 | 14.792 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.86201 | 13.979 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.86197 | 14.398 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.86702 | 13.979 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.87134 | 13.536 | Yes
Active | 2025W1-N11-WVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87063 | 13.598 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99456 | 0.91157 | 8.299 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9922 | 0.81758 | 17.462 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99268 | 0.81462 | 17.805 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.81716 | 17.455 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.80395 | 19.107 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.89514 | 9.321 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9753 | 0.75617 | 21.912 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9753 | 0.76773 | 20.757 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9753 | 0.77475 | 20.055 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9753 | 0.78654 | 18.876 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9753 | 0.79678 | 17.852 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9753 | 0.80132 | 17.397 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9753 | 0.80597 | 16.933 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9753 | 0.88704 | 8.826 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9753 | 0.89125 | 8.405 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99624 | 0.78887 | 20.736 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.80428 | 18.615 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.80491 | 18.615 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.81889 | 17.353 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98897 | 0.81129 | 17.768 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98897 | 0.90574 | 8.324 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99052 | 0.80692 | 18.36 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98912 | 0.79558 | 19.354 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98912 | 0.80812 | 18.099 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99506 | 0.78265 | 21.242 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98043 | 0.75574 | 22.47 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98043 | 0.77187 | 20.856 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98043 | 0.79345 | 18.699 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98043 | 0.80905 | 17.139 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99098 | 0.88622 | 10.476 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.76465 | 22.31 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.80852 | 18.75 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.81392 | 17.705 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98757 | 0.77291 | 21.467 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98757 | 0.77489 | 21.268 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.80633 | 19.073 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99706 | 0.91114 | 8.593 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98518 | 0.79229 | 19.289 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98518 | 0.80301 | 18.217 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.89835 | 9.626 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.89514 | 9.321 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.91021 | 8.392 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.91074 | 8.336 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.80147 | 19.038 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99185 | 0.90526 | 8.66 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.80692 | 18.551 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.81416 | 17.818 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.90375 | 9.052 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99346 | 0.91189 | 8.158 | Yes
Active | 2025W1-N11-WVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.81282 | 17.93 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98982 | 0.82262 | 16.72 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98999 | 0.81677 | 17.322 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.82062 | 16.837 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.80523 | 18.854 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98684 | 0.89794 | 8.89 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97354 | 0.7632 | 21.034 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97354 | 0.77404 | 19.95 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97354 | 0.77792 | 19.563 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97354 | 0.79222 | 18.133 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97354 | 0.79711 | 17.643 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97354 | 0.80504 | 16.85 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97354 | 0.8093 | 16.424 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97354 | 0.88976 | 8.378 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99354 | 0.79474 | 19.88 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98717 | 0.80398 | 18.319 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98797 | 0.80479 | 18.318 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99 | 0.82339 | 16.661 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98676 | 0.81631 | 17.045 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98676 | 0.9067 | 8.005 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9877 | 0.8109 | 17.68 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98636 | 0.79932 | 18.704 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98636 | 0.8107 | 17.566 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99226 | 0.78841 | 20.385 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97799 | 0.76283 | 21.516 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97799 | 0.77411 | 20.388 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97799 | 0.79922 | 17.878 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97799 | 0.80832 | 16.967 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98782 | 0.88677 | 10.106 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.77103 | 21.357 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.81426 | 17.909 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.81921 | 16.953 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98311 | 0.77498 | 20.812 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98311 | 0.77802 | 20.508 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.80974 | 18.381 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99355 | 0.91016 | 8.339 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98109 | 0.79264 | 18.845 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98109 | 0.80222 | 17.886 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99206 | 0.90017 | 9.189 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98684 | 0.89794 | 8.89 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.91043 | 8.081 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.91094 | 8.025 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.80186 | 18.784 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9897 | 0.90401 | 8.569 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.80719 | 18.248 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98968 | 0.81654 | 17.314 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9915 | 0.90421 | 8.729 | Yes
Active | 2025W1-N11-WVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98938 | 0.8149 | 17.448 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.88115 | 12.521 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87965 | 12.722 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87895 | 12.716 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87049 | 13.644 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99358 | 0.83206 | 16.152 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99358 | 0.8397 | 15.389 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99358 | 0.84125 | 15.233 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99358 | 0.85566 | 13.792 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99358 | 0.85604 | 13.754 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99358 | 0.86472 | 12.886 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99358 | 0.86573 | 12.786 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0091 | 0.86405 | 14.5 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.87265 | 13.295 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.873 | 13.29 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.88066 | 12.56 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.87063 | 13.21 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0078 | 0.88575 | 12.21 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99786 | 0.85189 | 14.597 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99786 | 0.8591 | 13.877 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.85305 | 15.337 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99506 | 0.83147 | 16.359 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99506 | 0.8363 | 15.876 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99506 | 0.86687 | 12.818 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99506 | 0.87178 | 12.328 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.83803 | 16.361 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.87393 | 13.547 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.87874 | 12.687 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.83916 | 16.133 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.84306 | 15.742 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.86701 | 14.047 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.86153 | 13.931 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.86794 | 13.29 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.86928 | 13.624 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.87428 | 13.228 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.87846 | 12.796 | Yes
Active | 2025W1-N11-WVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87789 | 12.843 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.91349 | 8.692 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99869 | 0.8179 | 18.079 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.81518 | 18.398 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9981 | 0.8176 | 18.05 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.80463 | 19.668 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.89511 | 9.723 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98259 | 0.75482 | 22.777 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98259 | 0.76782 | 21.477 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98259 | 0.7762 | 20.639 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98259 | 0.7863 | 19.629 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98259 | 0.79799 | 18.46 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98259 | 0.80257 | 18.002 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98259 | 0.80768 | 17.491 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98259 | 0.89039 | 9.219 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98259 | 0.89527 | 8.732 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.003 | 0.78625 | 21.674 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.8052 | 19.174 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99757 | 0.80581 | 19.176 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.91962 | 8.147 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.81935 | 17.949 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.81168 | 18.37 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99539 | 0.91027 | 8.512 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99938 | 0.91758 | 8.179 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.80826 | 18.845 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99464 | 0.79649 | 19.815 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99464 | 0.80939 | 18.526 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.78196 | 22.023 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98815 | 0.75438 | 23.376 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98815 | 0.77378 | 21.437 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98815 | 0.79138 | 19.677 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98815 | 0.81091 | 17.724 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99695 | 0.88856 | 10.838 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99485 | 0.76431 | 23.054 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.80835 | 19.418 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99742 | 0.81414 | 18.327 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99607 | 0.77446 | 22.16 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99607 | 0.77598 | 22.008 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.80775 | 19.704 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0048 | 0.91721 | 8.757 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99245 | 0.79311 | 19.933 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99245 | 0.80439 | 18.805 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.90159 | 9.984 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.89511 | 9.723 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91419 | 8.643 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91474 | 8.584 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.80227 | 19.592 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99819 | 0.90986 | 8.834 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99892 | 0.80776 | 19.115 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.81472 | 18.412 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.90776 | 9.303 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.91612 | 8.388 | Yes
Active | 2025W1-N11-WVD244338 | 244338 | 05POTH | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9986 | 0.81338 | 18.522 | Yes
Active | 2025W1-N11-WVD244341 | 244341 | 05SOFTAIL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0053 | 0.91887 | 8.646 | Yes
Active | 2025W1-N11-WVD244341 | 244341 | 05SOFTAIL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0053 | 0.92383 | 8.151 | Yes
Active | 2025W1-N11-WVD244341 | 244341 | 05SOFTAIL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0056 | 0.91166 | 9.393 | Yes
Active | 2025W1-N11-WVD244341 | 244341 | 05SOFTAIL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.92282 | 8.277 | Yes
Active | 2025W1-N11-WVD244341 | 244341 | 05SOFTAIL SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99954 | 0.91666 | 8.288 | Yes
Active | 2025W1-N11-WVD244489 | 244489 | 05FOGWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98665 | 0.87124 | 11.541 | Yes
Active | 2025W1-N11-WVD244489 | 244489 | 05FOGWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98489 | 0.90278 | 8.211 | Yes
Active | 2025W1-N11-WVD244489 | 244489 | 05FOGWELL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.965 | 0.88387 | 8.113 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.91054 | 9.297 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.9097 | 9.404 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.90706 | 9.584 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.90177 | 10.134 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9935 | 0.87394 | 11.957 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9935 | 0.87443 | 11.907 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9935 | 0.87878 | 11.473 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9935 | 0.88833 | 10.517 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9935 | 0.89162 | 10.188 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9935 | 0.89379 | 9.972 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9935 | 0.89771 | 9.579 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.005 | 0.89862 | 10.638 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.90403 | 9.86 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.90425 | 9.859 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.9101 | 9.303 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90199 | 9.889 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.92418 | 8.281 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.88533 | 10.827 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9936 | 0.88947 | 10.413 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.88966 | 11.302 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99346 | 0.87047 | 12.299 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99346 | 0.87338 | 12.007 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99346 | 0.90073 | 9.273 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99346 | 0.90214 | 9.132 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99865 | 0.87776 | 12.088 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.90453 | 10.064 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.90894 | 9.407 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9964 | 0.874 | 12.24 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.87712 | 11.928 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.89569 | 10.691 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99832 | 0.89542 | 10.29 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99832 | 0.89947 | 9.885 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.901 | 10.117 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.90513 | 9.815 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.90802 | 9.51 | Yes
Active | 2025W1-N11-WVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.90788 | 9.516 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.86743 | 13.734 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.86627 | 13.943 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.8664 | 13.871 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.85767 | 14.841 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99386 | 0.81209 | 18.177 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99386 | 0.82191 | 17.194 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99386 | 0.82742 | 16.643 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99386 | 0.83911 | 15.475 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99386 | 0.85116 | 14.27 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99386 | 0.85262 | 14.123 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99386 | 0.85494 | 13.892 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99386 | 0.9138 | 8.006 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0074 | 0.84699 | 16.041 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.85962 | 14.515 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.86 | 14.502 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.86409 | 14.042 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99726 | 0.84971 | 14.755 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.862 | 14.255 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.84568 | 15.586 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.85647 | 14.507 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.83518 | 17.082 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.81103 | 18.562 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99665 | 0.82385 | 17.279 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99665 | 0.85066 | 14.599 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99665 | 0.86254 | 13.411 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.92561 | 8.085 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.81897 | 18.321 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.85874 | 14.899 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.86469 | 13.932 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.82621 | 17.551 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.82802 | 17.369 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.8549 | 15.228 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.8481 | 15.332 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.85778 | 14.365 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.85636 | 14.852 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86135 | 14.422 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.86557 | 13.99 | Yes
Active | 2025W1-N11-WVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.86475 | 14.064 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.89914 | 10.392 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.89805 | 10.492 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.89779 | 10.476 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.89421 | 10.851 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0026 | 0.85853 | 14.409 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.86265 | 13.998 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0026 | 0.8824 | 12.023 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0026 | 0.88541 | 11.721 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0026 | 0.88708 | 11.554 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0026 | 0.89834 | 10.428 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0026 | 0.8998 | 10.282 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.87891 | 12.582 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.89687 | 10.595 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.897 | 10.597 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.89465 | 10.749 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99635 | 0.88518 | 11.116 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.89367 | 10.827 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.88604 | 11.431 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.89087 | 10.949 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.87243 | 13.191 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0005 | 0.84775 | 15.275 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.85841 | 14.209 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0005 | 0.88837 | 11.213 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0005 | 0.89916 | 10.134 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99821 | 0.87082 | 12.739 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.89497 | 10.97 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.89719 | 10.539 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99439 | 0.85554 | 13.885 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.8616 | 13.279 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.88094 | 12.006 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99963 | 0.88568 | 11.394 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99963 | 0.8898 | 10.982 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.89359 | 10.837 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.89769 | 10.556 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.89745 | 10.531 | Yes
Active | 2025W1-N11-WVD244566 | 244566 | 05LA RUE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.89691 | 10.578 | Yes
Active | 2025W1-N11-WVD244672 | 244672 | 05ROB PK_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99291 | 0.8806 | 11.231 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91743 | 8.084 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91743 | 8.084 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99786 | 0.90824 | 8.962 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.89709 | 9.845 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99411 | 0.79794 | 19.617 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9952 | 0.90876 | 8.644 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.79723 | 19.752 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.79863 | 19.498 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.78815 | 20.768 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.88853 | 10.492 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97016 | 0.73233 | 23.783 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97016 | 0.7474 | 22.276 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97016 | 0.75995 | 21.021 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97016 | 0.76531 | 20.485 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97016 | 0.78194 | 18.822 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97016 | 0.87174 | 9.841 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97016 | 0.87871 | 9.145 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99881 | 0.76225 | 23.656 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99799 | 0.90997 | 8.801 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98703 | 0.89752 | 8.951 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.78972 | 20.326 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99298 | 0.91109 | 8.188 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.79017 | 20.331 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99657 | 0.90502 | 9.155 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.909 | 8.813 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.90899 | 8.82 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.7996 | 19.453 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99774 | 0.91375 | 8.4 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9907 | 0.79237 | 19.833 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9907 | 0.89701 | 9.368 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.90281 | 9.189 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.90923 | 8.837 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.79065 | 20.178 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99243 | 0.90816 | 8.427 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9898 | 0.78037 | 20.943 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9898 | 0.79462 | 19.518 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9985 | 0.76154 | 23.696 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97702 | 0.73194 | 24.508 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97702 | 0.75955 | 21.747 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97702 | 0.76703 | 20.999 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97702 | 0.79665 | 18.037 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.87212 | 11.998 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.74447 | 24.744 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.9099 | 8.568 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99837 | 0.78619 | 21.219 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.91373 | 8.276 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99272 | 0.79423 | 19.85 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.76038 | 23.202 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9924 | 0.76086 | 23.154 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.79121 | 21.124 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.9072 | 9.525 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98704 | 0.77788 | 20.916 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98704 | 0.79107 | 19.597 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99833 | 0.91736 | 8.098 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.88503 | 11.221 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.91301 | 8.37 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.90306 | 8.659 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.90306 | 8.659 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99701 | 0.90777 | 8.924 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.91242 | 8.391 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.91021 | 8.166 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99187 | 0.91021 | 8.165 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.88853 | 10.492 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.89993 | 9.639 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99628 | 0.9005 | 9.578 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99721 | 0.91533 | 8.188 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.78652 | 20.687 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99338 | 0.898 | 9.538 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.79173 | 20.285 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.91239 | 8.42 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99443 | 0.7967 | 19.773 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99642 | 0.89339 | 10.303 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99566 | 0.90171 | 9.395 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.91489 | 8.203 | Yes
Active | 2025W1-N11-WVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.79561 | 19.864 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99289 | 0.9084 | 8.449 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.81402 | 17.66 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99118 | 0.81163 | 17.955 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.81397 | 17.623 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.80113 | 19.219 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89313 | 9.416 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97302 | 0.75226 | 22.076 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97302 | 0.76398 | 20.905 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97302 | 0.77177 | 20.126 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97302 | 0.78291 | 19.011 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97302 | 0.79417 | 17.885 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97302 | 0.80293 | 17.009 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97302 | 0.88382 | 8.92 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97302 | 0.88826 | 8.476 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99471 | 0.78508 | 20.963 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98903 | 0.80167 | 18.736 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98963 | 0.80227 | 18.736 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.91261 | 8.047 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99083 | 0.81553 | 17.53 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9874 | 0.80786 | 17.954 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9874 | 0.9032 | 8.42 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99143 | 0.91074 | 8.069 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98902 | 0.804 | 18.502 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98748 | 0.79278 | 19.47 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98748 | 0.8056 | 18.188 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.77902 | 21.459 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97835 | 0.75178 | 22.657 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97835 | 0.76923 | 20.912 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97835 | 0.78963 | 18.872 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97835 | 0.80676 | 17.159 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98945 | 0.88344 | 10.601 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.7609 | 22.549 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.80471 | 18.978 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98936 | 0.81029 | 17.907 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98628 | 0.77033 | 21.595 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98628 | 0.77192 | 21.436 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99579 | 0.80331 | 19.248 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99579 | 0.90911 | 8.668 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98376 | 0.78971 | 19.406 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98376 | 0.80078 | 18.299 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99311 | 0.89529 | 9.782 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89313 | 9.416 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99263 | 0.90761 | 8.503 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.90814 | 8.446 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.79879 | 19.151 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9903 | 0.90313 | 8.717 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.80422 | 18.672 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.81115 | 17.97 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.90116 | 9.16 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.90927 | 8.271 | Yes
Active | 2025W1-N11-WVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.80984 | 18.079 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.91054 | 8.445 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9931 | 0.81999 | 17.311 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99395 | 0.8196 | 17.434 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99302 | 0.8208 | 17.222 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99503 | 0.81023 | 18.48 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.90091 | 9.15 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97552 | 0.75739 | 21.813 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97552 | 0.76951 | 20.602 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97552 | 0.77931 | 19.621 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97552 | 0.78892 | 18.66 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97552 | 0.80461 | 17.092 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97552 | 0.80742 | 16.81 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97552 | 0.81066 | 16.486 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97552 | 0.88759 | 8.793 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97552 | 0.88945 | 8.607 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99693 | 0.79163 | 20.531 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.81177 | 18.065 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99285 | 0.81224 | 18.061 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99545 | 0.91544 | 8.001 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.82016 | 17.327 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98869 | 0.81154 | 17.715 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98869 | 0.90502 | 8.367 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99201 | 0.81236 | 17.965 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99008 | 0.80142 | 18.866 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99008 | 0.81534 | 17.474 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99617 | 0.78453 | 21.164 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98062 | 0.75631 | 22.43 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98062 | 0.77779 | 20.282 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98062 | 0.79608 | 18.454 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98062 | 0.81788 | 16.274 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99246 | 0.88864 | 10.383 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99011 | 0.76602 | 22.408 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99682 | 0.81003 | 18.68 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99188 | 0.8163 | 17.558 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.77923 | 21.08 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99003 | 0.77937 | 21.066 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99856 | 0.81056 | 18.8 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99856 | 0.91476 | 8.379 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98771 | 0.79966 | 18.805 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98771 | 0.81232 | 17.539 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99588 | 0.89668 | 9.921 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.90091 | 9.15 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99522 | 0.91166 | 8.356 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.91217 | 8.302 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99292 | 0.80853 | 18.44 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99292 | 0.9095 | 8.343 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99379 | 0.81385 | 17.994 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99368 | 0.81906 | 17.462 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99533 | 0.90561 | 8.973 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.91316 | 8.155 | Yes
Active | 2025W1-N11-WVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.81798 | 17.555 | Yes
Active | 2025W1-N11-WVD244935 | 244935 | 05MCKINLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99882 | 0.88303 | 11.58 | Yes
Active | 2025W1-N11-WVD244935 | 244935 | 05MCKINLEY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99705 | 0.91569 | 8.136 | Yes
Active | 2025W1-N11-WVD244935 | 244935 | 05MCKINLEY1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97831 | 0.89618 | 8.213 | Yes
Active | 2025W1-N11-WVD244936 | 244936 | 05MCKINLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99879 | 0.88299 | 11.58 | Yes
Active | 2025W1-N11-WVD244936 | 244936 | 05MCKINLEY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99701 | 0.91566 | 8.136 | Yes
Active | 2025W1-N11-WVD244936 | 244936 | 05MCKINLEY2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97827 | 0.89614 | 8.213 | Yes
Active | 2025W1-N11-WVD244967 | 244967 | 05ELLISON_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.994 | 0.87841 | 11.559 | Yes
Active | 2025W1-N11-WVD244967 | 244967 | 05ELLISON_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99223 | 0.91071 | 8.152 | Yes
Active | 2025W1-N11-WVD244967 | 244967 | 05ELLISON_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97322 | 0.89138 | 8.183 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.92321 | 8.11 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0003 | 0.89694 | 10.34 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0003 | 0.89784 | 10.25 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0003 | 0.90762 | 9.273 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0003 | 0.91375 | 8.659 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0003 | 0.91736 | 8.299 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.005 | 0.91459 | 9.045 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.92204 | 8.125 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99816 | 0.91405 | 8.411 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.9233 | 8.039 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.9175 | 8.537 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0029 | 0.92263 | 8.024 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.9076 | 9.72 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0012 | 0.89209 | 10.914 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.89499 | 10.625 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0012 | 0.91935 | 8.188 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.90269 | 9.943 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.92331 | 8.197 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99915 | 0.89626 | 10.289 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.89948 | 9.967 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.91565 | 8.795 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.91759 | 8.498 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.92212 | 8.045 | Yes
Active | 2025W1-N11-WVD244991 | 244991 | 05HOWARD2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.92273 | 8.113 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99638 | 0.914 | 8.238 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99638 | 0.914 | 8.238 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99596 | 0.90464 | 9.132 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.89316 | 10.042 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99214 | 0.79207 | 20.007 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99533 | 0.91402 | 8.131 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.90535 | 8.802 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.79136 | 20.145 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99163 | 0.79273 | 19.891 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99386 | 0.78236 | 21.15 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99153 | 0.88459 | 10.694 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.91248 | 8.087 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96771 | 0.72693 | 24.077 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96771 | 0.74214 | 22.557 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96771 | 0.75463 | 21.307 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96771 | 0.75967 | 20.803 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96771 | 0.77622 | 19.149 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96771 | 0.87449 | 9.322 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99696 | 0.75619 | 24.077 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9961 | 0.90638 | 8.972 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.89326 | 9.134 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.91186 | 8.083 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99101 | 0.78395 | 20.705 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99101 | 0.90759 | 8.342 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99151 | 0.78439 | 20.712 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99465 | 0.90134 | 9.331 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99521 | 0.90538 | 8.982 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.90538 | 8.99 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.79371 | 19.85 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.91021 | 8.56 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98866 | 0.7865 | 20.216 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98866 | 0.89319 | 9.547 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99274 | 0.89907 | 9.367 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99569 | 0.90562 | 9.007 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99042 | 0.78483 | 20.559 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99042 | 0.90456 | 8.586 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98771 | 0.77464 | 21.306 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98771 | 0.78882 | 19.889 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9967 | 0.75593 | 24.076 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97469 | 0.72655 | 24.814 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97469 | 0.75429 | 22.04 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97469 | 0.76096 | 21.372 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97469 | 0.79088 | 18.381 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.86763 | 12.243 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99008 | 0.73923 | 25.085 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99356 | 0.90611 | 8.745 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99652 | 0.78036 | 21.616 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.91022 | 8.435 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99075 | 0.78841 | 20.234 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99059 | 0.75507 | 23.552 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99059 | 0.75559 | 23.501 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.78557 | 21.52 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.90382 | 9.695 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98496 | 0.7722 | 21.276 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98496 | 0.78533 | 19.963 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99645 | 0.91391 | 8.253 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99541 | 0.88094 | 11.447 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99477 | 0.9095 | 8.527 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.89894 | 8.832 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.89894 | 8.832 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.90414 | 9.096 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.90883 | 8.555 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98972 | 0.90648 | 8.324 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98972 | 0.90648 | 8.324 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99153 | 0.88459 | 10.694 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.89614 | 9.825 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99436 | 0.89673 | 9.763 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.91185 | 8.346 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99139 | 0.78076 | 21.063 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99139 | 0.89422 | 9.717 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.78593 | 20.669 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.90886 | 8.581 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99248 | 0.79083 | 20.165 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.88948 | 10.501 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99373 | 0.89796 | 9.576 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.91141 | 8.361 | Yes
Active | 2025W1-N11-WVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.78974 | 20.255 | Yes
Active | 2025W1-N11-WVD245422 | 245422 | 05W.END FOS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0059 | 0.92126 | 8.467 | Yes
Active | 2025W1-N11-WVD245422 | 245422 | 05W.END FOS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0062 | 0.91423 | 9.199 | Yes
Active | 2025W1-N11-WVD245422 | 245422 | 05W.END FOS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92506 | 8.116 | Yes
Active | 2025W1-N11-WVD245422 | 245422 | 05W.END FOS2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.91919 | 8.125 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98176 | 0.88341 | 9.836 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98176 | 0.88982 | 9.194 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98176 | 0.89928 | 8.249 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98756 | 0.90313 | 8.444 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98713 | 0.89981 | 8.732 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98181 | 0.8745 | 10.731 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98181 | 0.88918 | 9.263 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97294 | 0.88081 | 9.213 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97294 | 0.88872 | 8.422 | Yes
Active | 2025W1-N11-WVD245456 | 245456 | 05NEWBERY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98384 | 0.90188 | 8.196 | Yes
Active | 2025W1-N11-WVD245476 | 245476 | 05ROB PK34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99341 | 0.88111 | 11.23 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91742 | 8.086 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91742 | 8.086 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99786 | 0.90823 | 8.963 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.89707 | 9.846 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.7979 | 19.621 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9952 | 0.90875 | 8.645 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.79719 | 19.756 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.79858 | 19.502 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.78811 | 20.772 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.88851 | 10.493 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97015 | 0.73229 | 23.786 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97015 | 0.74736 | 22.279 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97015 | 0.75991 | 21.024 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97015 | 0.76527 | 20.488 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97015 | 0.7819 | 18.825 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97015 | 0.87172 | 9.843 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97015 | 0.87869 | 9.147 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99881 | 0.76221 | 23.66 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99799 | 0.90996 | 8.803 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98703 | 0.8975 | 8.953 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.78968 | 20.329 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99298 | 0.91108 | 8.19 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.79013 | 20.335 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99657 | 0.905 | 9.157 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.90898 | 8.814 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99719 | 0.90898 | 8.822 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.79956 | 19.457 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99774 | 0.91373 | 8.401 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.79233 | 19.837 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99069 | 0.89699 | 9.37 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.90279 | 9.191 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.90921 | 8.838 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.79061 | 20.182 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99242 | 0.90814 | 8.428 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9898 | 0.78033 | 20.946 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9898 | 0.79458 | 19.522 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9985 | 0.7615 | 23.7 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97701 | 0.7319 | 24.511 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97701 | 0.75951 | 21.75 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97701 | 0.76699 | 21.003 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97701 | 0.79661 | 18.041 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.8721 | 12 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.74443 | 24.747 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.90988 | 8.57 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99837 | 0.78615 | 21.223 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.91371 | 8.278 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99272 | 0.79419 | 19.853 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.76034 | 23.206 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9924 | 0.76082 | 23.158 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.79117 | 21.128 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.90718 | 9.526 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98704 | 0.77784 | 20.92 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98704 | 0.79103 | 19.601 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99833 | 0.91734 | 8.099 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.88501 | 11.223 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.913 | 8.371 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.90304 | 8.661 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.90304 | 8.661 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99701 | 0.90775 | 8.926 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.9124 | 8.393 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.91019 | 8.167 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.91019 | 8.167 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.88851 | 10.493 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.89991 | 9.64 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99628 | 0.90048 | 9.58 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99721 | 0.91531 | 8.19 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.78648 | 20.69 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99338 | 0.89798 | 9.54 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.79169 | 20.289 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99658 | 0.91237 | 8.421 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99443 | 0.79666 | 19.777 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99641 | 0.89337 | 10.305 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99566 | 0.90169 | 9.397 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.91487 | 8.205 | Yes
Active | 2025W1-N11-WVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.79557 | 19.868 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99848 | 0.91776 | 8.072 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99848 | 0.91776 | 8.072 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.90858 | 8.948 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99574 | 0.89746 | 9.828 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99431 | 0.79844 | 19.587 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.90907 | 8.632 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99496 | 0.79774 | 19.721 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99381 | 0.79914 | 19.467 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.78865 | 20.738 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99365 | 0.88889 | 10.475 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9704 | 0.7328 | 23.76 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9704 | 0.74785 | 22.255 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9704 | 0.7604 | 21 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9704 | 0.7658 | 20.46 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9704 | 0.78244 | 18.796 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9704 | 0.87213 | 9.827 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9704 | 0.87909 | 9.132 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.999 | 0.7628 | 23.62 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.91031 | 8.788 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98732 | 0.89796 | 8.936 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.79022 | 20.296 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99318 | 0.91142 | 8.176 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.79067 | 20.301 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.90537 | 9.141 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99732 | 0.90933 | 8.799 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.90933 | 8.806 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.80011 | 19.422 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99795 | 0.91408 | 8.387 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99091 | 0.79288 | 19.803 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99091 | 0.89736 | 9.355 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.90316 | 9.175 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99779 | 0.90956 | 8.823 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99264 | 0.79115 | 20.148 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99264 | 0.90849 | 8.414 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.78087 | 20.915 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99002 | 0.79513 | 19.489 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99869 | 0.76203 | 23.665 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97725 | 0.73241 | 24.485 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97725 | 0.75999 | 21.726 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97725 | 0.76758 | 20.968 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97725 | 0.79715 | 18.011 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.87254 | 11.978 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.74492 | 24.718 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99579 | 0.91025 | 8.554 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99857 | 0.7867 | 21.187 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.91405 | 8.264 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99293 | 0.79473 | 19.82 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.76083 | 23.175 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99258 | 0.76131 | 23.127 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.79169 | 21.093 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.9075 | 9.512 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.77838 | 20.888 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98726 | 0.79157 | 19.569 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99853 | 0.91768 | 8.085 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.8854 | 11.203 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99691 | 0.91334 | 8.357 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98993 | 0.90348 | 8.645 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98993 | 0.90348 | 8.645 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99721 | 0.90811 | 8.911 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99654 | 0.91276 | 8.378 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.91055 | 8.153 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.91056 | 8.153 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99365 | 0.88889 | 10.475 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99651 | 0.90028 | 9.624 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.90085 | 9.563 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99741 | 0.91566 | 8.175 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.78702 | 20.657 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99359 | 0.89835 | 9.524 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.79223 | 20.255 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.91272 | 8.407 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99464 | 0.79721 | 19.742 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99662 | 0.89375 | 10.287 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99586 | 0.90205 | 9.381 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.91521 | 8.191 | Yes
Active | 2025W1-N11-WVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99445 | 0.79612 | 19.833 | Yes
Active | 2025W1-N11-WVD245511 | 245511 | 05INDUST PK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99644 | 0.88149 | 11.495 | Yes
Active | 2025W1-N11-WVD245511 | 245511 | 05INDUST PK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99467 | 0.91352 | 8.115 | Yes
Active | 2025W1-N11-WVD245511 | 245511 | 05INDUST PK2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97569 | 0.89502 | 8.067 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99406 | 0.90149 | 9.257 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.90046 | 9.325 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.89948 | 9.36 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99395 | 0.90042 | 9.353 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9849 | 0.85315 | 13.175 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9849 | 0.85954 | 12.537 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9849 | 0.87671 | 10.82 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9849 | 0.88169 | 10.322 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9849 | 0.89413 | 9.077 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9849 | 0.89637 | 8.853 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9849 | 0.89855 | 8.635 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99537 | 0.87874 | 11.662 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.90347 | 9.116 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99474 | 0.90345 | 9.129 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.8997 | 9.399 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9915 | 0.89544 | 9.605 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.89715 | 9.561 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.89151 | 9.96 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99111 | 0.89163 | 9.948 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.87507 | 11.965 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98492 | 0.84163 | 14.33 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98492 | 0.85878 | 12.614 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98492 | 0.88535 | 9.958 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98492 | 0.89614 | 8.878 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.88904 | 10.097 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.90162 | 9.397 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99365 | 0.89995 | 9.37 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97179 | 0.84595 | 12.584 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97179 | 0.85638 | 11.541 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98975 | 0.87899 | 11.075 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99006 | 0.89018 | 9.988 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99006 | 0.89056 | 9.95 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99325 | 0.90007 | 9.318 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.90375 | 9.11 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.89974 | 9.368 | Yes
Active | 2025W1-N11-WVD245516 | 245516 | 05ROCKHILL2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.89937 | 9.397 | Yes
Active | 2025W1-N11-WVD245632 | 245632 | 05ARBOLES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0178 | 0.93438 | 8.341 | Yes
Active | 2025W1-N11-WVD245632 | 245632 | 05ARBOLES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0178 | 0.93367 | 8.412 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.85089 | 14.033 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98816 | 0.84038 | 14.778 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.82967 | 16.403 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97838 | 0.79687 | 18.151 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97838 | 0.80408 | 17.43 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97838 | 0.80566 | 17.273 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97838 | 0.82308 | 15.53 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97838 | 0.8334 | 14.498 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97838 | 0.83507 | 14.331 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99378 | 0.82699 | 16.679 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98777 | 0.82815 | 15.962 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.82902 | 15.946 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.85128 | 13.996 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.989 | 0.84521 | 14.379 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98895 | 0.84056 | 14.839 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98667 | 0.82867 | 15.799 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98667 | 0.83737 | 14.929 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.81997 | 17.255 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98133 | 0.79668 | 18.465 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98133 | 0.7992 | 18.213 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98133 | 0.83081 | 15.052 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.90401 | 8.429 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98604 | 0.80322 | 18.283 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.84383 | 14.989 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.84799 | 14.249 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98249 | 0.80018 | 18.231 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98249 | 0.80454 | 17.795 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.83614 | 15.627 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.82584 | 16.408 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.83167 | 15.843 | Yes
Active | 2025W1-N11-WVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99023 | 0.83089 | 15.934 | Yes
Active | 2025W1-N11-WVD245832 | 245832 | 05LINCOLN2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98892 | 0.87726 | 11.165 | Yes
Active | 2025W1-N11-WVD245832 | 245832 | 05LINCOLN2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97036 | 0.88954 | 8.082 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99757 | 0.90821 | 8.936 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.81613 | 18.152 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.81194 | 18.596 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.81495 | 18.182 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.80126 | 19.943 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.89285 | 9.804 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98309 | 0.75418 | 22.891 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98309 | 0.7678 | 21.528 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98309 | 0.77479 | 20.829 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98309 | 0.7856 | 19.749 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98309 | 0.79566 | 18.743 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98309 | 0.80188 | 18.121 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98309 | 0.80662 | 17.647 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98309 | 0.89096 | 9.212 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98309 | 0.8956 | 8.749 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.78306 | 21.881 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.80116 | 19.424 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.80183 | 19.428 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.91798 | 8.184 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99778 | 0.81717 | 18.06 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99431 | 0.80977 | 18.455 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99431 | 0.90851 | 8.58 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99804 | 0.91576 | 8.228 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99541 | 0.80665 | 18.876 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99302 | 0.79452 | 19.85 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99302 | 0.80645 | 18.657 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.77993 | 22.128 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98837 | 0.7538 | 23.457 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98837 | 0.77166 | 21.671 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98837 | 0.7896 | 19.877 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98837 | 0.80783 | 18.054 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.88521 | 10.978 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.76299 | 23.005 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.80729 | 19.398 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.81256 | 18.39 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9943 | 0.77092 | 22.339 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.77325 | 22.106 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.80538 | 19.835 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0037 | 0.91511 | 8.862 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.78946 | 20.111 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99057 | 0.7999 | 19.067 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.89973 | 10.063 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.89285 | 9.804 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.91172 | 8.743 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9991 | 0.91228 | 8.682 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9971 | 0.79856 | 19.854 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9971 | 0.907 | 9.01 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99763 | 0.80391 | 19.373 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99757 | 0.81158 | 18.599 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9995 | 0.90565 | 9.385 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99863 | 0.91419 | 8.444 | Yes
Active | 2025W1-N11-WVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9973 | 0.81012 | 18.719 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.92324 | 8.109 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.89696 | 10.34 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0004 | 0.89787 | 10.249 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0004 | 0.90764 | 9.272 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0004 | 0.91377 | 8.659 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0004 | 0.91738 | 8.298 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0051 | 0.91461 | 9.045 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.92206 | 8.125 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99818 | 0.91407 | 8.411 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.92332 | 8.039 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.91752 | 8.537 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0029 | 0.92265 | 8.024 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.90762 | 9.72 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0013 | 0.89212 | 10.913 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89501 | 10.624 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0013 | 0.91938 | 8.188 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.90271 | 9.943 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.92333 | 8.196 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99918 | 0.89629 | 10.288 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99918 | 0.89951 | 9.967 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.91567 | 8.794 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.91762 | 8.498 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.92214 | 8.045 | Yes
Active | 2025W1-N11-WVD245875 | 245875 | 05HOWARD_BUC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.92275 | 8.113 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99442 | 0.89355 | 10.087 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99442 | 0.89926 | 9.516 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99442 | 0.91095 | 8.346 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.91353 | 8.662 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99977 | 0.90981 | 8.996 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99456 | 0.88478 | 10.977 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99456 | 0.89839 | 9.617 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98602 | 0.89016 | 9.585 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98602 | 0.89768 | 8.833 | Yes
Active | 2025W1-N11-WVD245905 | 245905 | 05NEW LIBR2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99668 | 0.91259 | 8.409 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98406 | 0.90033 | 8.373 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98069 | 0.88827 | 9.241 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98019 | 0.79985 | 18.034 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98023 | 0.79773 | 18.249 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97929 | 0.7991 | 18.02 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98058 | 0.78976 | 19.081 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9795 | 0.88183 | 9.767 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95828 | 0.73563 | 22.265 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95828 | 0.75139 | 20.689 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95828 | 0.75949 | 19.88 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95828 | 0.76725 | 19.103 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95828 | 0.7824 | 17.588 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98496 | 0.76407 | 22.089 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98416 | 0.90206 | 8.211 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97955 | 0.89796 | 8.159 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.979 | 0.79244 | 18.656 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97945 | 0.79281 | 18.664 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98206 | 0.89661 | 8.545 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98263 | 0.90039 | 8.224 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.90038 | 8.232 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98027 | 0.79994 | 18.033 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97657 | 0.79305 | 18.352 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97657 | 0.88809 | 8.848 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98034 | 0.8947 | 8.564 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98377 | 0.90134 | 8.243 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97841 | 0.79228 | 18.613 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97502 | 0.78154 | 19.347 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97502 | 0.79376 | 18.126 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.76395 | 22.058 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96398 | 0.73547 | 22.851 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96398 | 0.75781 | 20.617 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96398 | 0.7684 | 19.558 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96398 | 0.79524 | 16.874 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97651 | 0.86379 | 11.273 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97643 | 0.74858 | 22.786 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98448 | 0.7907 | 19.378 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97909 | 0.79661 | 18.248 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97625 | 0.75911 | 21.714 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97625 | 0.76018 | 21.607 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98745 | 0.79151 | 19.594 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98745 | 0.89719 | 9.026 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97231 | 0.77838 | 19.393 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97231 | 0.78959 | 18.272 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.983 | 0.87787 | 10.513 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97926 | 0.89904 | 8.022 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97926 | 0.89904 | 8.022 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98252 | 0.89921 | 8.33 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9795 | 0.88183 | 9.767 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97841 | 0.88503 | 9.338 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97824 | 0.88561 | 9.264 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97856 | 0.78845 | 19.011 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97856 | 0.88901 | 8.955 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98035 | 0.79419 | 18.617 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97985 | 0.79709 | 18.276 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98173 | 0.88531 | 9.642 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98098 | 0.89322 | 8.775 | Yes
Active | 2025W1-N11-WVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97966 | 0.79608 | 18.358 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98407 | 0.90035 | 8.373 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98071 | 0.88829 | 9.241 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98021 | 0.79987 | 18.034 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98025 | 0.79775 | 18.25 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97931 | 0.79911 | 18.02 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98059 | 0.78978 | 19.081 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97952 | 0.88185 | 9.767 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9583 | 0.73565 | 22.265 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9583 | 0.7514 | 20.69 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9583 | 0.7595 | 19.88 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9583 | 0.76727 | 19.103 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9583 | 0.78242 | 17.588 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98497 | 0.76409 | 22.088 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98418 | 0.90207 | 8.211 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97957 | 0.89798 | 8.16 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97901 | 0.79246 | 18.656 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97947 | 0.79283 | 18.664 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98208 | 0.89663 | 8.545 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98265 | 0.9004 | 8.224 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98272 | 0.9004 | 8.232 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98029 | 0.79996 | 18.033 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97659 | 0.79306 | 18.352 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97659 | 0.88811 | 8.848 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98036 | 0.89472 | 8.564 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98379 | 0.90136 | 8.243 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97843 | 0.79229 | 18.613 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97503 | 0.78156 | 19.347 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97503 | 0.79377 | 18.126 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98455 | 0.76397 | 22.058 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.964 | 0.73548 | 22.851 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.964 | 0.75782 | 20.617 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.964 | 0.76842 | 19.557 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.964 | 0.79526 | 16.874 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97653 | 0.8638 | 11.273 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97645 | 0.74859 | 22.786 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9845 | 0.79072 | 19.378 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97911 | 0.79663 | 18.248 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97626 | 0.75912 | 21.714 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97626 | 0.76019 | 21.607 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98747 | 0.79153 | 19.594 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98747 | 0.89721 | 9.026 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97233 | 0.77839 | 19.393 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97233 | 0.78961 | 18.272 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98302 | 0.87788 | 10.513 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97927 | 0.89905 | 8.022 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97927 | 0.89905 | 8.022 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98254 | 0.89923 | 8.331 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97952 | 0.88185 | 9.767 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97842 | 0.88504 | 9.338 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97826 | 0.88562 | 9.264 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97857 | 0.78847 | 19.01 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97857 | 0.88902 | 8.955 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98037 | 0.79421 | 18.617 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97987 | 0.79711 | 18.276 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98175 | 0.88533 | 9.642 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98099 | 0.89324 | 8.776 | Yes
Active | 2025W1-N11-WVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97968 | 0.7961 | 18.358 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.85458 | 14.59 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.85464 | 14.672 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.85504 | 14.57 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.84622 | 15.562 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99098 | 0.7987 | 19.228 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99098 | 0.80967 | 18.131 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99098 | 0.81503 | 17.595 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99098 | 0.82748 | 16.35 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99098 | 0.84267 | 14.831 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99098 | 0.84363 | 14.736 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99098 | 0.84496 | 14.602 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99098 | 0.90667 | 8.431 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.83231 | 17.082 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.84813 | 15.234 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.84852 | 15.221 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.85163 | 14.891 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99243 | 0.83777 | 15.466 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.84824 | 15.183 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99847 | 0.83641 | 16.205 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99847 | 0.84877 | 14.97 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.82176 | 18.06 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99311 | 0.79656 | 19.655 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99311 | 0.81171 | 18.14 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99311 | 0.83673 | 15.639 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99311 | 0.85306 | 14.005 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.9153 | 8.542 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99843 | 0.80503 | 19.34 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.84621 | 15.705 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99963 | 0.8514 | 14.823 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99786 | 0.81415 | 18.37 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99786 | 0.8146 | 18.326 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.84348 | 15.993 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99753 | 0.83645 | 16.108 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99753 | 0.84768 | 14.985 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.84487 | 15.575 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.8499 | 15.139 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.85405 | 14.713 | Yes
Active | 2025W1-N11-WVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.85315 | 14.793 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97788 | 0.88232 | 9.556 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97734 | 0.88136 | 9.598 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97681 | 0.88013 | 9.668 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97734 | 0.88464 | 9.271 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96649 | 0.83503 | 13.146 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96649 | 0.83878 | 12.77 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96649 | 0.86 | 10.649 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96649 | 0.86078 | 10.571 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96649 | 0.87038 | 9.61 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96649 | 0.874 | 9.249 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96649 | 0.87706 | 8.943 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97942 | 0.85941 | 12.001 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97964 | 0.88935 | 9.029 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97972 | 0.88921 | 9.051 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97761 | 0.8813 | 9.631 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97559 | 0.87725 | 9.835 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97631 | 0.87789 | 9.842 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97426 | 0.87171 | 10.255 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97426 | 0.87225 | 10.202 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97864 | 0.8561 | 12.254 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96685 | 0.8244 | 14.245 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96685 | 0.83836 | 12.849 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96685 | 0.86439 | 10.246 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96685 | 0.87446 | 9.239 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97307 | 0.86701 | 10.606 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9796 | 0.88197 | 9.763 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97741 | 0.88069 | 9.672 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95969 | 0.82829 | 13.139 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95969 | 0.83825 | 12.144 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97525 | 0.86261 | 11.264 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97221 | 0.86965 | 10.256 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97221 | 0.8697 | 10.251 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97657 | 0.88426 | 9.231 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97959 | 0.88924 | 9.035 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97688 | 0.88033 | 9.656 | Yes
Active | 2025W1-N11-WVD245977 | 245977 | 05GRISTMILL | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97676 | 0.87999 | 9.677 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.90309 | 9.819 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.90214 | 9.862 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.90078 | 9.937 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90557 | 9.532 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98998 | 0.85399 | 13.599 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98998 | 0.85871 | 13.127 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98998 | 0.87978 | 11.02 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98998 | 0.88131 | 10.866 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98998 | 0.89129 | 9.869 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98998 | 0.89505 | 9.493 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98998 | 0.89811 | 9.187 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0028 | 0.87965 | 12.32 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.91034 | 9.282 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.9102 | 9.305 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.90202 | 9.899 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99894 | 0.89782 | 10.112 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9997 | 0.89856 | 10.115 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99766 | 0.89226 | 10.539 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99766 | 0.89282 | 10.483 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.87611 | 12.593 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99038 | 0.84304 | 14.734 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99038 | 0.85826 | 13.212 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99038 | 0.88515 | 10.523 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99038 | 0.89552 | 9.486 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.88747 | 10.89 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.90274 | 10.029 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.90142 | 9.938 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98535 | 0.85002 | 13.534 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98535 | 0.86028 | 12.507 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99851 | 0.88246 | 11.605 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99564 | 0.89025 | 10.538 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.8903 | 10.534 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.90519 | 9.493 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.91022 | 9.289 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90108 | 9.922 | Yes
Active | 2025W1-N11-WVD245983 | 245983 | 05GRISTMILL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.90074 | 9.944 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.89976 | 9.838 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.89883 | 9.881 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.997 | 0.89742 | 9.958 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99785 | 0.90229 | 9.556 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98712 | 0.85037 | 13.675 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98712 | 0.85553 | 13.158 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98712 | 0.87613 | 11.099 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98712 | 0.87819 | 10.892 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98712 | 0.88825 | 9.887 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98712 | 0.89204 | 9.507 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98712 | 0.89506 | 9.205 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99969 | 0.87632 | 12.338 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.90702 | 9.304 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.90688 | 9.326 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99788 | 0.89867 | 9.921 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9958 | 0.89444 | 10.136 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99658 | 0.89523 | 10.135 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.88895 | 10.562 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99457 | 0.88951 | 10.506 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99889 | 0.87269 | 12.62 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98753 | 0.83939 | 14.815 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98753 | 0.85508 | 13.245 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98753 | 0.88211 | 10.542 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98753 | 0.89251 | 9.502 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99324 | 0.88418 | 10.906 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99989 | 0.89942 | 10.047 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99767 | 0.89809 | 9.958 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98422 | 0.84839 | 13.583 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98422 | 0.8587 | 12.553 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.87882 | 11.651 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99261 | 0.88701 | 10.56 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99261 | 0.88705 | 10.556 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99708 | 0.90192 | 9.516 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.9069 | 9.311 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99718 | 0.89777 | 9.942 | Yes
Active | 2025W1-N11-WVD245994 | 245994 | 05GEMINI | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.89743 | 9.963 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.88737 | 11.77 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.88436 | 12.155 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.88417 | 12.13 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.87692 | 12.921 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99665 | 0.83453 | 16.212 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99665 | 0.84375 | 15.29 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99665 | 0.8492 | 14.745 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99665 | 0.85926 | 13.74 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99665 | 0.87156 | 12.51 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99665 | 0.8724 | 12.425 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99665 | 0.87379 | 12.286 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0069 | 0.86805 | 13.881 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87876 | 12.659 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.87908 | 12.643 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.88089 | 12.326 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99586 | 0.86345 | 13.241 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.87968 | 12.548 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.86688 | 13.63 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0032 | 0.87667 | 12.651 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.85591 | 15.008 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9998 | 0.83383 | 16.597 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9998 | 0.84605 | 15.374 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9998 | 0.87139 | 12.84 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9998 | 0.88169 | 11.81 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.84129 | 16.238 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.87729 | 12.995 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.88544 | 11.918 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.84825 | 15.526 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.8499 | 15.361 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.87389 | 13.302 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.86855 | 13.467 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0032 | 0.87739 | 12.583 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.87585 | 12.955 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.88024 | 12.561 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.88377 | 12.201 | Yes
Active | 2025W1-N11-WVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.88306 | 12.267 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92821 | 8.075 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.83605 | 16.976 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.83597 | 17.092 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.8371 | 16.886 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.82548 | 18.252 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.9162 | 8.917 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98906 | 0.7758 | 21.325 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98906 | 0.78642 | 20.264 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98906 | 0.79413 | 19.492 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98906 | 0.80547 | 18.359 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98906 | 0.81855 | 17.051 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98906 | 0.81884 | 17.021 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98906 | 0.82478 | 16.428 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98906 | 0.9037 | 8.535 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98906 | 0.9048 | 8.425 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0098 | 0.81187 | 19.798 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.8271 | 17.81 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.82762 | 17.804 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.8383 | 16.797 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.82831 | 17.404 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.91971 | 8.265 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.82953 | 17.539 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.81326 | 18.843 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.8263 | 17.539 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.80187 | 20.643 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.77519 | 21.879 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99397 | 0.79161 | 20.237 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99397 | 0.81592 | 17.805 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99397 | 0.83122 | 16.275 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.90661 | 10.03 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.78376 | 21.845 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.01 | 0.82811 | 18.191 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.83215 | 17.236 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.79343 | 20.84 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.79479 | 20.704 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0103 | 0.82533 | 18.494 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0103 | 0.92659 | 8.368 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.8141 | 18.603 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.8257 | 17.443 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.91591 | 9.268 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.9162 | 8.917 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.92743 | 8.111 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.92793 | 8.059 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.82361 | 18.217 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0058 | 0.92293 | 8.285 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.82938 | 17.728 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.83529 | 17.129 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0084 | 0.92066 | 8.776 | Yes
Active | 2025W1-N11-WVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.83418 | 17.223 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99895 | 0.91036 | 8.859 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99856 | 0.81716 | 18.141 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.81306 | 18.58 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.81604 | 18.169 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.80234 | 19.929 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9911 | 0.89305 | 9.805 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98438 | 0.75519 | 22.919 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98438 | 0.76863 | 21.575 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98438 | 0.7757 | 20.868 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98438 | 0.78654 | 19.784 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98438 | 0.79657 | 18.781 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98438 | 0.80248 | 18.191 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98438 | 0.80749 | 17.689 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98438 | 0.89194 | 9.244 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98438 | 0.89663 | 8.775 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0028 | 0.78428 | 21.854 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99636 | 0.80226 | 19.409 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99707 | 0.80294 | 19.413 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.91932 | 8.145 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.81823 | 18.047 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99522 | 0.81078 | 18.444 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99522 | 0.9098 | 8.542 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.999 | 0.91712 | 8.189 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.80759 | 18.872 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99387 | 0.79527 | 19.86 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99387 | 0.80728 | 18.658 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.78104 | 22.112 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.75482 | 23.488 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9897 | 0.77263 | 21.707 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9897 | 0.79065 | 19.905 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9897 | 0.8088 | 18.09 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.88658 | 10.94 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.76399 | 23.003 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.80821 | 19.4 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99737 | 0.81357 | 18.38 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99553 | 0.77205 | 22.348 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.77432 | 22.121 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.80642 | 19.825 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.91644 | 8.823 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99179 | 0.79052 | 20.126 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99179 | 0.80102 | 19.077 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.9011 | 10.022 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9911 | 0.89305 | 9.805 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91311 | 8.702 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91367 | 8.64 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99804 | 0.79965 | 19.84 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99804 | 0.90836 | 8.968 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99859 | 0.80502 | 19.357 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99853 | 0.81269 | 18.584 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.90697 | 9.348 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99959 | 0.91555 | 8.405 | Yes
Active | 2025W1-N11-WVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99826 | 0.81123 | 18.703 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99416 | 0.90217 | 9.199 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9938 | 0.90112 | 9.268 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.90018 | 9.302 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.90098 | 9.303 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98514 | 0.85416 | 13.098 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98514 | 0.8605 | 12.464 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98514 | 0.87744 | 10.77 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98514 | 0.88252 | 10.262 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98514 | 0.89492 | 9.022 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98514 | 0.89711 | 8.803 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98514 | 0.89928 | 8.586 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99545 | 0.87954 | 11.591 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.90398 | 9.068 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.90397 | 9.081 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.90034 | 9.343 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.8961 | 9.549 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99286 | 0.89784 | 9.503 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.89224 | 9.9 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99123 | 0.89232 | 9.891 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.87589 | 11.892 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98512 | 0.84264 | 14.248 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98512 | 0.85973 | 12.539 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98512 | 0.88614 | 9.898 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98512 | 0.89684 | 8.828 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99015 | 0.88982 | 10.033 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99567 | 0.90229 | 9.338 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99375 | 0.90063 | 9.312 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97199 | 0.84696 | 12.503 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97199 | 0.85737 | 11.462 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98981 | 0.8797 | 11.012 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9902 | 0.89089 | 9.931 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.89131 | 9.889 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.90063 | 9.269 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.90428 | 9.062 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.90041 | 9.311 | Yes
Active | 2025W1-N11-WVD246155 | 246155 | 05FORD LIMA2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99344 | 0.90004 | 9.34 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.91446 | 8.235 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.91446 | 8.235 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99638 | 0.90509 | 9.129 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.89362 | 10.038 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.79258 | 19.998 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.91447 | 8.128 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99379 | 0.90581 | 8.798 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99323 | 0.79186 | 20.136 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.79323 | 19.882 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.78286 | 21.142 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.88506 | 10.689 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.91293 | 8.084 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96814 | 0.7274 | 24.074 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96814 | 0.74262 | 22.552 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96814 | 0.75512 | 21.302 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96814 | 0.76016 | 20.798 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96814 | 0.77672 | 19.142 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96814 | 0.86791 | 10.023 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96814 | 0.87496 | 9.318 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99738 | 0.75668 | 24.071 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99652 | 0.90684 | 8.968 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98502 | 0.89372 | 9.13 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99311 | 0.91231 | 8.08 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99143 | 0.78446 | 20.697 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99143 | 0.90805 | 8.338 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.7849 | 20.704 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.9018 | 9.327 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99563 | 0.90584 | 8.979 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9957 | 0.90584 | 8.986 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99263 | 0.79422 | 19.841 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99623 | 0.91066 | 8.557 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98908 | 0.787 | 20.208 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98908 | 0.89366 | 9.543 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.89953 | 9.363 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.90608 | 9.004 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99084 | 0.78533 | 20.551 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99084 | 0.90502 | 8.582 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98813 | 0.77514 | 21.299 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98813 | 0.78932 | 19.881 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.75642 | 24.07 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97512 | 0.72702 | 24.81 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97512 | 0.75477 | 22.034 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97512 | 0.76145 | 21.367 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97512 | 0.79138 | 18.373 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.8681 | 12.237 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9905 | 0.73971 | 25.08 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.90657 | 8.741 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.78086 | 21.608 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.91068 | 8.431 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.78892 | 20.226 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.75556 | 23.546 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99102 | 0.75608 | 23.494 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.78608 | 21.512 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0012 | 0.90428 | 9.691 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98539 | 0.7727 | 21.269 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98539 | 0.78584 | 19.955 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99687 | 0.91437 | 8.25 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.88141 | 11.442 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.90996 | 8.523 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98768 | 0.8994 | 8.828 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98768 | 0.8994 | 8.828 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99552 | 0.9046 | 9.092 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.90928 | 8.552 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99014 | 0.90694 | 8.32 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99014 | 0.90694 | 8.32 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.88506 | 10.689 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.89661 | 9.821 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.89719 | 9.759 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.9123 | 8.342 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.78126 | 21.055 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99182 | 0.89469 | 9.713 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99305 | 0.78644 | 20.661 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.90931 | 8.578 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.79133 | 20.157 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.88995 | 10.496 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.89843 | 9.572 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99544 | 0.91186 | 8.357 | Yes
Active | 2025W1-N11-WVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99271 | 0.79025 | 20.246 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.85868 | 14.338 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.85839 | 14.457 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.85871 | 14.364 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.84992 | 15.35 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99209 | 0.80288 | 18.921 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99209 | 0.81353 | 17.856 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99209 | 0.81898 | 17.311 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99209 | 0.83116 | 16.093 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99209 | 0.84588 | 14.621 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99209 | 0.8461 | 14.599 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99209 | 0.84816 | 14.392 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99209 | 0.90901 | 8.308 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.837 | 16.772 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.85184 | 15.022 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.85223 | 15.009 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.85558 | 14.643 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99416 | 0.84156 | 15.26 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.85261 | 14.909 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99967 | 0.83943 | 16.024 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99967 | 0.8513 | 14.838 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.826 | 17.773 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99443 | 0.80108 | 19.335 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99443 | 0.81556 | 17.887 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99443 | 0.84118 | 15.325 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99443 | 0.85613 | 13.83 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.91871 | 8.406 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.80942 | 19.041 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.85022 | 15.468 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.85563 | 14.561 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9993 | 0.81798 | 18.132 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9993 | 0.81887 | 18.043 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.84714 | 15.769 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99899 | 0.84019 | 15.879 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99899 | 0.85094 | 14.805 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.84858 | 15.362 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.8536 | 14.927 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.85777 | 14.5 | Yes
Active | 2025W1-N11-WVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.85689 | 14.578 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.92388 | 8.108 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.92248 | 8.205 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.91788 | 8.686 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99691 | 0.89438 | 10.253 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99691 | 0.89508 | 10.183 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99691 | 0.89814 | 9.876 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99691 | 0.90979 | 8.712 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99691 | 0.91103 | 8.588 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99691 | 0.9117 | 8.521 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99691 | 0.91442 | 8.248 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0062 | 0.91585 | 9.033 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.91971 | 8.461 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.9199 | 8.457 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.91651 | 8.579 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99827 | 0.9083 | 8.998 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99827 | 0.9122 | 8.608 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.90796 | 9.579 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99639 | 0.89235 | 10.404 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99639 | 0.89374 | 10.265 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.89728 | 10.387 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.91987 | 8.661 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.89549 | 10.519 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.89728 | 10.341 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.9131 | 9.177 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.91231 | 8.927 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.9164 | 8.518 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91728 | 8.682 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.92065 | 8.415 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.92301 | 8.169 | Yes
Active | 2025W1-N11-WVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.92268 | 8.197 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9864 | 0.90233 | 8.407 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9843 | 0.89221 | 9.209 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98288 | 0.79967 | 18.32 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98269 | 0.90023 | 8.247 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98348 | 0.79919 | 18.429 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98241 | 0.80058 | 18.184 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98455 | 0.79011 | 19.445 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98233 | 0.88409 | 9.824 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96026 | 0.73405 | 22.621 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96026 | 0.74881 | 21.145 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96026 | 0.76138 | 19.888 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96026 | 0.76724 | 19.302 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96026 | 0.78379 | 17.647 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98725 | 0.76506 | 22.219 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98654 | 0.90398 | 8.255 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97846 | 0.8953 | 8.316 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98179 | 0.79164 | 19.015 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98227 | 0.7921 | 19.017 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98522 | 0.89934 | 8.588 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98573 | 0.90305 | 8.267 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9858 | 0.90305 | 8.275 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98274 | 0.80154 | 18.12 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97971 | 0.79442 | 18.528 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97971 | 0.89181 | 8.79 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98347 | 0.89729 | 8.618 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98617 | 0.90327 | 8.29 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98134 | 0.79254 | 18.88 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97894 | 0.78227 | 19.667 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97894 | 0.79638 | 18.255 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.76354 | 22.332 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96675 | 0.73367 | 23.308 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96675 | 0.76085 | 20.59 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96675 | 0.76978 | 19.697 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96675 | 0.7983 | 16.845 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98112 | 0.86901 | 11.211 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98047 | 0.74593 | 23.454 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98444 | 0.90428 | 8.016 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98685 | 0.78843 | 19.842 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98152 | 0.79592 | 18.56 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9809 | 0.76186 | 21.904 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9809 | 0.76221 | 21.869 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.79287 | 19.76 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99047 | 0.90084 | 8.963 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97614 | 0.77977 | 19.637 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97614 | 0.79282 | 18.332 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98565 | 0.88078 | 10.487 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98052 | 0.89952 | 8.1 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98052 | 0.89952 | 8.1 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.9019 | 8.373 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98233 | 0.88409 | 9.824 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98496 | 0.89459 | 9.037 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98493 | 0.89513 | 8.98 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98222 | 0.78845 | 19.377 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98222 | 0.89265 | 8.957 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98331 | 0.79366 | 18.966 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98318 | 0.79867 | 18.451 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98506 | 0.88846 | 9.66 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98434 | 0.89623 | 8.811 | Yes
Active | 2025W1-N11-WVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.983 | 0.79758 | 18.542 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0058 | 0.89633 | 10.948 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0058 | 0.90826 | 9.755 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0058 | 0.91196 | 9.385 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0058 | 0.92577 | 8.004 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0107 | 0.92307 | 8.758 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.91988 | 9.071 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.90224 | 10.261 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.90861 | 9.625 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98802 | 0.9046 | 8.343 | Yes
Active | 2025W1-N11-WVD246352 | 246352 | 05HAVILAND2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99897 | 0.90544 | 9.353 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98288 | 0.88575 | 9.713 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98288 | 0.89216 | 9.072 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98288 | 0.90135 | 8.153 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98853 | 0.90526 | 8.327 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9881 | 0.90195 | 8.615 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98293 | 0.87695 | 10.599 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98293 | 0.89153 | 9.141 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97422 | 0.88332 | 9.09 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97422 | 0.89113 | 8.309 | Yes
Active | 2025W1-N11-WVD246354 | 246354 | 05E.LEIPSIC1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98487 | 0.90396 | 8.091 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.90913 | 8.284 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98821 | 0.89507 | 9.314 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98847 | 0.80358 | 18.489 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98878 | 0.80035 | 18.844 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98764 | 0.80278 | 18.486 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9909 | 0.79043 | 20.047 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98377 | 0.8838 | 9.997 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97075 | 0.7401 | 23.065 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97075 | 0.75523 | 21.553 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97075 | 0.76415 | 20.66 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97075 | 0.77238 | 19.838 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97075 | 0.78482 | 18.593 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97075 | 0.87782 | 9.293 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97075 | 0.88276 | 8.8 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99287 | 0.76823 | 22.464 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.91059 | 8.154 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98696 | 0.90561 | 8.135 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98656 | 0.79104 | 19.552 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98719 | 0.79161 | 19.558 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99064 | 0.9058 | 8.484 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.90963 | 8.155 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99125 | 0.90963 | 8.162 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98861 | 0.80471 | 18.391 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9851 | 0.79742 | 18.768 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9851 | 0.8968 | 8.83 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.90359 | 8.524 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99173 | 0.90985 | 8.188 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98636 | 0.7949 | 19.146 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98375 | 0.78362 | 20.014 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98375 | 0.79572 | 18.804 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.7672 | 22.538 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97638 | 0.73974 | 23.665 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97638 | 0.76161 | 21.477 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97638 | 0.77439 | 20.199 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97638 | 0.79728 | 17.91 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98561 | 0.87267 | 11.294 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98463 | 0.75091 | 23.373 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99198 | 0.79484 | 19.714 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.80005 | 18.722 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98601 | 0.76143 | 22.458 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98601 | 0.76317 | 22.284 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99577 | 0.79471 | 20.105 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99577 | 0.90513 | 9.064 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98128 | 0.77927 | 20.201 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98128 | 0.7901 | 19.118 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.88717 | 10.413 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.90843 | 8.263 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98377 | 0.8838 | 9.997 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.89979 | 9.026 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99 | 0.90036 | 8.965 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98773 | 0.78818 | 19.955 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98773 | 0.89594 | 9.178 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98856 | 0.79346 | 19.51 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98845 | 0.79993 | 18.853 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9904 | 0.89381 | 9.658 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98956 | 0.90219 | 8.737 | Yes
Active | 2025W1-N11-WVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98822 | 0.79862 | 18.959 | Yes
Active | 2025W1-N11-WVD246373 | 246373 | 05SPY RUN1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99309 | 0.87897 | 11.412 | Yes
Active | 2025W1-N11-WVD246373 | 246373 | 05SPY RUN1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99131 | 0.91082 | 8.049 | Yes
Active | 2025W1-N11-WVD246373 | 246373 | 05SPY RUN1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97278 | 0.89276 | 8.002 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.91554 | 8.041 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.91554 | 8.041 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.90643 | 8.911 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.8951 | 9.806 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.7969 | 19.492 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9931 | 0.90726 | 8.583 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99245 | 0.7961 | 19.635 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9913 | 0.79751 | 19.379 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.78702 | 20.646 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.88676 | 10.437 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96795 | 0.73143 | 23.652 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96795 | 0.74691 | 22.103 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96795 | 0.75945 | 20.85 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96795 | 0.76428 | 20.367 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96795 | 0.78086 | 18.708 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96795 | 0.87026 | 9.769 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96795 | 0.87717 | 9.078 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99655 | 0.76036 | 23.619 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99568 | 0.90809 | 8.759 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98363 | 0.89442 | 8.921 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.78863 | 20.206 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99069 | 0.90925 | 8.144 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.78907 | 20.211 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.90319 | 9.106 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99479 | 0.90712 | 8.767 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.90712 | 8.774 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99188 | 0.79854 | 19.334 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.91182 | 8.356 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98842 | 0.79126 | 19.716 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98842 | 0.89532 | 9.311 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99237 | 0.90096 | 9.142 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.90734 | 8.794 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.78956 | 20.054 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9901 | 0.9063 | 8.38 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98742 | 0.7793 | 20.813 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98742 | 0.79355 | 19.388 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.76051 | 23.583 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97476 | 0.73105 | 24.371 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97476 | 0.75909 | 21.567 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97476 | 0.76519 | 20.957 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97476 | 0.79564 | 17.912 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98969 | 0.87026 | 11.943 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.74397 | 24.592 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99326 | 0.90795 | 8.531 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99608 | 0.78507 | 21.101 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.91184 | 8.234 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.79322 | 19.725 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99044 | 0.75986 | 23.058 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99044 | 0.76036 | 23.008 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.79047 | 20.99 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.90577 | 9.46 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98479 | 0.77681 | 20.798 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98479 | 0.79001 | 19.478 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.91545 | 8.058 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.88337 | 11.162 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.91121 | 8.319 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98627 | 0.90002 | 8.625 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98627 | 0.90002 | 8.625 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.9059 | 8.878 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.91044 | 8.354 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.90825 | 8.125 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.90826 | 8.124 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.88676 | 10.437 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.8981 | 9.59 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.89867 | 9.53 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.91341 | 8.148 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.78541 | 20.565 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99106 | 0.89623 | 9.483 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.79063 | 20.165 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.91051 | 8.377 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.79557 | 19.656 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.89164 | 10.246 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.89989 | 9.346 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.91299 | 8.162 | Yes
Active | 2025W1-N11-WVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.79448 | 19.747 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99822 | 0.91448 | 8.374 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99243 | 0.88562 | 10.682 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99243 | 0.89092 | 10.151 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99243 | 0.89449 | 9.794 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99243 | 0.90265 | 8.978 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99243 | 0.91088 | 8.156 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99243 | 0.91169 | 8.075 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99243 | 0.91236 | 8.008 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99831 | 0.91056 | 8.776 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99807 | 0.91594 | 8.213 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.91611 | 8.199 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99656 | 0.91041 | 8.615 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99789 | 0.91582 | 8.207 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99748 | 0.90939 | 8.809 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99748 | 0.91401 | 8.348 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99805 | 0.90046 | 9.758 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.8854 | 11.058 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99598 | 0.88979 | 10.619 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99598 | 0.9129 | 8.308 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.88948 | 10.803 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99858 | 0.91375 | 8.483 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99758 | 0.89166 | 10.592 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99758 | 0.89513 | 10.245 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99843 | 0.91093 | 8.75 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9975 | 0.90924 | 8.826 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9975 | 0.9136 | 8.39 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.91394 | 8.412 | Yes
Active | 2025W1-N11-WVD246399 | 246399 | 05GLOBE MT Z | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.9168 | 8.139 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99754 | 0.9145 | 8.303 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99194 | 0.88574 | 10.62 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99194 | 0.89121 | 10.073 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99194 | 0.8948 | 9.714 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99194 | 0.9027 | 8.924 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99194 | 0.91103 | 8.091 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99194 | 0.91175 | 8.019 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99763 | 0.91033 | 8.73 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99738 | 0.91594 | 8.143 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99741 | 0.91612 | 8.13 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.90981 | 8.567 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99718 | 0.91578 | 8.14 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.90938 | 8.738 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99676 | 0.91358 | 8.318 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99733 | 0.90048 | 9.685 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.88553 | 10.966 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99519 | 0.88957 | 10.562 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99519 | 0.91271 | 8.249 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.88973 | 10.706 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99789 | 0.91381 | 8.408 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99693 | 0.89141 | 10.552 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.89539 | 10.154 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99778 | 0.91103 | 8.674 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.90928 | 8.751 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99679 | 0.91321 | 8.358 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99737 | 0.91396 | 8.341 | Yes
Active | 2025W1-N11-WVD246481 | 246481 | 05NMUSKG_BP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9975 | 0.9168 | 8.07 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98925 | 0.88608 | 10.317 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98925 | 0.8921 | 9.715 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98925 | 0.8957 | 9.356 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98925 | 0.90262 | 8.663 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99427 | 0.90927 | 8.5 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.90719 | 8.35 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99328 | 0.909 | 8.428 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99328 | 0.91177 | 8.151 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99387 | 0.90028 | 9.359 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99151 | 0.88588 | 10.563 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99151 | 0.88867 | 10.284 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.89047 | 10.288 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.91366 | 8.085 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99371 | 0.89038 | 10.333 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.8961 | 9.761 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99454 | 0.91107 | 8.346 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99332 | 0.90909 | 8.423 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99332 | 0.91152 | 8.18 | Yes
Active | 2025W1-N11-WVD246490 | 246490 | 05PHILO_BP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.91367 | 8.031 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98501 | 0.90455 | 8.046 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98159 | 0.89133 | 9.026 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98191 | 0.80953 | 17.237 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98204 | 0.80737 | 17.467 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98097 | 0.80883 | 17.213 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98294 | 0.7986 | 18.434 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98133 | 0.88739 | 9.394 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95994 | 0.74157 | 21.837 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95994 | 0.75999 | 19.995 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95994 | 0.77025 | 18.969 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95994 | 0.77596 | 18.399 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95994 | 0.79244 | 16.75 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.95994 | 0.87938 | 8.057 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98599 | 0.76988 | 21.611 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98039 | 0.80033 | 18.006 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98087 | 0.80077 | 18.011 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98364 | 0.90122 | 8.242 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98201 | 0.81025 | 17.177 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9786 | 0.80349 | 17.511 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9786 | 0.8934 | 8.52 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98223 | 0.89966 | 8.256 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98474 | 0.90464 | 8.01 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97991 | 0.80189 | 17.802 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97714 | 0.79163 | 18.552 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97714 | 0.80323 | 17.392 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98642 | 0.77171 | 21.471 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96523 | 0.74116 | 22.408 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96523 | 0.7676 | 19.763 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96523 | 0.77522 | 19.001 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96523 | 0.80451 | 16.072 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97846 | 0.87047 | 10.799 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97661 | 0.75674 | 21.987 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98515 | 0.80202 | 18.313 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98084 | 0.80632 | 17.452 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97967 | 0.76873 | 21.093 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97967 | 0.77051 | 20.915 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99015 | 0.80266 | 18.75 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99015 | 0.90322 | 8.694 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97449 | 0.78812 | 18.637 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97449 | 0.79876 | 17.573 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98471 | 0.88406 | 10.065 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98406 | 0.90362 | 8.043 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98133 | 0.88739 | 9.394 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98329 | 0.89605 | 8.724 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98324 | 0.89657 | 8.667 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9806 | 0.79695 | 18.365 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9806 | 0.89331 | 8.729 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9819 | 0.80228 | 17.962 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98173 | 0.80687 | 17.486 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98357 | 0.89092 | 9.266 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98285 | 0.89828 | 8.457 | Yes
Active | 2025W1-N11-WVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98155 | 0.8058 | 17.575 | Yes
Active | 2025W1-N11-WVD246526 | 246526 | 05GUERNSEY | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9774 | 0.88745 | 8.995 | Yes
Active | 2025W1-N11-WVD246526 | 246526 | 05GUERNSEY | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97044 | 0.85644 | 11.4 | Yes
Active | 2025W1-N11-WVD246526 | 246526 | 05GUERNSEY | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97799 | 0.85802 | 11.997 | Yes
Active | 2025W1-N11-WVD246526 | 246526 | 05GUERNSEY | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97695 | 0.88662 | 9.033 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99239 | 0.90492 | 8.747 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.8141 | 17.819 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99248 | 0.80936 | 18.312 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.81266 | 17.872 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9956 | 0.79862 | 19.697 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.89122 | 9.59 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97717 | 0.75297 | 22.42 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97717 | 0.76614 | 21.103 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97717 | 0.77214 | 20.503 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97717 | 0.78388 | 19.329 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97717 | 0.79277 | 18.44 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97717 | 0.79987 | 17.73 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97717 | 0.80396 | 17.321 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97717 | 0.88737 | 8.98 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97717 | 0.89177 | 8.54 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99636 | 0.78198 | 21.438 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.79814 | 19.175 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.79884 | 19.179 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.91363 | 8.078 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.81505 | 17.737 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98906 | 0.80781 | 18.125 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98906 | 0.90423 | 8.483 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.91138 | 8.123 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99 | 0.80459 | 18.54 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98787 | 0.79265 | 19.523 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98787 | 0.80417 | 18.37 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.77833 | 21.725 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.75259 | 22.958 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98217 | 0.76868 | 21.349 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98217 | 0.78835 | 19.381 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98217 | 0.80451 | 17.765 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9896 | 0.88135 | 10.824 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98741 | 0.76144 | 22.597 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99584 | 0.80558 | 19.027 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.81062 | 18.053 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98777 | 0.76799 | 21.978 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98777 | 0.77065 | 21.712 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99782 | 0.80278 | 19.503 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99782 | 0.90995 | 8.786 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98449 | 0.78666 | 19.784 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98449 | 0.79674 | 18.775 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99489 | 0.89578 | 9.911 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.89122 | 9.59 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.90704 | 8.655 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99354 | 0.90759 | 8.594 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99183 | 0.79574 | 19.609 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99183 | 0.90229 | 8.953 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99222 | 0.80099 | 19.122 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.80905 | 18.311 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99405 | 0.90135 | 9.27 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99315 | 0.90978 | 8.337 | Yes
Active | 2025W1-N11-WVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99188 | 0.80754 | 18.434 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96359 | 0.88096 | 8.264 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96164 | 0.87026 | 9.138 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96085 | 0.79133 | 16.952 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96117 | 0.79034 | 17.083 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96011 | 0.79117 | 16.894 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96138 | 0.7823 | 17.908 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96144 | 0.86607 | 9.537 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9329 | 0.71591 | 21.698 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9329 | 0.74168 | 19.122 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9329 | 0.75396 | 17.894 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9329 | 0.75778 | 17.511 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9329 | 0.77643 | 15.647 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96507 | 0.73902 | 22.606 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96366 | 0.88147 | 8.219 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96154 | 0.88004 | 8.151 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95999 | 0.78453 | 17.546 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96032 | 0.78486 | 17.546 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9626 | 0.87791 | 8.468 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96296 | 0.88109 | 8.187 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96301 | 0.88111 | 8.191 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96088 | 0.79236 | 16.852 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95819 | 0.78596 | 17.223 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95819 | 0.87667 | 8.152 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96021 | 0.87474 | 8.547 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96331 | 0.88076 | 8.255 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95916 | 0.78457 | 17.46 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95654 | 0.77502 | 18.152 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95654 | 0.79618 | 16.036 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96523 | 0.75017 | 21.506 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94087 | 0.71568 | 22.518 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.94087 | 0.74482 | 19.604 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.94087 | 0.76202 | 17.884 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.94087 | 0.7987 | 14.216 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95787 | 0.84784 | 11.003 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96392 | 0.7386 | 22.532 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96479 | 0.77054 | 19.425 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95995 | 0.78828 | 17.167 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96263 | 0.75856 | 20.407 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96263 | 0.76362 | 19.901 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97067 | 0.7889 | 18.177 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97067 | 0.88799 | 8.267 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95489 | 0.77284 | 18.205 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95489 | 0.79359 | 16.13 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96306 | 0.86136 | 10.17 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96064 | 0.88004 | 8.06 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96064 | 0.88004 | 8.06 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96284 | 0.88003 | 8.281 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96144 | 0.86607 | 9.537 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9627 | 0.87395 | 8.875 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96268 | 0.87444 | 8.824 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9598 | 0.78111 | 17.868 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9598 | 0.87708 | 8.272 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96107 | 0.78616 | 17.491 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96091 | 0.7898 | 17.111 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96253 | 0.8683 | 9.422 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96187 | 0.87494 | 8.693 | Yes
Active | 2025W1-N11-WVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96079 | 0.78891 | 17.189 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98749 | 0.9034 | 8.409 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98514 | 0.89221 | 9.293 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98412 | 0.80389 | 18.023 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98589 | 0.90517 | 8.072 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98463 | 0.80295 | 18.168 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98352 | 0.80417 | 17.934 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98533 | 0.79412 | 19.122 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.984 | 0.88602 | 9.798 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96028 | 0.735 | 22.529 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96028 | 0.7533 | 20.699 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96028 | 0.76726 | 19.302 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96028 | 0.76987 | 19.042 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96028 | 0.78794 | 17.235 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98871 | 0.76222 | 22.648 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98767 | 0.90468 | 8.299 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9837 | 0.90121 | 8.25 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98308 | 0.796 | 18.707 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98352 | 0.79642 | 18.71 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98627 | 0.90024 | 8.602 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98676 | 0.90385 | 8.291 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98683 | 0.90385 | 8.297 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98423 | 0.80525 | 17.898 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98094 | 0.7982 | 18.274 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98094 | 0.89391 | 8.703 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98439 | 0.89799 | 8.64 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.90395 | 8.333 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98238 | 0.79667 | 18.571 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97965 | 0.78641 | 19.325 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97965 | 0.80168 | 17.798 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98878 | 0.76599 | 22.279 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96686 | 0.73465 | 23.221 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96686 | 0.76747 | 19.939 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96686 | 0.76758 | 19.929 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96686 | 0.80389 | 16.297 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98165 | 0.86914 | 11.251 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9834 | 0.75024 | 23.315 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98552 | 0.9047 | 8.082 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.7903 | 19.8 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98295 | 0.80042 | 18.252 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98391 | 0.76778 | 21.614 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98391 | 0.76896 | 21.495 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99313 | 0.7988 | 19.433 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99313 | 0.90476 | 8.837 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97741 | 0.78393 | 19.349 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97741 | 0.79835 | 17.906 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98708 | 0.88206 | 10.502 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98224 | 0.90092 | 8.132 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98224 | 0.90092 | 8.132 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98665 | 0.9027 | 8.394 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.984 | 0.88602 | 9.798 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98609 | 0.89551 | 9.058 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98606 | 0.89604 | 9.002 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98321 | 0.79262 | 19.059 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98321 | 0.89462 | 8.859 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98448 | 0.7979 | 18.658 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98433 | 0.80241 | 18.192 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98617 | 0.8897 | 9.648 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98548 | 0.89722 | 8.826 | Yes
Active | 2025W1-N11-WVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.80138 | 18.279 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.90317 | 8.411 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98472 | 0.89178 | 9.293 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9838 | 0.80332 | 18.048 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98573 | 0.90532 | 8.041 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98421 | 0.80212 | 18.21 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98314 | 0.80337 | 17.976 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98484 | 0.79347 | 19.136 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98356 | 0.88553 | 9.803 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96034 | 0.73541 | 22.493 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96034 | 0.75307 | 20.727 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96034 | 0.76586 | 19.449 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96034 | 0.76959 | 19.075 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96034 | 0.78703 | 17.332 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98844 | 0.7629 | 22.554 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98745 | 0.90455 | 8.29 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98334 | 0.90094 | 8.24 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98273 | 0.79553 | 18.719 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98317 | 0.79594 | 18.723 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9859 | 0.89989 | 8.601 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9864 | 0.90354 | 8.287 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98648 | 0.90354 | 8.294 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98391 | 0.8044 | 17.951 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98053 | 0.79737 | 18.316 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98053 | 0.89307 | 8.746 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98405 | 0.89771 | 8.634 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98706 | 0.90382 | 8.324 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98205 | 0.79601 | 18.604 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97918 | 0.78564 | 19.354 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97918 | 0.80023 | 17.895 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9884 | 0.76584 | 22.256 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96675 | 0.73511 | 23.164 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96675 | 0.76575 | 20.1 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96675 | 0.76795 | 19.881 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96675 | 0.80229 | 16.447 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98106 | 0.86837 | 11.269 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98239 | 0.75007 | 23.232 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98536 | 0.90496 | 8.04 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98801 | 0.79062 | 19.738 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98265 | 0.7999 | 18.275 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98276 | 0.76641 | 21.635 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98276 | 0.76712 | 21.565 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99244 | 0.79752 | 19.492 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99244 | 0.90356 | 8.888 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97683 | 0.78301 | 19.382 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97683 | 0.79672 | 18.012 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98674 | 0.88156 | 10.517 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98213 | 0.90094 | 8.119 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98213 | 0.90094 | 8.119 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98629 | 0.90238 | 8.391 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98356 | 0.88553 | 9.803 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98496 | 0.89366 | 9.13 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9849 | 0.8942 | 9.07 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98274 | 0.79202 | 19.072 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98274 | 0.89383 | 8.891 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98412 | 0.7974 | 18.672 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9839 | 0.80155 | 18.234 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98575 | 0.88917 | 9.658 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98505 | 0.89678 | 8.826 | Yes
Active | 2025W1-N11-WVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98373 | 0.80053 | 18.32 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99534 | 0.91421 | 8.113 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.82113 | 17.17 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99324 | 0.81776 | 17.548 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.82041 | 17.187 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9957 | 0.80698 | 18.873 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98904 | 0.89741 | 9.163 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9763 | 0.76021 | 21.609 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9763 | 0.77154 | 20.476 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9763 | 0.7779 | 19.84 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9763 | 0.79027 | 18.603 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9763 | 0.79963 | 17.667 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9763 | 0.80423 | 17.207 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9763 | 0.80908 | 16.722 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9763 | 0.88959 | 8.671 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9763 | 0.89352 | 8.278 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99678 | 0.79295 | 20.383 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.80717 | 18.377 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99158 | 0.80781 | 18.377 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.82225 | 17.081 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98962 | 0.81475 | 17.487 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98962 | 0.9076 | 8.202 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.80984 | 18.124 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.79849 | 19.137 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98986 | 0.81079 | 17.907 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99553 | 0.78643 | 20.91 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98123 | 0.75979 | 22.144 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98123 | 0.77476 | 20.647 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98123 | 0.79747 | 18.376 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98123 | 0.81157 | 16.966 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99163 | 0.8886 | 10.303 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9882 | 0.76851 | 21.969 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.81232 | 18.427 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99163 | 0.81754 | 17.409 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98781 | 0.77581 | 21.2 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98781 | 0.77809 | 20.972 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99735 | 0.80948 | 18.786 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99735 | 0.9125 | 8.485 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9856 | 0.79517 | 19.043 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9856 | 0.80559 | 18.001 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.90079 | 9.437 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98904 | 0.89741 | 9.163 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.91217 | 8.254 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.91269 | 8.198 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99246 | 0.80441 | 18.805 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99246 | 0.90683 | 8.564 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.80985 | 18.312 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.81731 | 17.56 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99482 | 0.90571 | 8.911 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.91381 | 8.021 | Yes
Active | 2025W1-N11-WVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99267 | 0.81594 | 17.672 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.91954 | 8.222 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99961 | 0.90967 | 8.994 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99803 | 0.81402 | 18.401 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99863 | 0.81215 | 18.648 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99755 | 0.81422 | 18.332 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.80195 | 19.847 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.89494 | 9.875 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9798 | 0.74998 | 22.981 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9798 | 0.76364 | 21.616 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9798 | 0.77343 | 20.637 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9798 | 0.78213 | 19.767 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9798 | 0.79554 | 18.426 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9798 | 0.79974 | 18.006 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9798 | 0.80476 | 17.503 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9798 | 0.88649 | 9.33 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9798 | 0.89184 | 8.796 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.78135 | 22.11 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.92146 | 8.039 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.91465 | 8.084 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99657 | 0.80289 | 19.369 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99715 | 0.80345 | 19.371 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.91653 | 8.397 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.92037 | 8.066 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.92036 | 8.073 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99817 | 0.81575 | 18.242 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99476 | 0.80805 | 18.671 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99476 | 0.90756 | 8.72 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99876 | 0.9145 | 8.427 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.92075 | 8.073 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99622 | 0.80529 | 19.093 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99396 | 0.79386 | 20.01 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99396 | 0.8072 | 18.676 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.77786 | 22.395 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98569 | 0.74952 | 23.617 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98569 | 0.77158 | 21.41 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98569 | 0.78644 | 19.925 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98569 | 0.80903 | 17.666 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.88534 | 11.097 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.76021 | 23.452 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.80406 | 19.787 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9967 | 0.81018 | 18.652 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99568 | 0.77243 | 22.325 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99568 | 0.77333 | 22.235 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.80496 | 19.982 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0048 | 0.91545 | 8.933 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99166 | 0.79081 | 20.085 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99166 | 0.80268 | 18.898 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.89806 | 10.281 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.91919 | 8.174 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.89494 | 9.875 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91127 | 8.882 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91182 | 8.823 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99755 | 0.79983 | 19.772 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99755 | 0.90772 | 8.983 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99841 | 0.80529 | 19.312 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99831 | 0.81166 | 18.665 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.90488 | 9.536 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99947 | 0.91314 | 8.633 | Yes
Active | 2025W1-N11-WVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99809 | 0.81039 | 18.77 | Yes
Active | 2025W1-N11-WVD246769 | 246769 | 05MINERR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0022 | 0.88969 | 11.255 | Yes
Active | 2025W1-N11-WVD246769 | 246769 | 05MINERR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0004 | 0.91841 | 8.201 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.88127 | 12.271 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.87867 | 12.591 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.87863 | 12.558 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.87103 | 13.376 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99692 | 0.8263 | 17.062 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99692 | 0.83625 | 16.067 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99692 | 0.84174 | 15.518 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99692 | 0.85242 | 14.45 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99692 | 0.86635 | 13.056 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99692 | 0.86642 | 13.049 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99692 | 0.86803 | 12.889 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99692 | 0.91225 | 8.466 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0054 | 0.86055 | 14.486 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.87288 | 13.122 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.87322 | 13.102 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.87228 | 13.1 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99183 | 0.85329 | 13.854 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.87314 | 13.077 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.86132 | 14.12 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.87207 | 13.045 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.84874 | 15.605 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99954 | 0.82547 | 17.407 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99954 | 0.83908 | 16.046 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99954 | 0.86418 | 13.536 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99954 | 0.87658 | 12.296 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.83348 | 16.926 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.8712 | 13.447 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.8791 | 12.45 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.84129 | 16.119 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.84236 | 16.012 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.86803 | 13.747 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.86226 | 14.008 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.87201 | 13.033 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.86988 | 13.428 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.87443 | 13.01 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.8781 | 12.637 | Yes
Active | 2025W1-N11-WVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.87733 | 12.71 | Yes
Active | 2025W1-N11-WVD246854 | 246854 | 05AUBURN2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99678 | 0.88491 | 11.187 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99567 | 0.88021 | 11.546 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.87823 | 11.707 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.87728 | 11.74 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.8685 | 12.673 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98251 | 0.81986 | 16.265 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98251 | 0.83709 | 14.541 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98251 | 0.83967 | 14.284 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98251 | 0.84276 | 13.975 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98251 | 0.858 | 12.451 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98251 | 0.86231 | 12.019 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98251 | 0.86294 | 11.957 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99818 | 0.865 | 13.318 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99363 | 0.87054 | 12.309 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.8709 | 12.311 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.88006 | 11.537 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.87446 | 11.906 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99551 | 0.81462 | 18.089 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99551 | 0.82541 | 17.01 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.85589 | 13.975 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98393 | 0.83504 | 14.89 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98393 | 0.83671 | 14.722 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98393 | 0.86747 | 11.647 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98393 | 0.86819 | 11.575 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.84142 | 14.825 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.87398 | 12.443 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99496 | 0.878 | 11.695 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98576 | 0.83792 | 14.784 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98576 | 0.8419 | 14.386 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.86484 | 12.988 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98735 | 0.85975 | 12.76 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98735 | 0.86482 | 12.253 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99351 | 0.8672 | 12.631 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.87217 | 12.263 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99459 | 0.87674 | 11.786 | Yes
Active | 2025W1-N11-WVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99445 | 0.87625 | 11.82 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.87939 | 12.335 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.87723 | 12.515 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.87625 | 12.553 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.86663 | 13.578 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98957 | 0.82533 | 16.424 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98957 | 0.83312 | 15.645 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98957 | 0.83691 | 15.266 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98957 | 0.83949 | 15.008 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98957 | 0.85542 | 13.415 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98957 | 0.86023 | 12.934 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98957 | 0.86172 | 12.785 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.86248 | 14.272 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.86873 | 13.202 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.86912 | 13.201 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.87928 | 12.324 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.87305 | 12.746 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0129 | 0.92619 | 8.672 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99839 | 0.82024 | 17.814 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99839 | 0.83008 | 16.831 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.85299 | 14.978 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99114 | 0.83184 | 15.93 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.83269 | 15.845 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99114 | 0.86526 | 12.588 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99114 | 0.86649 | 12.465 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.83796 | 15.902 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.87274 | 13.267 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.877 | 12.503 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99343 | 0.8347 | 15.874 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.83905 | 15.438 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.86347 | 13.869 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99448 | 0.85736 | 13.711 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99448 | 0.86276 | 13.172 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.8652 | 13.547 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.87049 | 13.142 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.87519 | 12.65 | Yes
Active | 2025W1-N11-WVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.87497 | 12.655 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.87484 | 12.521 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99967 | 0.87252 | 12.716 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99908 | 0.87161 | 12.747 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99973 | 0.86184 | 13.788 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98673 | 0.82447 | 16.227 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98673 | 0.82769 | 15.904 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98673 | 0.83173 | 15.5 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98673 | 0.83424 | 15.249 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98673 | 0.85033 | 13.64 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98673 | 0.85529 | 13.144 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98673 | 0.85691 | 12.982 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.85758 | 14.497 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99805 | 0.86399 | 13.406 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99843 | 0.86439 | 13.404 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99983 | 0.87473 | 12.511 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99767 | 0.8681 | 12.956 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.912 | 9.553 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.8196 | 17.374 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99334 | 0.82862 | 16.472 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.84786 | 15.218 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98827 | 0.82651 | 16.176 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98827 | 0.82726 | 16.101 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98827 | 0.8604 | 12.787 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98827 | 0.86162 | 12.665 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.83268 | 16.151 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.86807 | 13.47 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99933 | 0.87242 | 12.691 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99072 | 0.82939 | 16.133 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99072 | 0.83387 | 15.685 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99952 | 0.85865 | 14.087 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.85235 | 13.935 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9917 | 0.85781 | 13.39 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99796 | 0.86039 | 13.756 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99922 | 0.86577 | 13.344 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99899 | 0.87052 | 12.847 | Yes
Active | 2025W1-N11-WVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.87027 | 12.857 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.9201 | 8.003 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99629 | 0.90644 | 8.985 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.81531 | 18.138 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99693 | 0.81112 | 18.581 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.81412 | 18.169 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.8005 | 19.92 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99031 | 0.89235 | 9.795 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98201 | 0.75342 | 22.859 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98201 | 0.76719 | 21.482 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98201 | 0.77422 | 20.779 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98201 | 0.78492 | 19.709 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98201 | 0.79509 | 18.692 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98201 | 0.8014 | 18.061 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98201 | 0.80604 | 17.597 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98201 | 0.89014 | 9.187 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98201 | 0.89474 | 8.727 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0009 | 0.78208 | 21.882 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99444 | 0.80041 | 19.403 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99515 | 0.80108 | 19.407 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99885 | 0.91686 | 8.199 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99682 | 0.81634 | 18.048 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.80897 | 18.439 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99336 | 0.90744 | 8.592 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.91464 | 8.243 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99447 | 0.8059 | 18.857 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.79391 | 19.818 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99209 | 0.80579 | 18.63 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.77909 | 22.117 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.75304 | 23.425 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98729 | 0.77108 | 21.621 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98729 | 0.78879 | 19.85 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98729 | 0.80723 | 18.006 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.88411 | 10.988 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99208 | 0.76223 | 22.985 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.80654 | 19.375 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99551 | 0.81176 | 18.375 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99326 | 0.77018 | 22.307 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99326 | 0.77252 | 22.074 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.80465 | 19.816 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0028 | 0.91408 | 8.873 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.78874 | 20.076 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9895 | 0.79916 | 19.033 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99939 | 0.89861 | 10.078 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99031 | 0.89235 | 9.795 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99818 | 0.91062 | 8.756 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99813 | 0.91118 | 8.695 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.79782 | 19.83 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99613 | 0.90593 | 9.02 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99667 | 0.80315 | 19.352 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99661 | 0.81076 | 18.584 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99853 | 0.90457 | 9.396 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99766 | 0.91308 | 8.458 | Yes
Active | 2025W1-N11-WVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99634 | 0.80931 | 18.703 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99112 | 0.88094 | 11.018 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99112 | 0.88985 | 10.127 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99112 | 0.89298 | 9.814 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99112 | 0.90803 | 8.31 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.90685 | 9.466 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99768 | 0.91513 | 8.256 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.90389 | 9.633 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99013 | 0.88265 | 10.748 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99013 | 0.89028 | 9.985 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96972 | 0.88337 | 8.635 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9844 | 0.88832 | 9.608 | Yes
Active | 2025W1-N11-WVD246929 | 246929 | 05MADDOX | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99682 | 0.91424 | 8.258 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0072 | 0.90961 | 9.761 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0072 | 0.9153 | 9.193 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0072 | 0.9191 | 8.813 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0072 | 0.92564 | 8.158 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0158 | 0.93364 | 8.22 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0141 | 0.9269 | 8.719 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0073 | 0.90718 | 10.016 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.91482 | 9.252 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.9182 | 9.243 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0067 | 0.91088 | 9.58 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.91269 | 9.4 | Yes
Active | 2025W1-N11-WVD246942 | 246942 | 05WARERD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0125 | 0.92795 | 8.452 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99704 | 0.88689 | 11.015 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99704 | 0.9064 | 9.065 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.92086 | 8.243 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.9179 | 8.473 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99579 | 0.90703 | 8.876 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99579 | 0.91001 | 8.579 | Yes
Active | 2025W1-N11-WVD246950 | 246950 | 05TIMBER SW | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98604 | 0.89695 | 8.908 | Yes
Active | 2025W1-N11-WVD246982 | 246982 | 05HUNT JT_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98918 | 0.88083 | 10.835 | Yes
Active | 2025W1-N11-WVD246993 | 246993 | 05PURDUE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99302 | 0.8796 | 11.342 | Yes
Active | 2025W1-N11-WVD246993 | 246993 | 05PURDUE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99125 | 0.91114 | 8.01 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96431 | 0.88298 | 8.132 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9489 | 0.82933 | 11.958 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9489 | 0.83102 | 11.788 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9489 | 0.85626 | 9.264 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96606 | 0.85578 | 11.028 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96306 | 0.88217 | 8.089 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9641 | 0.8835 | 8.06 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9624 | 0.86776 | 9.464 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9624 | 0.88024 | 8.215 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96288 | 0.85392 | 10.895 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94381 | 0.832 | 11.18 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.94381 | 0.8597 | 8.411 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96508 | 0.88505 | 8.003 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96428 | 0.83653 | 12.775 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96428 | 0.88195 | 8.233 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96097 | 0.86657 | 9.44 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96097 | 0.87912 | 8.185 | Yes
Active | 2025W1-N11-WVD246999 | 246999 | 05SORENS | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9638 | 0.88299 | 8.08 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98164 | 0.88257 | 9.907 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98164 | 0.88898 | 9.265 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98164 | 0.8986 | 8.304 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98752 | 0.9024 | 8.512 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98709 | 0.89908 | 8.8 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98167 | 0.8736 | 10.808 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.88834 | 9.334 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97272 | 0.87987 | 9.284 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97272 | 0.88784 | 8.487 | Yes
Active | 2025W1-N11-WVD247000 | 247000 | 05YELLOW CK1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98377 | 0.90119 | 8.257 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98163 | 0.88259 | 9.904 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98163 | 0.88901 | 9.263 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98163 | 0.89862 | 8.302 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98752 | 0.90242 | 8.509 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98708 | 0.8991 | 8.798 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98167 | 0.87363 | 10.805 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.88836 | 9.331 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97272 | 0.8799 | 9.281 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97272 | 0.88787 | 8.485 | Yes
Active | 2025W1-N11-WVD247001 | 247001 | 05YELLOW CK2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98376 | 0.90121 | 8.255 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99518 | 0.85089 | 14.429 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99487 | 0.8471 | 14.776 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.84782 | 14.643 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99585 | 0.8357 | 16.015 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98081 | 0.79736 | 18.345 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98081 | 0.80521 | 17.56 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98081 | 0.80548 | 17.533 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98081 | 0.81214 | 16.867 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98081 | 0.82291 | 15.79 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98081 | 0.82802 | 15.279 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98081 | 0.83335 | 14.746 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99802 | 0.8295 | 16.852 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.993 | 0.83724 | 15.576 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.83776 | 15.573 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99506 | 0.85103 | 14.403 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.84387 | 14.87 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99741 | 0.86822 | 12.919 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.989 | 0.80688 | 18.212 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.989 | 0.81653 | 17.248 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99578 | 0.81996 | 17.582 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98319 | 0.79695 | 18.623 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98319 | 0.79973 | 18.346 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98319 | 0.83293 | 15.026 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98319 | 0.83582 | 14.736 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99552 | 0.90905 | 8.647 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98937 | 0.80344 | 18.593 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99814 | 0.84332 | 15.482 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99436 | 0.84804 | 14.632 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98664 | 0.80204 | 18.46 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98664 | 0.80676 | 17.988 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99589 | 0.8347 | 16.119 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.8245 | 16.223 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98672 | 0.83115 | 15.558 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99351 | 0.83373 | 15.978 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9945 | 0.83949 | 15.502 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99432 | 0.84563 | 14.87 | Yes
Active | 2025W1-N11-WVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99414 | 0.84494 | 14.92 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.85939 | 14.675 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.85612 | 15.032 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.85703 | 14.854 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.84555 | 16.209 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99161 | 0.8041 | 18.75 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99161 | 0.81342 | 17.819 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99161 | 0.81639 | 17.522 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99161 | 0.83064 | 16.097 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99161 | 0.83211 | 15.949 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99161 | 0.83844 | 15.317 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99161 | 0.84415 | 14.746 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0093 | 0.83768 | 17.162 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.8469 | 15.772 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.84741 | 15.768 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.85946 | 14.67 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.85091 | 15.204 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.86111 | 14.568 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.82716 | 17.112 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99828 | 0.83635 | 16.193 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.82753 | 17.95 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.80361 | 19.073 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99433 | 0.8115 | 18.283 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99433 | 0.8412 | 15.314 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99433 | 0.84723 | 14.71 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.91962 | 8.775 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.81122 | 18.979 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0095 | 0.8517 | 15.78 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.85649 | 14.876 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99987 | 0.81361 | 18.627 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99987 | 0.81756 | 18.231 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.84511 | 16.315 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9992 | 0.83469 | 16.451 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9992 | 0.8424 | 15.68 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.92791 | 8.062 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.84362 | 16.168 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.84913 | 15.7 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.85517 | 15.086 | Yes
Active | 2025W1-N11-WVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.85423 | 15.161 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.88738 | 11.782 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.88438 | 12.166 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.88419 | 12.141 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87693 | 12.932 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99678 | 0.83451 | 16.227 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99678 | 0.84373 | 15.305 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99678 | 0.84919 | 14.759 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99678 | 0.85925 | 13.753 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99678 | 0.87157 | 12.522 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99678 | 0.87241 | 12.438 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99678 | 0.8738 | 12.298 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.007 | 0.86804 | 13.894 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.87877 | 12.67 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.87909 | 12.654 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.88089 | 12.339 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99597 | 0.86344 | 13.252 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.87969 | 12.559 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.86688 | 13.642 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.87669 | 12.662 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.8559 | 15.021 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99992 | 0.8338 | 16.612 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99992 | 0.84604 | 15.388 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99992 | 0.87138 | 12.854 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99992 | 0.88171 | 11.821 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.84127 | 16.252 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.8773 | 13.007 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.88544 | 11.93 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0036 | 0.84824 | 15.539 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.84988 | 15.375 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.8739 | 13.313 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.86855 | 13.479 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.8774 | 12.594 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.87586 | 12.966 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.88025 | 12.572 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.88379 | 12.211 | Yes
Active | 2025W1-N11-WVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.88307 | 12.278 | Yes
Active | 2025W1-N11-WVD247106 | 247106 | 05VARNER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98958 | 0.88206 | 10.752 | Yes
Active | 2025W1-N11-WVD247108 | 247108 | 05SOWERS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0047 | 0.90928 | 9.546 | Yes
Active | 2025W1-N11-WVD247132 | 247132 | 05ELLISN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99262 | 0.87713 | 11.549 | Yes
Active | 2025W1-N11-WVD247132 | 247132 | 05ELLISN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99085 | 0.90941 | 8.144 | Yes
Active | 2025W1-N11-WVD247132 | 247132 | 05ELLISN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97181 | 0.89001 | 8.18 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.8768 | 12.655 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.87489 | 12.854 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.87408 | 12.867 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.86494 | 13.854 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99021 | 0.82807 | 16.214 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99021 | 0.8349 | 15.531 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99021 | 0.83527 | 15.494 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99021 | 0.84017 | 15.004 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99021 | 0.85145 | 13.876 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99021 | 0.85871 | 13.151 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99021 | 0.86001 | 13.02 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.006 | 0.85943 | 14.656 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.86714 | 13.485 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.86751 | 13.482 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.87647 | 12.672 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.8678 | 13.237 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.89213 | 11.437 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99364 | 0.83578 | 15.787 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99364 | 0.84353 | 15.012 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.84886 | 15.451 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99173 | 0.82754 | 16.419 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99173 | 0.82974 | 16.199 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99173 | 0.86229 | 12.944 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99173 | 0.8655 | 12.623 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99802 | 0.83363 | 16.439 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.8697 | 13.658 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.87435 | 12.825 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99573 | 0.83263 | 16.31 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.83687 | 15.886 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.86151 | 14.217 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.85559 | 14.08 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9964 | 0.86162 | 13.477 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.8636 | 13.828 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.86885 | 13.42 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.87331 | 12.956 | Yes
Active | 2025W1-N11-WVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.87288 | 12.986 | Yes
Active | 2025W1-N11-WVD247156 | 247156 | 05STEAMT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99684 | 0.91662 | 8.022 | Yes
Active | 2025W1-N11-WVD247156 | 247156 | 05STEAMT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9981 | 0.91792 | 8.018 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0024 | 0.90861 | 9.377 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.9137 | 8.868 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.92328 | 8.352 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0026 | 0.90069 | 10.194 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.91275 | 8.988 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99552 | 0.90585 | 8.967 | Yes
Active | 2025W1-N11-WVD247172 | 247172 | 05EBERSO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99552 | 0.91243 | 8.308 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97796 | 0.89559 | 8.237 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97287 | 0.87824 | 9.463 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97465 | 0.79346 | 18.12 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97479 | 0.78987 | 18.492 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97365 | 0.79229 | 18.135 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97695 | 0.78027 | 19.668 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9723 | 0.87435 | 9.795 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95515 | 0.73039 | 22.476 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95515 | 0.74595 | 20.92 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95515 | 0.75413 | 20.102 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95515 | 0.76238 | 19.277 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95515 | 0.77433 | 18.082 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97888 | 0.75808 | 22.081 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97814 | 0.89684 | 8.131 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97371 | 0.89291 | 8.08 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97255 | 0.78078 | 19.178 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97319 | 0.78134 | 19.186 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97662 | 0.89223 | 8.439 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97715 | 0.89596 | 8.119 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97722 | 0.89597 | 8.126 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97476 | 0.79427 | 18.049 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97129 | 0.78744 | 18.385 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97129 | 0.88338 | 8.791 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97492 | 0.89015 | 8.476 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97772 | 0.89608 | 8.163 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97245 | 0.78504 | 18.741 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96975 | 0.77425 | 19.549 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96975 | 0.78558 | 18.417 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97876 | 0.75761 | 22.115 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96049 | 0.73003 | 23.046 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96049 | 0.75123 | 20.925 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96049 | 0.76382 | 19.666 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96049 | 0.78607 | 17.442 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97141 | 0.85934 | 11.206 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97008 | 0.74206 | 22.802 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97803 | 0.78574 | 19.23 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97353 | 0.79019 | 18.334 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97128 | 0.75143 | 21.986 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97128 | 0.75354 | 21.774 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98191 | 0.78486 | 19.705 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98191 | 0.89168 | 9.024 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96648 | 0.76925 | 19.723 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96648 | 0.77949 | 18.699 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97743 | 0.87406 | 10.337 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97703 | 0.89478 | 8.225 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9723 | 0.87435 | 9.795 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97604 | 0.88629 | 8.975 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97599 | 0.88684 | 8.915 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97375 | 0.77801 | 19.574 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97375 | 0.88219 | 9.156 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97457 | 0.78316 | 19.141 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97447 | 0.7895 | 18.497 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97639 | 0.8805 | 9.589 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97556 | 0.88868 | 8.688 | Yes
Active | 2025W1-N11-WVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97424 | 0.78822 | 18.601 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.89508 | 11.115 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.89325 | 11.329 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.89322 | 11.3 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.88677 | 11.991 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0014 | 0.84635 | 15.502 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0014 | 0.85698 | 14.439 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0014 | 0.85751 | 14.385 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0014 | 0.87046 | 13.09 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0014 | 0.88298 | 11.838 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0014 | 0.88373 | 11.764 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0014 | 0.88449 | 11.687 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0072 | 0.87568 | 13.155 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.88856 | 11.767 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.88884 | 11.749 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.88534 | 12.035 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.86842 | 12.559 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.88769 | 11.825 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.87867 | 12.658 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.8883 | 11.695 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.86571 | 14.121 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.84503 | 15.794 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.003 | 0.8543 | 14.867 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.003 | 0.8799 | 12.307 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.003 | 0.89226 | 11.071 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.85324 | 15.173 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.88673 | 12.067 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.89301 | 11.293 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0038 | 0.85712 | 14.667 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.85834 | 14.545 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.88229 | 12.462 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.87875 | 12.611 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0049 | 0.88747 | 11.738 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.88579 | 12.041 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.88989 | 11.666 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.89276 | 11.37 | Yes
Active | 2025W1-N11-WVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.89206 | 11.436 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.91123 | 9.286 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.91026 | 9.409 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.91004 | 9.386 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.90548 | 9.89 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99964 | 0.87398 | 12.566 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99964 | 0.87738 | 12.226 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99964 | 0.88485 | 11.478 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99964 | 0.89391 | 10.573 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99964 | 0.90032 | 9.932 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99964 | 0.90508 | 9.455 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99964 | 0.90577 | 9.387 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0053 | 0.89562 | 10.965 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.90727 | 9.673 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.90745 | 9.667 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90525 | 9.813 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.89482 | 10.216 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.90592 | 9.766 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.89865 | 10.403 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.90564 | 9.703 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.88745 | 11.75 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.87186 | 12.882 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0007 | 0.8722 | 12.848 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0007 | 0.9006 | 10.008 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0007 | 0.91011 | 9.057 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.87959 | 12.237 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.90552 | 9.995 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.90946 | 9.425 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99933 | 0.87619 | 12.314 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99933 | 0.87862 | 12.071 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.89839 | 10.559 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.89876 | 10.357 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.90502 | 9.731 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.90481 | 9.899 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.90823 | 9.615 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.90982 | 9.441 | Yes
Active | 2025W1-N11-WVD247316 | 247316 | 05SALERNO | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.90928 | 9.49 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99494 | 0.9005 | 9.445 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99494 | 0.90516 | 8.979 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99494 | 0.90829 | 8.666 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.91354 | 8.704 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99856 | 0.90036 | 9.821 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99856 | 0.90355 | 9.501 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.9038 | 9.634 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0003 | 0.90518 | 9.511 | Yes
Active | 2025W1-N11-WVD247319 | 247319 | 05WOLFCK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90875 | 9.155 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.89389 | 11.269 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.89303 | 11.397 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.893 | 11.355 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.88691 | 12.021 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.84904 | 15.26 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0016 | 0.85618 | 14.546 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0016 | 0.86052 | 14.112 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0016 | 0.87277 | 12.887 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0016 | 0.88287 | 11.876 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0016 | 0.88577 | 11.587 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0016 | 0.8866 | 11.503 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0082 | 0.87525 | 13.294 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.88888 | 11.766 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.88913 | 11.756 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.88801 | 11.817 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.87505 | 12.341 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.88778 | 11.832 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.87879 | 12.635 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0051 | 0.8878 | 11.733 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0078 | 0.86594 | 14.182 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.84671 | 15.597 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0027 | 0.85137 | 15.131 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.0027 | 0.88048 | 12.221 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0027 | 0.89263 | 11.006 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.85487 | 14.968 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.88695 | 12.139 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.89164 | 11.445 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0026 | 0.85518 | 14.742 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.85699 | 14.561 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.88069 | 12.653 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.87885 | 12.587 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.88698 | 11.775 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.886 | 12.038 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.89013 | 11.689 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.89252 | 11.435 | Yes
Active | 2025W1-N11-WVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.89185 | 11.496 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.91451 | 8.372 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99245 | 0.88565 | 10.679 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99245 | 0.89096 | 10.149 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99245 | 0.89452 | 9.792 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99245 | 0.90268 | 8.976 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99245 | 0.91091 | 8.154 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99245 | 0.91172 | 8.073 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99245 | 0.91239 | 8.006 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99833 | 0.91059 | 8.774 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99808 | 0.91597 | 8.211 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.91614 | 8.198 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99657 | 0.91044 | 8.613 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.91585 | 8.205 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9975 | 0.90942 | 8.807 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9975 | 0.91404 | 8.346 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.90049 | 9.756 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.88544 | 11.056 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99599 | 0.88982 | 10.617 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99599 | 0.91293 | 8.306 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.88952 | 10.8 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99859 | 0.91378 | 8.482 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99759 | 0.89169 | 10.59 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.89516 | 10.243 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99844 | 0.91096 | 8.749 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.90927 | 8.825 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99752 | 0.91363 | 8.389 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99807 | 0.91397 | 8.411 | Yes
Active | 2025W1-N11-WVD247370 | 247370 | 05MUSKINGUM1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9982 | 0.91683 | 8.137 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99824 | 0.91449 | 8.375 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99245 | 0.88562 | 10.684 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99245 | 0.89092 | 10.153 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99245 | 0.89449 | 9.796 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99245 | 0.90265 | 8.98 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99245 | 0.91088 | 8.157 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99245 | 0.91169 | 8.076 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99245 | 0.91236 | 8.009 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99833 | 0.91056 | 8.777 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99809 | 0.91594 | 8.214 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.91612 | 8.2 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99657 | 0.91041 | 8.616 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99791 | 0.91583 | 8.208 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9975 | 0.9094 | 8.81 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9975 | 0.91401 | 8.349 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.90046 | 9.76 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.8854 | 11.06 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.996 | 0.88979 | 10.621 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.996 | 0.9129 | 8.309 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.88948 | 10.804 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9986 | 0.91375 | 8.484 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99759 | 0.89166 | 10.594 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.89513 | 10.247 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.91093 | 8.751 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.90924 | 8.828 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99752 | 0.91361 | 8.391 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99807 | 0.91394 | 8.413 | Yes
Active | 2025W1-N11-WVD247373 | 247373 | 05MUSKINGUM2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9982 | 0.9168 | 8.14 | Yes
Active | 2025W1-N11-WVD247433 | 247433 | 05CHARGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0031 | 0.90408 | 9.904 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.91448 | 8.375 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99244 | 0.88561 | 10.684 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99244 | 0.89091 | 10.153 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99244 | 0.89448 | 9.796 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99244 | 0.90264 | 8.98 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99244 | 0.91087 | 8.157 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99244 | 0.91168 | 8.076 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99244 | 0.91235 | 8.009 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99832 | 0.91055 | 8.777 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99807 | 0.91593 | 8.214 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.91611 | 8.2 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99656 | 0.91041 | 8.616 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.91582 | 8.208 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99749 | 0.90939 | 8.81 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99749 | 0.914 | 8.349 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99805 | 0.90045 | 9.76 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.88539 | 11.059 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99599 | 0.88978 | 10.621 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99599 | 0.91289 | 8.309 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.88947 | 10.804 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99858 | 0.91374 | 8.484 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99758 | 0.89164 | 10.594 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99758 | 0.89512 | 10.246 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99844 | 0.91092 | 8.751 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.90923 | 8.828 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99751 | 0.9136 | 8.391 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.91393 | 8.413 | Yes
Active | 2025W1-N11-WVD247434 | 247434 | 05MUSKNG_DSZ | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.91679 | 8.14 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.91448 | 8.375 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99244 | 0.88561 | 10.684 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99244 | 0.89091 | 10.153 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99244 | 0.89448 | 9.796 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99244 | 0.90264 | 8.98 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99244 | 0.91087 | 8.157 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99244 | 0.91168 | 8.076 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99244 | 0.91235 | 8.009 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99832 | 0.91055 | 8.777 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99807 | 0.91593 | 8.214 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.91611 | 8.2 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99656 | 0.91041 | 8.616 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9979 | 0.91582 | 8.208 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99749 | 0.90939 | 8.81 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99749 | 0.914 | 8.349 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99805 | 0.90045 | 9.76 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.88539 | 11.059 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99599 | 0.88978 | 10.621 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99599 | 0.91289 | 8.309 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.88947 | 10.804 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99858 | 0.91374 | 8.484 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99758 | 0.89164 | 10.594 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99758 | 0.89512 | 10.246 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99844 | 0.91092 | 8.751 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.90923 | 8.828 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99751 | 0.9136 | 8.391 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.91393 | 8.413 | Yes
Active | 2025W1-N11-WVD247435 | 247435 | 05MUSKNG_ESZ | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.91679 | 8.14 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.86293 | 14.277 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.86198 | 14.482 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.86218 | 14.394 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.85293 | 15.432 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99372 | 0.80647 | 18.725 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99372 | 0.81621 | 17.751 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99372 | 0.82234 | 17.139 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99372 | 0.83389 | 15.983 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99372 | 0.84584 | 14.788 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99372 | 0.8473 | 14.642 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99372 | 0.85037 | 14.335 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99372 | 0.9127 | 8.102 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0086 | 0.84243 | 16.621 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.85488 | 15.088 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.85528 | 15.075 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.8607 | 14.522 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99918 | 0.84684 | 15.234 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.85726 | 14.831 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.84058 | 16.178 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.85216 | 15.02 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.83029 | 17.695 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99734 | 0.80566 | 19.168 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99734 | 0.81953 | 17.781 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99734 | 0.84607 | 15.127 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99734 | 0.85827 | 13.907 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.92357 | 8.4 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.81356 | 18.958 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.8544 | 15.459 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.86003 | 14.485 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0027 | 0.82177 | 18.095 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.8231 | 17.962 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.85066 | 15.787 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.84303 | 15.915 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.85341 | 14.876 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.85154 | 15.439 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.85671 | 14.993 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.86127 | 14.529 | Yes
Active | 2025W1-N11-WVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.8604 | 14.607 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.91421 | 8.395 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9924 | 0.88525 | 10.715 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9924 | 0.89056 | 10.184 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9924 | 0.89414 | 9.827 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9924 | 0.90234 | 9.006 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9924 | 0.91058 | 8.182 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9924 | 0.91139 | 8.101 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9924 | 0.91208 | 8.032 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99825 | 0.91025 | 8.8 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.998 | 0.91567 | 8.233 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99804 | 0.91584 | 8.22 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99654 | 0.9102 | 8.634 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.91555 | 8.227 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.90912 | 8.831 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99743 | 0.91375 | 8.367 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99798 | 0.90015 | 9.783 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99594 | 0.88503 | 11.09 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99594 | 0.88945 | 10.649 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99594 | 0.91259 | 8.334 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.88912 | 10.832 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99851 | 0.91347 | 8.504 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99751 | 0.89132 | 10.619 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.89478 | 10.273 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99836 | 0.91064 | 8.772 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.90895 | 8.85 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99745 | 0.91334 | 8.411 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99799 | 0.91366 | 8.433 | Yes
Active | 2025W1-N11-WVD247500 | 247500 | 05MUSK_D_XFL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.91653 | 8.159 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99815 | 0.91421 | 8.395 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9924 | 0.88525 | 10.715 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9924 | 0.89056 | 10.184 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9924 | 0.89414 | 9.827 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9924 | 0.90234 | 9.006 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9924 | 0.91058 | 8.182 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9924 | 0.91139 | 8.101 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9924 | 0.91208 | 8.032 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99825 | 0.91025 | 8.8 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.998 | 0.91567 | 8.233 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99804 | 0.91584 | 8.22 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99654 | 0.9102 | 8.634 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.91555 | 8.227 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.90912 | 8.831 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99743 | 0.91375 | 8.367 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99798 | 0.90015 | 9.783 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99594 | 0.88503 | 11.09 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99594 | 0.88945 | 10.649 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99594 | 0.91259 | 8.334 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.88912 | 10.832 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99851 | 0.91347 | 8.504 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99751 | 0.89132 | 10.619 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.89478 | 10.273 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99836 | 0.91064 | 8.772 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99745 | 0.90895 | 8.85 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99745 | 0.91334 | 8.411 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99799 | 0.91366 | 8.433 | Yes
Active | 2025W1-N11-WVD247501 | 247501 | 05MUSK_E_XFL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.91653 | 8.159 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97966 | 0.89842 | 8.124 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97413 | 0.87988 | 9.424 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97639 | 0.79718 | 17.921 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97657 | 0.79327 | 18.331 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97544 | 0.79595 | 17.948 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97908 | 0.7835 | 19.559 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97405 | 0.87735 | 9.67 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95723 | 0.73438 | 22.285 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95723 | 0.74941 | 20.781 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95723 | 0.75689 | 20.034 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95723 | 0.76613 | 19.109 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95723 | 0.77733 | 17.99 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98053 | 0.76261 | 21.792 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97983 | 0.89968 | 8.015 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97423 | 0.78361 | 19.062 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9749 | 0.78421 | 19.069 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97834 | 0.8951 | 8.324 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97887 | 0.8988 | 8.007 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97894 | 0.8988 | 8.014 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9765 | 0.79799 | 17.851 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97308 | 0.79116 | 18.192 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97308 | 0.88622 | 8.686 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97664 | 0.893 | 8.364 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97942 | 0.89894 | 8.048 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97419 | 0.78861 | 18.559 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97156 | 0.77772 | 19.384 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97156 | 0.78893 | 18.263 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98028 | 0.76144 | 21.884 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96243 | 0.73402 | 22.841 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96243 | 0.75378 | 20.865 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96243 | 0.76824 | 19.419 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96243 | 0.78896 | 17.348 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97316 | 0.86249 | 11.067 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97162 | 0.74559 | 22.603 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97977 | 0.78948 | 19.029 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97528 | 0.79392 | 18.136 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97241 | 0.754 | 21.84 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97241 | 0.75634 | 21.606 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98317 | 0.78796 | 19.521 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98317 | 0.8938 | 8.937 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96814 | 0.77228 | 19.587 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96814 | 0.78241 | 18.573 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97909 | 0.87715 | 10.194 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97875 | 0.89763 | 8.112 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97405 | 0.87735 | 9.67 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97774 | 0.88916 | 8.858 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97769 | 0.8897 | 8.799 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9757 | 0.78103 | 19.467 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9757 | 0.88487 | 9.084 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97634 | 0.78612 | 19.022 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97626 | 0.79294 | 18.332 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97811 | 0.88336 | 9.475 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97726 | 0.89152 | 8.574 | Yes
Active | 2025W1-N11-WVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97601 | 0.7916 | 18.441 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99787 | 0.91345 | 8.442 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99755 | 0.91242 | 8.513 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.91161 | 8.544 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99767 | 0.9119 | 8.577 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9903 | 0.86941 | 12.089 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9903 | 0.87553 | 11.477 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9903 | 0.89053 | 9.977 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9903 | 0.89575 | 9.454 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9903 | 0.90634 | 8.396 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9903 | 0.90909 | 8.121 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99899 | 0.89287 | 10.611 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99817 | 0.91457 | 8.36 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91457 | 8.371 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.91129 | 8.614 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.90738 | 8.805 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99674 | 0.90937 | 8.737 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99534 | 0.90421 | 9.112 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99534 | 0.90443 | 9.091 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99843 | 0.88925 | 10.918 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99026 | 0.85873 | 13.153 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99026 | 0.87471 | 11.555 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99026 | 0.89926 | 9.1 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99026 | 0.90888 | 8.138 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99434 | 0.9014 | 9.294 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99916 | 0.91324 | 8.592 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.91205 | 8.547 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9785 | 0.86341 | 11.509 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9785 | 0.87293 | 10.557 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.89257 | 10.142 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99447 | 0.90321 | 9.126 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99447 | 0.90344 | 9.103 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99707 | 0.91158 | 8.549 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.91488 | 8.352 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99732 | 0.9118 | 8.552 | Yes
Active | 2025W1-N11-WVD247513 | 247513 | 05BOUTWELL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99725 | 0.91145 | 8.58 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.83925 | 16.297 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.83456 | 16.79 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.83704 | 16.449 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.82315 | 18.19 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.999 | 0.91228 | 8.672 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98716 | 0.78088 | 20.627 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98716 | 0.79101 | 19.615 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98716 | 0.79381 | 19.335 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98716 | 0.80904 | 17.811 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98716 | 0.81285 | 17.431 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98716 | 0.81541 | 17.175 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98716 | 0.82436 | 16.28 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98716 | 0.905 | 8.216 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.81294 | 19.275 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.82323 | 17.687 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.8239 | 17.685 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.83984 | 16.245 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99921 | 0.83231 | 16.69 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.83888 | 16.325 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99604 | 0.80705 | 18.899 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99604 | 0.81785 | 17.819 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.80533 | 19.88 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.78048 | 21.041 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99089 | 0.78926 | 20.163 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99089 | 0.81729 | 17.36 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99089 | 0.82548 | 16.541 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.90316 | 9.78 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99686 | 0.78818 | 20.868 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.83097 | 17.458 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.83598 | 16.524 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99547 | 0.79054 | 20.493 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99547 | 0.7943 | 20.118 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.82494 | 18.024 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.9225 | 8.268 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.81103 | 18.346 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99449 | 0.81967 | 17.482 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.91525 | 8.93 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.999 | 0.91228 | 8.672 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.82043 | 18.13 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.91836 | 8.337 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.826 | 17.614 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.83381 | 16.824 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.91842 | 8.525 | Yes
Active | 2025W1-N11-WVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.83255 | 16.925 | Yes
Active | 2025W1-N11-WVD247566 | 247566 | 05LAMPING_BP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0079 | 0.92568 | 8.222 | Yes
Active | 2025W1-N11-WVD247566 | 247566 | 05LAMPING_BP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0103 | 0.92544 | 8.482 | Yes
Active | 2025W1-N11-WVD247566 | 247566 | 05LAMPING_BP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0103 | 0.92676 | 8.35 | Yes
Active | 2025W1-N11-WVD247566 | 247566 | 05LAMPING_BP | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0106 | 0.92837 | 8.227 | Yes
Active | 2025W1-N11-WVD247566 | 247566 | 05LAMPING_BP | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0107 | 0.92816 | 8.251 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.9156 | 8.324 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9966 | 0.82125 | 17.535 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99702 | 0.81803 | 17.9 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99603 | 0.82064 | 17.539 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99943 | 0.80728 | 19.216 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.89803 | 9.382 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98022 | 0.75952 | 22.07 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98022 | 0.77129 | 20.893 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98022 | 0.7782 | 20.202 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98022 | 0.79005 | 19.017 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98022 | 0.80011 | 18.011 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98022 | 0.80485 | 17.537 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98022 | 0.8096 | 17.062 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98022 | 0.89139 | 8.883 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98022 | 0.89561 | 8.461 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.79204 | 20.861 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.80755 | 18.717 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.80819 | 18.718 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99681 | 0.82248 | 17.433 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.8149 | 17.844 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99334 | 0.91002 | 8.333 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.81051 | 18.431 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.79898 | 19.436 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99334 | 0.81148 | 18.187 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99951 | 0.78605 | 21.346 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98536 | 0.7591 | 22.626 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98536 | 0.77523 | 21.013 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98536 | 0.79675 | 18.861 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98536 | 0.81235 | 17.301 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.89011 | 10.512 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.76811 | 22.399 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.81222 | 18.818 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.8176 | 17.777 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99221 | 0.77616 | 21.605 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99221 | 0.77826 | 21.395 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.80989 | 19.165 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.91545 | 8.609 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.79551 | 19.415 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98965 | 0.80618 | 18.347 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99904 | 0.90259 | 9.645 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.89803 | 9.382 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99848 | 0.91442 | 8.407 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.91495 | 8.35 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.80475 | 19.144 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99619 | 0.90932 | 8.687 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.81022 | 18.655 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.81757 | 17.912 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99863 | 0.90793 | 9.069 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99782 | 0.91616 | 8.166 | Yes
Active | 2025W1-N11-WVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99645 | 0.81621 | 18.024 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99272 | 0.91236 | 8.036 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.9104 | 8.259 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99273 | 0.91007 | 8.266 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.90559 | 8.75 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98761 | 0.87535 | 11.226 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98761 | 0.88273 | 10.488 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98761 | 0.8861 | 10.151 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98761 | 0.89306 | 9.454 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98761 | 0.90328 | 8.433 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98761 | 0.90337 | 8.424 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98761 | 0.90345 | 8.416 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99301 | 0.89953 | 9.348 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.90691 | 8.586 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.90711 | 8.572 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.90366 | 8.83 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98593 | 0.89148 | 9.444 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99253 | 0.90622 | 8.631 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.89947 | 9.252 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99199 | 0.90421 | 8.778 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99303 | 0.88997 | 10.306 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.87484 | 11.518 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99001 | 0.87993 | 11.008 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99001 | 0.90252 | 8.749 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99001 | 0.90746 | 8.255 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.88032 | 11.173 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.90531 | 8.826 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99254 | 0.91102 | 8.151 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99205 | 0.88157 | 11.048 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.88612 | 10.593 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99366 | 0.90279 | 9.087 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99181 | 0.89993 | 9.187 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99181 | 0.90387 | 8.794 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.90492 | 8.785 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.90786 | 8.512 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99293 | 0.91004 | 8.289 | Yes
Active | 2025W1-N11-WVD247664 | 247664 | 05BLACK DIAM | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.90955 | 8.335 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99677 | 0.90094 | 9.584 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99713 | 0.89887 | 9.826 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99654 | 0.89765 | 9.889 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.89172 | 10.521 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98658 | 0.86182 | 12.476 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98658 | 0.86665 | 11.993 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98658 | 0.86732 | 11.926 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98658 | 0.8805 | 10.608 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98658 | 0.88101 | 10.557 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98658 | 0.88585 | 10.073 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98658 | 0.88733 | 9.925 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99876 | 0.88803 | 11.073 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99627 | 0.89377 | 10.25 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.894 | 10.246 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.90035 | 9.595 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99363 | 0.89042 | 10.321 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99795 | 0.9039 | 9.405 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98863 | 0.87787 | 11.076 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98863 | 0.88221 | 10.642 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99576 | 0.87852 | 11.724 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9863 | 0.86122 | 12.508 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9863 | 0.86222 | 12.408 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9863 | 0.89017 | 9.613 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9863 | 0.89199 | 9.431 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99234 | 0.86628 | 12.606 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.89418 | 10.499 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99624 | 0.89934 | 9.69 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99204 | 0.86533 | 12.671 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99204 | 0.86879 | 12.325 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99724 | 0.88728 | 10.995 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99267 | 0.88491 | 10.775 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99267 | 0.88924 | 10.343 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99604 | 0.89094 | 10.51 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.89494 | 10.198 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.89788 | 9.892 | Yes
Active | 2025W1-N11-WVD247679 | 247679 | 05LEE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99673 | 0.89747 | 9.927 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98742 | 0.90335 | 8.407 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98508 | 0.89217 | 9.291 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98406 | 0.80392 | 18.014 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98584 | 0.90513 | 8.071 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98457 | 0.80298 | 18.159 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98345 | 0.8042 | 17.925 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98526 | 0.79415 | 19.111 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98395 | 0.886 | 9.795 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9602 | 0.73496 | 22.524 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9602 | 0.75339 | 20.681 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9602 | 0.76736 | 19.284 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9602 | 0.76987 | 19.033 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9602 | 0.78797 | 17.223 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98865 | 0.7621 | 22.656 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98761 | 0.90463 | 8.298 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98366 | 0.90118 | 8.248 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98302 | 0.79605 | 18.697 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98346 | 0.79646 | 18.7 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9862 | 0.90019 | 8.601 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98669 | 0.9038 | 8.289 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98676 | 0.9038 | 8.296 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.80528 | 17.889 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98089 | 0.79823 | 18.265 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98089 | 0.89389 | 8.699 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98432 | 0.89793 | 8.639 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98721 | 0.90389 | 8.332 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98231 | 0.7967 | 18.561 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97959 | 0.78644 | 19.314 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97959 | 0.80176 | 17.783 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.76599 | 22.273 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96678 | 0.73462 | 23.216 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96678 | 0.76735 | 19.942 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96678 | 0.7677 | 19.908 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96678 | 0.80398 | 16.28 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98158 | 0.86909 | 11.249 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.75033 | 23.309 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98546 | 0.90466 | 8.081 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98826 | 0.7903 | 19.796 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98289 | 0.80046 | 18.243 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9839 | 0.76787 | 21.603 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9839 | 0.76908 | 21.482 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.79888 | 19.421 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99309 | 0.90477 | 8.832 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97735 | 0.78397 | 19.339 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97735 | 0.79844 | 17.892 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98701 | 0.88202 | 10.499 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9822 | 0.90089 | 8.131 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9822 | 0.90089 | 8.131 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98658 | 0.90265 | 8.393 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98395 | 0.886 | 9.795 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98603 | 0.89548 | 9.056 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.986 | 0.896 | 9 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98315 | 0.79266 | 19.049 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98315 | 0.8946 | 8.855 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98442 | 0.79794 | 18.648 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98427 | 0.80244 | 18.183 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.88966 | 9.645 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98542 | 0.89717 | 8.825 | Yes
Active | 2025W1-N11-WVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98411 | 0.80141 | 18.27 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98486 | 0.90428 | 8.058 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98146 | 0.8911 | 9.036 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98175 | 0.80911 | 17.264 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98189 | 0.80698 | 17.491 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98082 | 0.80844 | 17.238 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9828 | 0.79819 | 18.461 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98118 | 0.8871 | 9.408 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95972 | 0.74106 | 21.866 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95972 | 0.75937 | 20.034 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95972 | 0.76998 | 18.974 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95972 | 0.77549 | 18.423 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95972 | 0.79204 | 16.768 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.95972 | 0.87905 | 8.067 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98586 | 0.76933 | 21.652 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98025 | 0.79992 | 18.033 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98073 | 0.80035 | 18.037 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9835 | 0.90097 | 8.253 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98186 | 0.80985 | 17.2 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97845 | 0.80308 | 17.537 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97845 | 0.89319 | 8.526 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98205 | 0.89936 | 8.269 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.9044 | 8.02 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97976 | 0.80148 | 17.828 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.977 | 0.79121 | 18.579 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.977 | 0.80294 | 17.406 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98627 | 0.77126 | 21.501 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96505 | 0.74066 | 22.44 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96505 | 0.76744 | 19.761 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96505 | 0.77467 | 19.038 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96505 | 0.80424 | 16.081 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97835 | 0.87022 | 10.813 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97675 | 0.75613 | 22.062 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.985 | 0.80159 | 18.341 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98068 | 0.80589 | 17.479 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97965 | 0.76858 | 21.107 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97965 | 0.77025 | 20.939 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99005 | 0.80234 | 18.771 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99005 | 0.90308 | 8.697 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97436 | 0.78773 | 18.663 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97436 | 0.7985 | 17.586 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98457 | 0.88377 | 10.08 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98392 | 0.90338 | 8.054 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98118 | 0.8871 | 9.408 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98317 | 0.89586 | 8.731 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98313 | 0.89638 | 8.675 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98046 | 0.79655 | 18.392 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98046 | 0.89312 | 8.734 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98175 | 0.80187 | 17.988 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98159 | 0.80648 | 17.511 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98343 | 0.89065 | 9.278 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.89802 | 8.469 | Yes
Active | 2025W1-N11-WVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98141 | 0.80542 | 17.599 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99864 | 0.91382 | 8.482 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99658 | 0.90439 | 9.219 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99485 | 0.80855 | 18.631 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99556 | 0.80803 | 18.753 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.80953 | 18.498 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99684 | 0.79859 | 19.825 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.8944 | 9.932 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97341 | 0.7439 | 22.951 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97341 | 0.75719 | 21.622 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97341 | 0.7687 | 20.471 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97341 | 0.77647 | 19.694 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97341 | 0.79231 | 18.11 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97341 | 0.79986 | 17.355 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97341 | 0.87953 | 9.388 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97341 | 0.88552 | 8.789 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99918 | 0.77676 | 22.241 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9986 | 0.91583 | 8.277 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99019 | 0.90624 | 8.395 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99379 | 0.79997 | 19.381 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99429 | 0.80046 | 19.383 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99736 | 0.91095 | 8.641 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99791 | 0.91481 | 8.31 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99796 | 0.91478 | 8.318 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99488 | 0.81045 | 18.443 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99159 | 0.80296 | 18.863 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99159 | 0.90258 | 8.901 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99568 | 0.90906 | 8.662 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99825 | 0.91513 | 8.312 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.80104 | 19.234 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.79042 | 20.072 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99114 | 0.80451 | 18.663 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99851 | 0.7726 | 22.591 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97973 | 0.74334 | 23.64 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97973 | 0.76778 | 21.196 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97973 | 0.78136 | 19.838 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97973 | 0.8065 | 17.324 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.88067 | 11.285 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9918 | 0.75415 | 23.766 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99889 | 0.79769 | 20.12 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99346 | 0.80468 | 18.878 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99204 | 0.76898 | 22.306 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99204 | 0.76913 | 22.291 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.8004 | 20.128 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.911 | 9.069 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.788 | 20.03 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9883 | 0.80086 | 18.744 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99765 | 0.89198 | 10.568 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99246 | 0.91114 | 8.132 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99246 | 0.91114 | 8.132 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99781 | 0.91363 | 8.418 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.8944 | 9.932 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.90617 | 9.087 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99702 | 0.90672 | 9.03 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.79681 | 19.757 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99438 | 0.90384 | 9.055 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.8021 | 19.328 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.80751 | 18.775 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99715 | 0.89979 | 9.736 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99642 | 0.90781 | 8.861 | Yes
Active | 2025W1-N11-WVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.80638 | 18.869 | Yes
Active | 2025W1-N11-WVD247790 | 247790 | 05DUNTONLAKE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99534 | 0.88332 | 11.202 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.89568 | 10.816 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.89446 | 10.968 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.89278 | 11.06 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.88593 | 11.788 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99242 | 0.85308 | 13.934 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99242 | 0.85753 | 13.489 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99242 | 0.85916 | 13.326 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99242 | 0.87165 | 12.077 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99242 | 0.87355 | 11.887 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99242 | 0.87934 | 11.308 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99242 | 0.88095 | 11.147 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.006 | 0.88133 | 12.465 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.88819 | 11.477 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.88847 | 11.475 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.89514 | 10.84 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.88602 | 11.46 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.90497 | 10.13 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.86814 | 12.614 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99428 | 0.87347 | 12.082 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.87132 | 13.201 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99296 | 0.85251 | 14.044 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99296 | 0.8528 | 14.016 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99296 | 0.88374 | 10.921 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99296 | 0.8864 | 10.656 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99887 | 0.85788 | 14.099 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.88906 | 11.714 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.89369 | 10.952 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99706 | 0.85603 | 14.103 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.85984 | 13.722 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.88098 | 12.278 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99831 | 0.87827 | 12.004 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99831 | 0.88321 | 11.511 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.88496 | 11.769 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.88954 | 11.423 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.893 | 11.06 | Yes
Active | 2025W1-N11-WVD247791 | 247791 | 05ELK | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.89267 | 11.084 | Yes
Active | 2025W1-N11-WVD247799 | 247799 | 05S.OLIVE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99587 | 0.91294 | 8.294 | Yes
Active | 2025W1-N11-WVD247799 | 247799 | 05S.OLIVE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.91422 | 8.166 | Yes
Active | 2025W1-N11-WVD247799 | 247799 | 05S.OLIVE SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99708 | 0.9168 | 8.028 | Yes
Active | 2025W1-N11-WVD247799 | 247799 | 05S.OLIVE SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99725 | 0.91428 | 8.297 | Yes
Active | 2025W1-N11-WVD247829 | 247829 | 05AVIATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99567 | 0.88027 | 11.54 | Yes
Active | 2025W1-N11-WVD247829 | 247829 | 05AVIATION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99391 | 0.91304 | 8.087 | Yes
Active | 2025W1-N11-WVD247829 | 247829 | 05AVIATION | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97539 | 0.89321 | 8.218 | Yes
Active | 2025W1-N11-WVD247831 | 247831 | 05DALMATN SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99392 | 0.87842 | 11.551 | Yes
Active | 2025W1-N11-WVD247831 | 247831 | 05DALMATN SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99216 | 0.9109 | 8.125 | Yes
Active | 2025W1-N11-WVD247831 | 247831 | 05DALMATN SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9733 | 0.89132 | 8.198 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.85155 | 14.303 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99426 | 0.84785 | 14.641 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99364 | 0.84844 | 14.52 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.83648 | 15.868 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98025 | 0.79838 | 18.187 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98025 | 0.80595 | 17.43 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98025 | 0.80639 | 17.386 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98025 | 0.81208 | 16.817 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98025 | 0.82375 | 15.65 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98025 | 0.82884 | 15.141 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98025 | 0.83391 | 14.634 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9974 | 0.83046 | 16.694 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.83808 | 15.432 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99288 | 0.83859 | 15.429 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99446 | 0.85166 | 14.28 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.84452 | 14.747 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.86979 | 12.727 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98815 | 0.80687 | 18.128 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98815 | 0.8164 | 17.175 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99512 | 0.82084 | 17.428 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98256 | 0.79798 | 18.458 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98256 | 0.80045 | 18.21 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98256 | 0.83384 | 14.871 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98256 | 0.83653 | 14.603 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.90927 | 8.574 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98875 | 0.80439 | 18.435 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99754 | 0.84403 | 15.351 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.84873 | 14.505 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98595 | 0.80282 | 18.313 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98595 | 0.80755 | 17.84 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.8353 | 15.989 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98609 | 0.82537 | 16.073 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98609 | 0.83192 | 15.418 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99286 | 0.83455 | 15.831 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.8403 | 15.359 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.84633 | 14.737 | Yes
Active | 2025W1-N11-WVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.84567 | 14.784 | Yes
Active | 2025W1-N11-WVD247864 | 247864 | 05LOGTOWN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98556 | 0.89234 | 9.321 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98457 | 0.9021 | 8.248 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97981 | 0.88584 | 9.397 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98119 | 0.79777 | 18.342 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98137 | 0.794 | 18.737 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98023 | 0.79661 | 18.361 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98374 | 0.78414 | 19.96 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97758 | 0.87863 | 9.895 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96358 | 0.73556 | 22.803 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96358 | 0.75066 | 21.293 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96358 | 0.75851 | 20.507 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96358 | 0.76739 | 19.619 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96358 | 0.77888 | 18.47 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96358 | 0.87659 | 8.699 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98545 | 0.763 | 22.245 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98473 | 0.90345 | 8.128 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98009 | 0.89916 | 8.093 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97905 | 0.78447 | 19.458 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97971 | 0.78506 | 19.466 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98324 | 0.89874 | 8.45 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98378 | 0.90253 | 8.124 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98385 | 0.90254 | 8.131 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9813 | 0.79867 | 18.262 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97782 | 0.79163 | 18.619 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97782 | 0.88964 | 8.818 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98146 | 0.89655 | 8.491 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98432 | 0.90271 | 8.162 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97899 | 0.78906 | 18.992 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9764 | 0.77798 | 19.842 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9764 | 0.78948 | 18.692 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98515 | 0.76181 | 22.334 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96896 | 0.73519 | 23.377 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96896 | 0.75557 | 21.339 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96896 | 0.76953 | 19.943 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96896 | 0.79077 | 17.819 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97812 | 0.86558 | 11.253 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97681 | 0.74595 | 23.086 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98465 | 0.78969 | 19.496 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.79437 | 18.566 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9778 | 0.75493 | 22.287 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9778 | 0.75709 | 22.071 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98816 | 0.78855 | 19.961 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98816 | 0.8975 | 9.066 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97327 | 0.77292 | 20.035 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97327 | 0.78323 | 19.004 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98394 | 0.88032 | 10.362 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98366 | 0.90134 | 8.232 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97758 | 0.87863 | 9.895 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98261 | 0.89261 | 9 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98255 | 0.89317 | 8.939 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9804 | 0.78176 | 19.864 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9804 | 0.88838 | 9.202 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98114 | 0.78694 | 19.42 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98105 | 0.79364 | 18.741 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98298 | 0.88672 | 9.626 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98213 | 0.89507 | 8.705 | Yes
Active | 2025W1-N11-WVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9808 | 0.79231 | 18.849 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99824 | 0.90094 | 9.73 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99824 | 0.90632 | 9.192 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99824 | 0.91781 | 8.043 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.92018 | 8.329 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.91639 | 8.674 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99843 | 0.8926 | 10.583 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99843 | 0.90541 | 9.303 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99062 | 0.89787 | 9.275 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.90492 | 8.57 | Yes
Active | 2025W1-N11-WVD247893 | 247893 | 05FLAG CITY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.91919 | 8.111 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.81965 | 17.005 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98963 | 0.81333 | 17.631 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98858 | 0.81731 | 17.127 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.80209 | 19.139 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.89541 | 9.092 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97396 | 0.7602 | 21.376 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97396 | 0.77201 | 20.196 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97396 | 0.77563 | 19.833 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97396 | 0.78966 | 18.431 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97396 | 0.79462 | 17.934 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97396 | 0.80382 | 17.014 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97396 | 0.80722 | 16.674 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97396 | 0.88876 | 8.521 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97396 | 0.89272 | 8.124 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99344 | 0.79028 | 20.316 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98677 | 0.80077 | 18.6 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98759 | 0.80157 | 18.603 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98981 | 0.8204 | 16.942 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98667 | 0.81344 | 17.323 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98667 | 0.90506 | 8.161 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98724 | 0.80985 | 17.738 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.79749 | 18.813 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98562 | 0.80832 | 17.73 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99234 | 0.78508 | 20.726 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9783 | 0.75981 | 21.849 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9783 | 0.77155 | 20.675 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9783 | 0.79555 | 18.275 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9783 | 0.80553 | 17.277 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98713 | 0.88345 | 10.368 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9844 | 0.76825 | 21.614 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99313 | 0.81157 | 18.156 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98864 | 0.81632 | 17.232 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9832 | 0.77172 | 21.148 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9832 | 0.77501 | 20.819 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99385 | 0.80694 | 18.691 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99385 | 0.90878 | 8.507 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98054 | 0.78939 | 19.115 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98054 | 0.79879 | 18.174 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.89769 | 9.438 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.89541 | 9.092 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.90705 | 8.35 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99047 | 0.90758 | 8.289 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98926 | 0.7987 | 19.056 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98926 | 0.90183 | 8.743 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98934 | 0.80395 | 18.54 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98932 | 0.81313 | 17.62 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99121 | 0.9021 | 8.911 | Yes
Active | 2025W1-N11-WVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.81148 | 17.753 | Yes
Active | 2025W1-N11-WVD247918 | 247918 | 05HENDERSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0104 | 0.89868 | 11.168 | Yes
Active | 2025W1-N11-WVD247918 | 247918 | 05HENDERSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0086 | 0.92593 | 8.271 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.87713 | 12.756 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.87534 | 12.959 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.87464 | 12.959 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.8656 | 13.943 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99157 | 0.82775 | 16.382 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99157 | 0.83523 | 15.635 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99157 | 0.83575 | 15.582 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99157 | 0.84415 | 14.742 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99157 | 0.85147 | 14.01 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99157 | 0.85945 | 13.212 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99157 | 0.86088 | 13.069 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0074 | 0.85961 | 14.778 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.86777 | 13.577 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.86814 | 13.573 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.87676 | 12.781 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.86756 | 13.377 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.8884 | 11.873 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99547 | 0.83978 | 15.569 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99547 | 0.84755 | 14.792 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.84883 | 15.595 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.82719 | 16.597 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99316 | 0.83066 | 16.25 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99316 | 0.8625 | 13.066 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99316 | 0.86649 | 12.667 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9996 | 0.83354 | 16.606 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.86994 | 13.777 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.87466 | 12.927 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99774 | 0.83351 | 16.422 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99774 | 0.83762 | 16.011 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.86227 | 14.312 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99822 | 0.85627 | 14.195 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99822 | 0.86257 | 13.565 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.86428 | 13.919 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.86948 | 13.511 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.87391 | 13.051 | Yes
Active | 2025W1-N11-WVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.87341 | 13.088 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99799 | 0.91351 | 8.448 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99682 | 0.81876 | 17.806 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9972 | 0.81446 | 18.274 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.81763 | 17.855 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.80348 | 19.678 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.89395 | 9.591 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98167 | 0.7567 | 22.496 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98167 | 0.76876 | 21.291 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98167 | 0.77471 | 20.696 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98167 | 0.78726 | 19.441 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98167 | 0.79645 | 18.522 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98167 | 0.8025 | 17.917 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98167 | 0.80663 | 17.504 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.98167 | 0.89125 | 9.041 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.98167 | 0.89565 | 8.602 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0009 | 0.78822 | 21.263 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.80314 | 19.154 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99541 | 0.80384 | 19.156 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99702 | 0.81985 | 17.716 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.81232 | 18.126 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99358 | 0.90952 | 8.406 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99728 | 0.91702 | 8.026 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.995 | 0.80919 | 18.581 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.79624 | 19.685 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99309 | 0.80823 | 18.486 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.78287 | 21.684 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.75632 | 23.039 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98672 | 0.77126 | 21.546 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98672 | 0.79337 | 19.335 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98672 | 0.80838 | 17.834 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.88784 | 10.692 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.76517 | 22.653 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.80985 | 19.069 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.81516 | 18.048 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99217 | 0.77169 | 22.049 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.77433 | 21.784 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.80655 | 19.511 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.91441 | 8.725 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.79143 | 19.858 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99001 | 0.80166 | 18.835 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99925 | 0.90143 | 9.782 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.89395 | 9.591 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99838 | 0.91311 | 8.527 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99833 | 0.91366 | 8.467 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.80063 | 19.596 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99659 | 0.90804 | 8.855 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99695 | 0.806 | 19.095 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99687 | 0.81408 | 18.279 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99874 | 0.90695 | 9.179 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.91543 | 8.239 | Yes
Active | 2025W1-N11-WVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9966 | 0.81259 | 18.401 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99698 | 0.8827 | 11.428 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99748 | 0.88096 | 11.651 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99677 | 0.88008 | 11.669 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99743 | 0.8726 | 12.483 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98499 | 0.83677 | 14.822 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98499 | 0.84382 | 14.117 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98499 | 0.84509 | 13.99 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98499 | 0.85874 | 12.625 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98499 | 0.85922 | 12.577 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98499 | 0.86731 | 11.768 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98499 | 0.86743 | 11.756 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99947 | 0.86713 | 13.233 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.87475 | 12.163 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99664 | 0.87505 | 12.158 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.88204 | 11.461 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99344 | 0.87189 | 12.155 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99831 | 0.88615 | 11.216 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98839 | 0.85549 | 13.29 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98839 | 0.86129 | 12.71 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.85642 | 14.005 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98558 | 0.83618 | 14.94 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98558 | 0.83992 | 14.567 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98558 | 0.86964 | 11.594 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98558 | 0.87322 | 11.236 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99226 | 0.84245 | 14.981 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99989 | 0.87561 | 12.428 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.88061 | 11.57 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99174 | 0.84289 | 14.885 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99174 | 0.84704 | 14.47 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99794 | 0.86878 | 12.916 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.86445 | 12.764 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99209 | 0.86983 | 12.226 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99623 | 0.87157 | 12.466 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99722 | 0.8762 | 12.102 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99709 | 0.87989 | 11.721 | Yes
Active | 2025W1-N11-WVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.997 | 0.87935 | 11.765 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9896 | 0.89005 | 9.955 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9896 | 0.89618 | 9.342 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9896 | 0.90688 | 8.272 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99529 | 0.90997 | 8.532 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99489 | 0.90642 | 8.847 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9897 | 0.88125 | 10.845 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.8954 | 9.43 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98097 | 0.88702 | 9.395 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98097 | 0.89468 | 8.629 | Yes
Active | 2025W1-N11-WVD247957 | 247957 | 05RADER ROAD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99174 | 0.90889 | 8.285 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98667 | 0.88805 | 9.862 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98667 | 0.89442 | 9.225 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98667 | 0.90448 | 8.22 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99233 | 0.9079 | 8.444 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.90446 | 8.746 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98674 | 0.87923 | 10.752 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98674 | 0.8937 | 9.304 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97791 | 0.88526 | 9.266 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97791 | 0.893 | 8.492 | Yes
Active | 2025W1-N11-WVD247960 | 247960 | 05SHAWTOWNSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98874 | 0.90674 | 8.2 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.91267 | 8.298 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.90212 | 9.029 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99167 | 0.81374 | 17.793 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.81187 | 18.008 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.81297 | 17.806 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.80378 | 18.862 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.89555 | 9.574 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97092 | 0.74909 | 22.183 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97092 | 0.76383 | 20.709 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97092 | 0.77206 | 19.886 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97092 | 0.78061 | 19.031 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97092 | 0.79669 | 17.423 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97092 | 0.80317 | 16.775 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97092 | 0.88171 | 8.921 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97092 | 0.88396 | 8.696 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99602 | 0.78032 | 21.57 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.91519 | 8.021 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.91107 | 8.009 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9908 | 0.80627 | 18.453 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.80665 | 18.456 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99364 | 0.90957 | 8.408 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.91351 | 8.075 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.91346 | 8.087 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9922 | 0.813 | 17.921 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9874 | 0.80533 | 18.207 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9874 | 0.9 | 8.74 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.90821 | 8.391 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.91451 | 8.054 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99023 | 0.80601 | 18.422 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.79529 | 19.196 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98726 | 0.80816 | 17.91 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.77722 | 21.826 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97664 | 0.74878 | 22.786 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97664 | 0.77082 | 20.582 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97664 | 0.78457 | 19.207 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97664 | 0.80999 | 16.665 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98894 | 0.87883 | 11.01 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.76102 | 22.702 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99574 | 0.80401 | 19.173 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.81052 | 18.012 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9877 | 0.77225 | 21.545 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9877 | 0.77272 | 21.499 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99781 | 0.80415 | 19.366 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99781 | 0.90985 | 8.796 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98476 | 0.79258 | 19.217 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98476 | 0.80441 | 18.035 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.89003 | 10.479 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.91233 | 8.185 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.89555 | 9.574 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.89987 | 9.08 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99054 | 0.90044 | 9.01 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99051 | 0.80244 | 18.807 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99051 | 0.90315 | 8.736 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99206 | 0.80805 | 18.401 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99161 | 0.81123 | 18.038 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.89891 | 9.444 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99262 | 0.90661 | 8.6 | Yes
Active | 2025W1-N11-WVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99144 | 0.81022 | 18.122 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.90717 | 9.599 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.90453 | 9.928 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90413 | 9.927 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.89854 | 10.543 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99546 | 0.86376 | 13.17 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99546 | 0.87144 | 12.402 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99546 | 0.87592 | 11.955 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99546 | 0.88403 | 11.143 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99546 | 0.89428 | 10.118 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99546 | 0.89515 | 10.031 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99546 | 0.89583 | 9.963 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0043 | 0.89227 | 11.205 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.9001 | 10.327 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.90035 | 10.315 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.90123 | 10.104 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99549 | 0.88625 | 10.924 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.90062 | 10.256 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.89027 | 11.131 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.89747 | 10.411 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.88107 | 12.272 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99874 | 0.86324 | 13.55 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99874 | 0.87173 | 12.701 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99874 | 0.89522 | 10.352 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99874 | 0.90186 | 9.688 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.86925 | 13.279 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.89868 | 10.622 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.90565 | 9.716 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.87361 | 12.84 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.87634 | 12.567 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.89566 | 10.902 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.8918 | 10.985 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.89812 | 10.353 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.89771 | 10.569 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.90127 | 10.25 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.90405 | 9.965 | Yes
Active | 2025W1-N11-WVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.90348 | 10.018 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.89666 | 10.703 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.89383 | 11.061 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.89352 | 11.049 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0046 | 0.8871 | 11.752 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99559 | 0.84842 | 14.717 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99559 | 0.85687 | 13.872 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99559 | 0.86186 | 13.373 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99559 | 0.87096 | 12.464 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99559 | 0.88226 | 11.334 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99559 | 0.88313 | 11.246 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99559 | 0.88416 | 11.144 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0052 | 0.87956 | 12.56 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.8888 | 11.513 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.88909 | 11.498 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.89041 | 11.236 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.87412 | 12.11 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.88952 | 11.422 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.87791 | 12.403 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.88649 | 11.546 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.86781 | 13.665 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99883 | 0.84781 | 15.103 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99883 | 0.85827 | 14.056 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99883 | 0.88271 | 11.613 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99883 | 0.8912 | 10.763 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.85455 | 14.787 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.88735 | 11.83 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.89493 | 10.835 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.86031 | 14.202 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.86243 | 13.99 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.88412 | 12.124 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.87953 | 12.247 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.88718 | 11.483 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.88615 | 11.782 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.89013 | 11.425 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.89329 | 11.102 | Yes
Active | 2025W1-N11-WVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.89265 | 11.162 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98919 | 0.88656 | 10.263 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98919 | 0.89262 | 9.656 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98919 | 0.8962 | 9.299 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98919 | 0.90302 | 8.617 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99415 | 0.90957 | 8.458 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.90726 | 8.317 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.90934 | 8.382 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99316 | 0.912 | 8.116 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99376 | 0.90066 | 9.31 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.88636 | 10.502 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99138 | 0.88903 | 10.235 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99323 | 0.89097 | 10.226 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.91402 | 8.038 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99361 | 0.89073 | 10.287 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.89658 | 9.703 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99444 | 0.91146 | 8.298 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.90946 | 8.374 | Yes
Active | 2025W1-N11-WVD247981 | 247981 | 05CHANDLR SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9932 | 0.91176 | 8.144 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98924 | 0.89069 | 9.856 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98924 | 0.89688 | 9.237 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98924 | 0.90024 | 8.901 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98924 | 0.90649 | 8.276 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99396 | 0.91257 | 8.139 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.90866 | 8.086 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.91241 | 8.063 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.90403 | 8.966 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99127 | 0.8905 | 10.077 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99127 | 0.89257 | 9.87 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99313 | 0.89509 | 9.804 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99349 | 0.89415 | 9.934 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99349 | 0.90045 | 9.304 | Yes
Active | 2025W1-N11-WVD247982 | 247982 | 05E.NEWCONSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99303 | 0.91265 | 8.037 | Yes
Active | 2025W1-N11-WVD253002 | 253002 | 09AIRWAY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98711 | 0.88429 | 10.282 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.986 | 0.85472 | 13.128 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.986 | 0.86154 | 12.445 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.986 | 0.87856 | 10.744 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.986 | 0.8825 | 10.35 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99695 | 0.88066 | 11.629 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9922 | 0.89179 | 10.041 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.87663 | 11.936 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98633 | 0.84445 | 14.188 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.86111 | 12.522 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99101 | 0.88648 | 10.452 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97805 | 0.84952 | 12.853 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97805 | 0.85909 | 11.896 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99237 | 0.88091 | 11.146 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99017 | 0.88979 | 10.038 | Yes
Active | 2025W1-N11-WVD253004 | 253004 | 09AMSTRD | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99017 | 0.88982 | 10.035 | Yes
Active | 2025W1-N11-WVD253005 | 253005 | 09BATH | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99183 | 0.88582 | 10.601 | Yes
Active | 2025W1-N11-WVD253005 | 253005 | 09BATH | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99229 | 0.88012 | 11.217 | Yes
Active | 2025W1-N11-WVD253005 | 253005 | 09BATH | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98714 | 0.8816 | 10.553 | Yes
Active | 2025W1-N11-WVD253005 | 253005 | 09BATH | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98714 | 0.8867 | 10.044 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97412 | 0.87468 | 9.944 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97412 | 0.88322 | 9.09 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97412 | 0.89215 | 8.197 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97412 | 0.89225 | 8.187 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98355 | 0.89927 | 8.428 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98227 | 0.89416 | 8.811 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97468 | 0.86928 | 10.54 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97468 | 0.88291 | 9.177 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97796 | 0.89091 | 8.705 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96937 | 0.87105 | 9.831 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96937 | 0.87603 | 9.334 | Yes
Active | 2025W1-N11-WVD253006 | 253006 | 09BATH | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97937 | 0.89455 | 8.482 | Yes
Active | 2025W1-N11-WVD253014 | 253014 | 09CLINTO | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99231 | 0.90274 | 8.957 | Yes
Active | 2025W1-N11-WVD253014 | 253014 | 09CLINTO | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99231 | 0.91073 | 8.158 | Yes
Active | 2025W1-N11-WVD253014 | 253014 | 09CLINTO | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99274 | 0.89812 | 9.462 | Yes
Active | 2025W1-N11-WVD253014 | 253014 | 09CLINTO | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99274 | 0.91042 | 8.232 | Yes
Active | 2025W1-N11-WVD253014 | 253014 | 09CLINTO | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98857 | 0.8999 | 8.868 | Yes
Active | 2025W1-N11-WVD253014 | 253014 | 09CLINTO | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98857 | 0.90408 | 8.45 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97386 | 0.80061 | 17.325 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97344 | 0.79816 | 17.528 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97272 | 0.79929 | 17.343 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97306 | 0.79263 | 18.043 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95257 | 0.74103 | 21.154 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95257 | 0.75601 | 19.655 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95257 | 0.75727 | 19.53 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95257 | 0.76956 | 18.3 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95257 | 0.78273 | 16.983 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97923 | 0.76963 | 20.96 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97323 | 0.79694 | 17.63 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97363 | 0.79717 | 17.646 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97385 | 0.80049 | 17.336 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97088 | 0.79454 | 17.635 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97223 | 0.79362 | 17.861 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96774 | 0.78256 | 18.519 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96774 | 0.79237 | 17.538 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97815 | 0.76768 | 21.047 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95761 | 0.7413 | 21.631 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95761 | 0.7544 | 20.321 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95761 | 0.77242 | 18.518 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95761 | 0.79333 | 16.427 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96846 | 0.85803 | 11.043 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9676 | 0.75399 | 21.361 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97883 | 0.79368 | 18.514 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97283 | 0.79765 | 17.519 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96608 | 0.75607 | 21.001 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96608 | 0.75887 | 20.721 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97982 | 0.79015 | 18.967 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96484 | 0.77925 | 18.559 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96484 | 0.78803 | 17.682 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97643 | 0.87499 | 10.145 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97158 | 0.79188 | 17.97 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97427 | 0.79822 | 17.605 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97293 | 0.79729 | 17.564 | Yes
Active | 2025W1-N11-WVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97272 | 0.79643 | 17.629 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.89179 | 10.053 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99153 | 0.89065 | 10.089 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9912 | 0.88935 | 10.185 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98096 | 0.84493 | 13.603 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98096 | 0.85024 | 13.072 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98096 | 0.86995 | 11.101 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98096 | 0.87076 | 11.02 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98096 | 0.8752 | 10.576 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99387 | 0.87064 | 12.323 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99202 | 0.89078 | 10.124 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.88686 | 10.336 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99072 | 0.8872 | 10.351 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98817 | 0.88032 | 10.786 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98817 | 0.88172 | 10.645 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99259 | 0.86625 | 12.633 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98139 | 0.83537 | 14.602 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98139 | 0.84971 | 13.168 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98139 | 0.87517 | 10.622 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98705 | 0.87213 | 11.492 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99404 | 0.89014 | 10.39 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.8901 | 10.172 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97406 | 0.83802 | 13.605 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97406 | 0.8468 | 12.726 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98954 | 0.87191 | 11.763 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98548 | 0.87763 | 10.784 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98548 | 0.87839 | 10.709 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.88937 | 10.159 | Yes
Active | 2025W1-N11-WVD253024 | 253024 | 09ESIDNY | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.88907 | 10.175 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96727 | 0.81003 | 15.724 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96603 | 0.80699 | 15.905 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96597 | 0.80804 | 15.793 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96394 | 0.80519 | 15.875 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95141 | 0.76247 | 18.894 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95141 | 0.76686 | 18.455 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95141 | 0.77492 | 17.65 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95141 | 0.78587 | 16.554 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95141 | 0.79421 | 15.721 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97093 | 0.78569 | 18.524 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96697 | 0.81193 | 15.504 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96729 | 0.81194 | 15.535 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96715 | 0.80967 | 15.748 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96426 | 0.8045 | 15.976 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96482 | 0.80326 | 16.156 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96133 | 0.79382 | 16.752 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96133 | 0.80061 | 16.072 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96937 | 0.78104 | 18.833 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95267 | 0.7605 | 19.218 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95267 | 0.761 | 19.168 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95267 | 0.78956 | 16.311 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95267 | 0.79975 | 15.292 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9611 | 0.85716 | 10.395 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96005 | 0.77104 | 18.9 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9708 | 0.80408 | 16.673 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96635 | 0.80758 | 15.877 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95383 | 0.7619 | 19.193 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95383 | 0.76654 | 18.729 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96872 | 0.79505 | 17.367 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9567 | 0.78904 | 16.765 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9567 | 0.7949 | 16.179 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95274 | 0.8523 | 10.044 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96221 | 0.80441 | 15.78 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96754 | 0.81246 | 15.508 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96534 | 0.80579 | 15.955 | Yes
Active | 2025W1-N11-WVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9651 | 0.80519 | 15.991 | Yes
Active | 2025W1-N11-WVD253026 | 253026 | 09GREENE | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98986 | 0.88449 | 10.537 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97549 | 0.87353 | 10.196 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97549 | 0.88168 | 9.381 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97549 | 0.88982 | 8.567 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97549 | 0.89162 | 8.388 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97549 | 0.89514 | 8.035 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98527 | 0.89827 | 8.7 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9799 | 0.89956 | 8.034 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98395 | 0.89296 | 9.099 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9762 | 0.86832 | 10.789 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9762 | 0.88137 | 9.483 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97943 | 0.88851 | 9.093 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97107 | 0.86999 | 10.109 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97107 | 0.87477 | 9.631 | Yes
Active | 2025W1-N11-WVD253027 | 253027 | 09GREENE | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98118 | 0.89391 | 8.727 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97335 | 0.85693 | 11.642 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97335 | 0.86375 | 10.96 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98534 | 0.88313 | 10.221 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98413 | 0.87873 | 10.54 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97356 | 0.84834 | 12.522 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97356 | 0.86333 | 11.023 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96618 | 0.8503 | 11.588 | Yes
Active | 2025W1-N11-WVD253031 | 253031 | 09HALTER | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96618 | 0.85825 | 10.793 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97803 | 0.85175 | 12.629 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97705 | 0.84989 | 12.716 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97683 | 0.84947 | 12.735 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97595 | 0.85183 | 12.412 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96632 | 0.804 | 16.232 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96632 | 0.80712 | 15.921 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96632 | 0.82964 | 13.668 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96632 | 0.83042 | 13.591 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96632 | 0.83342 | 13.291 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96632 | 0.84176 | 12.456 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96632 | 0.84636 | 11.996 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97989 | 0.82752 | 15.237 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.979 | 0.85799 | 12.101 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97917 | 0.85789 | 12.129 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9777 | 0.85065 | 12.705 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9758 | 0.84646 | 12.934 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97644 | 0.84639 | 13.005 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97397 | 0.83884 | 13.513 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97397 | 0.84199 | 13.199 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97817 | 0.82265 | 15.551 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96721 | 0.79476 | 17.245 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96721 | 0.80628 | 16.093 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96721 | 0.83406 | 13.315 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96721 | 0.84427 | 12.294 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97223 | 0.82612 | 14.61 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97999 | 0.8486 | 13.139 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97737 | 0.84971 | 12.766 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9604 | 0.79645 | 16.395 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9604 | 0.8046 | 15.58 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97579 | 0.8319 | 14.39 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97119 | 0.8359 | 13.53 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97119 | 0.83824 | 13.296 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97539 | 0.85171 | 12.368 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97913 | 0.85803 | 12.11 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97647 | 0.84868 | 12.779 | Yes
Active | 2025W1-N11-WVD253042 | 253042 | 09LOGAN | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9763 | 0.84824 | 12.806 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96923 | 0.8056 | 16.364 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9683 | 0.80274 | 16.555 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96799 | 0.80388 | 16.411 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9668 | 0.79936 | 16.745 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95128 | 0.75338 | 19.79 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95128 | 0.76204 | 18.923 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95128 | 0.76668 | 18.46 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95128 | 0.77876 | 17.252 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95128 | 0.78892 | 16.236 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97354 | 0.77878 | 19.476 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96877 | 0.80523 | 16.355 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96913 | 0.80532 | 16.38 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96915 | 0.80531 | 16.384 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96622 | 0.79983 | 16.639 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96708 | 0.79871 | 16.837 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96322 | 0.78867 | 17.455 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96322 | 0.7966 | 16.661 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97215 | 0.77505 | 19.71 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95397 | 0.75256 | 20.141 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95397 | 0.75695 | 19.702 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95397 | 0.78223 | 17.173 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95397 | 0.79639 | 15.758 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96333 | 0.85671 | 10.661 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96233 | 0.7635 | 19.883 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97331 | 0.7992 | 17.411 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96827 | 0.80294 | 16.533 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95781 | 0.75845 | 19.936 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95781 | 0.76244 | 19.537 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97236 | 0.79222 | 18.014 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95922 | 0.78441 | 17.481 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95922 | 0.79138 | 16.784 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96517 | 0.79859 | 16.658 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96952 | 0.80606 | 16.347 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96767 | 0.80168 | 16.6 | Yes
Active | 2025W1-N11-WVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96744 | 0.80097 | 16.647 | Yes
Active | 2025W1-N11-WVD253046 | 253046 | 09MIAMI | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98152 | 0.87663 | 10.488 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96775 | 0.86706 | 10.068 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96775 | 0.8754 | 9.235 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96775 | 0.88474 | 8.301 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97722 | 0.89157 | 8.565 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97598 | 0.88702 | 8.896 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96793 | 0.86014 | 10.78 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96793 | 0.87509 | 9.284 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97211 | 0.88862 | 8.349 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96205 | 0.86241 | 9.965 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96205 | 0.86889 | 9.317 | Yes
Active | 2025W1-N11-WVD253047 | 253047 | 09MIAMI | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97295 | 0.88751 | 8.544 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98706 | 0.87647 | 11.059 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98618 | 0.87503 | 11.115 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98591 | 0.87409 | 11.181 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98547 | 0.87906 | 10.641 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9755 | 0.82901 | 14.649 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9755 | 0.83368 | 14.182 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9755 | 0.85497 | 12.053 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9755 | 0.85589 | 11.961 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9755 | 0.85798 | 11.752 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9755 | 0.86651 | 10.899 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9755 | 0.87065 | 10.485 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98873 | 0.85416 | 13.457 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98883 | 0.8852 | 10.363 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98894 | 0.88502 | 10.391 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98674 | 0.87541 | 11.133 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9849 | 0.87139 | 11.351 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.87157 | 11.388 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98292 | 0.86442 | 11.85 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98292 | 0.86648 | 11.644 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.84954 | 13.773 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97611 | 0.81954 | 15.657 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97611 | 0.83303 | 14.308 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97611 | 0.85944 | 11.667 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97611 | 0.86816 | 10.795 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98153 | 0.85446 | 12.708 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98888 | 0.87424 | 11.464 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9865 | 0.87464 | 11.185 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96883 | 0.82183 | 14.701 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96883 | 0.8304 | 13.843 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98444 | 0.85653 | 12.791 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98017 | 0.86161 | 11.856 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98017 | 0.86297 | 11.72 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98488 | 0.87887 | 10.6 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.88496 | 10.377 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98561 | 0.87378 | 11.183 | Yes
Active | 2025W1-N11-WVD253065 | 253065 | 09QUINCY | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.87342 | 11.203 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98354 | 0.85352 | 13.002 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98354 | 0.85918 | 12.435 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98354 | 0.87746 | 10.608 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98354 | 0.87926 | 10.428 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99627 | 0.87952 | 11.675 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99064 | 0.88887 | 10.177 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99064 | 0.88989 | 10.075 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.87527 | 11.982 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98386 | 0.84391 | 13.995 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98386 | 0.85871 | 12.515 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98386 | 0.88363 | 10.023 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98966 | 0.88168 | 10.798 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97649 | 0.84676 | 12.972 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97649 | 0.85566 | 12.083 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.88016 | 11.175 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98797 | 0.88625 | 10.172 | Yes
Active | 2025W1-N11-WVD253068 | 253068 | 09SHELBY | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98797 | 0.88667 | 10.13 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9748 | 0.88713 | 8.767 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9741 | 0.88634 | 8.776 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97374 | 0.8847 | 8.904 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97393 | 0.89319 | 8.073 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96437 | 0.84303 | 12.133 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96437 | 0.84856 | 11.581 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96437 | 0.86533 | 9.904 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96437 | 0.8677 | 9.667 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96437 | 0.87366 | 9.071 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96437 | 0.87816 | 8.621 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96437 | 0.88155 | 8.282 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9762 | 0.86782 | 10.838 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97452 | 0.88621 | 8.831 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97278 | 0.88253 | 9.025 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97319 | 0.88301 | 9.018 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97105 | 0.87693 | 9.411 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97105 | 0.87755 | 9.35 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97513 | 0.86386 | 11.127 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96459 | 0.83361 | 13.098 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96459 | 0.84817 | 11.643 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96459 | 0.87189 | 9.271 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96459 | 0.87865 | 8.594 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97022 | 0.87098 | 9.924 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97641 | 0.88618 | 9.023 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97437 | 0.88564 | 8.873 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95783 | 0.83675 | 12.108 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95783 | 0.84556 | 11.227 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97186 | 0.86803 | 10.383 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96838 | 0.87442 | 9.396 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96838 | 0.87448 | 9.39 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97329 | 0.89291 | 8.038 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97353 | 0.88507 | 8.846 | Yes
Active | 2025W1-N11-WVD253069 | 253069 | 09SHELBY | 345 | 209 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97339 | 0.88483 | 8.856 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9722 | 0.84501 | 12.719 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9722 | 0.85134 | 12.086 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9722 | 0.8686 | 10.36 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9722 | 0.87097 | 10.123 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98594 | 0.87264 | 11.33 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98474 | 0.86825 | 11.649 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97248 | 0.83553 | 13.695 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97248 | 0.85088 | 12.16 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97873 | 0.8737 | 10.503 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96427 | 0.83786 | 12.641 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96427 | 0.84663 | 11.764 | Yes
Active | 2025W1-N11-WVD253071 | 253071 | 09SIDNEY | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98156 | 0.87263 | 10.893 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97315 | 0.85608 | 11.707 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97315 | 0.86287 | 11.028 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98524 | 0.88236 | 10.288 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98403 | 0.87796 | 10.607 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97336 | 0.84743 | 12.593 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97336 | 0.86244 | 11.092 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96593 | 0.84941 | 11.652 | Yes
Active | 2025W1-N11-WVD253072 | 253072 | 09SPRING | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96593 | 0.85741 | 10.852 | Yes
Active | 2025W1-N11-WVD253074 | 253074 | 09STATAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9763 | 0.87314 | 10.316 | Yes
Active | 2025W1-N11-WVD253074 | 253074 | 09STATAP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97653 | 0.86634 | 11.019 | Yes
Active | 2025W1-N11-WVD253074 | 253074 | 09STATAP | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96996 | 0.86743 | 10.253 | Yes
Active | 2025W1-N11-WVD253079 | 253079 | 09SUGRCK | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97683 | 0.88699 | 8.984 | Yes
Active | 2025W1-N11-WVD253079 | 253079 | 09SUGRCK | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97683 | 0.89635 | 8.049 | Yes
Active | 2025W1-N11-WVD253079 | 253079 | 09SUGRCK | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97735 | 0.88234 | 9.501 | Yes
Active | 2025W1-N11-WVD253079 | 253079 | 09SUGRCK | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97735 | 0.89607 | 8.128 | Yes
Active | 2025W1-N11-WVD253079 | 253079 | 09SUGRCK | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97203 | 0.88397 | 8.805 | Yes
Active | 2025W1-N11-WVD253079 | 253079 | 09SUGRCK | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97203 | 0.88825 | 8.377 | Yes
Active | 2025W1-N11-WVD253083 | 253083 | 09TREBEI | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98972 | 0.8892 | 10.052 | Yes
Active | 2025W1-N11-WVD253083 | 253083 | 09TREBEI | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99013 | 0.88382 | 10.632 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96584 | 0.81234 | 15.349 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96442 | 0.8092 | 15.522 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9645 | 0.81018 | 15.432 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.962 | 0.80841 | 15.358 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95119 | 0.76749 | 18.37 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95119 | 0.76952 | 18.167 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95119 | 0.77952 | 17.167 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95119 | 0.78975 | 16.145 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95119 | 0.79703 | 15.416 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96912 | 0.7894 | 17.972 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96563 | 0.81562 | 15 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96593 | 0.81559 | 15.035 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96569 | 0.81194 | 15.375 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96281 | 0.80695 | 15.586 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96321 | 0.80564 | 15.756 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95994 | 0.79655 | 16.339 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95994 | 0.80268 | 15.726 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96746 | 0.78426 | 18.32 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95163 | 0.76245 | 18.918 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95163 | 0.76564 | 18.599 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95163 | 0.79352 | 15.81 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95163 | 0.80147 | 15.016 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95951 | 0.85715 | 10.237 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95843 | 0.77524 | 18.319 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96905 | 0.80668 | 16.238 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96494 | 0.81001 | 15.493 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95128 | 0.7638 | 18.748 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95128 | 0.7688 | 18.248 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96632 | 0.79649 | 16.984 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95494 | 0.79149 | 16.345 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95494 | 0.79671 | 15.823 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94998 | 0.84866 | 10.132 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96022 | 0.80762 | 15.26 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96609 | 0.81598 | 15.011 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96369 | 0.80793 | 15.576 | Yes
Active | 2025W1-N11-WVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96344 | 0.80739 | 15.606 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96825 | 0.87391 | 9.435 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96825 | 0.88317 | 8.508 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97566 | 0.89378 | 8.188 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96834 | 0.86732 | 10.102 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96834 | 0.8829 | 8.544 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96248 | 0.86953 | 9.295 | Yes
Active | 2025W1-N11-WVD253090 | 253090 | 09WMILTN | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96248 | 0.87573 | 8.676 | Yes
Active | 2025W1-N11-WVD253098 | 253098 | 09STAUNT | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97415 | 0.86975 | 10.441 | Yes
Active | 2025W1-N11-WVD253098 | 253098 | 09STAUNT | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9744 | 0.86294 | 11.145 | Yes
Active | 2025W1-N11-WVD253098 | 253098 | 09STAUNT | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96746 | 0.8637 | 10.376 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.86456 | 12.926 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98977 | 0.85292 | 13.685 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.8444 | 15.027 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9813 | 0.81478 | 16.652 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9813 | 0.8187 | 16.26 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9813 | 0.82235 | 15.895 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9813 | 0.83872 | 14.258 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9813 | 0.84771 | 13.359 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9813 | 0.84802 | 13.328 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99618 | 0.84334 | 15.285 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.84406 | 14.595 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99065 | 0.8448 | 14.585 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99379 | 0.86481 | 12.898 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.85923 | 13.248 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9914 | 0.85514 | 13.626 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98869 | 0.84355 | 14.514 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98869 | 0.85108 | 13.761 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99477 | 0.83609 | 15.868 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98399 | 0.81376 | 17.023 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98399 | 0.81468 | 16.931 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98399 | 0.84669 | 13.73 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98832 | 0.82031 | 16.801 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9962 | 0.85809 | 13.811 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99313 | 0.86192 | 13.122 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98377 | 0.81488 | 16.89 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98377 | 0.81943 | 16.434 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99411 | 0.84947 | 14.465 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.84104 | 15.019 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99219 | 0.84723 | 14.496 | Yes
Active | 2025W1-N11-WVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.83193 | 15.837 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.82482 | 15.789 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98243 | 0.82289 | 15.954 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98153 | 0.82288 | 15.864 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98254 | 0.81995 | 16.259 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97022 | 0.77167 | 19.855 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97022 | 0.78238 | 18.784 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97022 | 0.79507 | 17.515 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97022 | 0.79967 | 17.055 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97022 | 0.81363 | 15.659 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97022 | 0.81577 | 15.445 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97022 | 0.82015 | 15.007 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98543 | 0.79347 | 19.195 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98299 | 0.82425 | 15.874 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9833 | 0.82439 | 15.891 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98264 | 0.82367 | 15.897 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98029 | 0.81866 | 16.163 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98168 | 0.81861 | 16.307 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97988 | 0.81016 | 16.972 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97988 | 0.8175 | 16.238 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98408 | 0.78951 | 19.457 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9727 | 0.77039 | 20.231 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9727 | 0.77564 | 19.706 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9727 | 0.80287 | 16.982 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9727 | 0.82214 | 15.056 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97941 | 0.87823 | 10.118 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97841 | 0.78892 | 18.949 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98532 | 0.81995 | 16.536 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98185 | 0.82218 | 15.967 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.975 | 0.77681 | 19.819 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.975 | 0.78189 | 19.311 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98436 | 0.80835 | 17.601 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97804 | 0.80782 | 17.021 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97804 | 0.81414 | 16.39 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9818 | 0.81964 | 16.216 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98374 | 0.82518 | 15.856 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98196 | 0.82195 | 16 | Yes
Active | 2025W1-N11-WVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98178 | 0.82122 | 16.056 | Yes
Active | 2025W1-N11-WVD253106 | 253106 | 09NCARLI | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98432 | 0.88405 | 10.027 | Yes
Active | 2025W1-N11-WVD253106 | 253106 | 09NCARLI | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98462 | 0.87792 | 10.67 | Yes
Active | 2025W1-N11-WVD253139 | 253139 | 09ELDEAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97753 | 0.87402 | 10.351 | Yes
Active | 2025W1-N11-WVD253139 | 253139 | 09ELDEAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97769 | 0.86665 | 11.104 | Yes
Active | 2025W1-N11-WVD253139 | 253139 | 09ELDEAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97125 | 0.86816 | 10.309 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97614 | 0.84662 | 12.952 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97614 | 0.85295 | 12.319 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97614 | 0.87052 | 10.562 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97614 | 0.87309 | 10.305 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98895 | 0.87351 | 11.544 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98323 | 0.88282 | 10.042 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98783 | 0.86923 | 11.86 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97647 | 0.83691 | 13.956 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97647 | 0.85249 | 12.398 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.87596 | 10.621 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96842 | 0.84006 | 12.836 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96842 | 0.84905 | 11.937 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.87376 | 11.078 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98072 | 0.88034 | 10.038 | Yes
Active | 2025W1-N11-WVD253150 | 253150 | 09FRANKL | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98072 | 0.88066 | 10.007 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9699 | 0.8046 | 16.53 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96905 | 0.80181 | 16.724 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96868 | 0.80296 | 16.572 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96773 | 0.79804 | 16.97 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95139 | 0.75114 | 20.024 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95139 | 0.76102 | 19.036 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95139 | 0.7647 | 18.669 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95139 | 0.77706 | 17.433 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95139 | 0.78771 | 16.367 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97438 | 0.77711 | 19.728 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96941 | 0.80365 | 16.576 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96977 | 0.80378 | 16.599 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96983 | 0.80435 | 16.548 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9669 | 0.79878 | 16.811 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96783 | 0.7977 | 17.014 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96386 | 0.78748 | 17.638 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96386 | 0.79573 | 16.813 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97304 | 0.77365 | 19.94 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95446 | 0.7505 | 20.396 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95446 | 0.75628 | 19.818 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95446 | 0.78045 | 17.402 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95446 | 0.79571 | 15.876 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96408 | 0.85679 | 10.729 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9631 | 0.76171 | 20.139 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97412 | 0.79811 | 17.601 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96893 | 0.8019 | 16.703 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95906 | 0.75781 | 20.124 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95906 | 0.76161 | 19.745 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97349 | 0.79169 | 18.18 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96004 | 0.78337 | 17.667 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96004 | 0.79064 | 16.94 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96612 | 0.79727 | 16.885 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97021 | 0.80456 | 16.565 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96844 | 0.80078 | 16.766 | Yes
Active | 2025W1-N11-WVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96822 | 0.80005 | 16.817 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.87611 | 11.646 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.8698 | 12.117 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.87166 | 11.916 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.014 | 0.8246 | 18.942 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9798 | 0.83175 | 14.805 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9798 | 0.83358 | 14.623 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9798 | 0.84125 | 13.855 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9798 | 0.85029 | 12.952 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9798 | 0.85413 | 12.567 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9798 | 0.8586 | 12.121 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9798 | 0.86239 | 11.741 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99495 | 0.85802 | 13.693 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9925 | 0.87614 | 11.636 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99029 | 0.87131 | 11.899 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.86794 | 12.192 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9872 | 0.85838 | 12.882 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9872 | 0.86421 | 12.299 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.85136 | 14.209 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98215 | 0.82647 | 15.568 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98215 | 0.83328 | 14.887 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98215 | 0.85636 | 12.579 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98215 | 0.86119 | 12.096 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98647 | 0.83929 | 14.717 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.87084 | 12.415 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99188 | 0.8739 | 11.799 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97913 | 0.82772 | 15.141 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97913 | 0.83247 | 14.666 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.86014 | 13.157 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97985 | 0.847 | 13.285 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97985 | 0.85214 | 12.771 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99903 | 0.81233 | 18.67 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99903 | 0.91391 | 8.512 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99026 | 0.86872 | 12.154 | Yes
Active | 2025W1-N11-WVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98995 | 0.86775 | 12.22 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98418 | 0.90168 | 8.25 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.82983 | 15.434 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98404 | 0.82813 | 15.592 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98314 | 0.82881 | 15.433 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98429 | 0.82126 | 16.303 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98431 | 0.89884 | 8.547 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96163 | 0.75479 | 20.684 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96163 | 0.78474 | 17.69 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96163 | 0.79229 | 16.934 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96163 | 0.80841 | 15.322 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96163 | 0.81537 | 14.626 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98736 | 0.78418 | 20.318 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98304 | 0.82378 | 15.926 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9834 | 0.82406 | 15.933 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98417 | 0.83013 | 15.403 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98107 | 0.82406 | 15.701 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98107 | 0.89793 | 8.314 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98212 | 0.82307 | 15.905 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97949 | 0.81408 | 16.541 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97949 | 0.81703 | 16.245 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98839 | 0.7881 | 20.029 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96341 | 0.75443 | 20.898 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96341 | 0.77403 | 18.938 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96341 | 0.78948 | 17.393 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96341 | 0.8188 | 14.461 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97867 | 0.8797 | 9.897 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97547 | 0.80546 | 17.001 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98701 | 0.82999 | 15.703 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9833 | 0.82709 | 15.621 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97834 | 0.77564 | 20.27 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97834 | 0.78564 | 19.27 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.82132 | 17.063 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99195 | 0.9065 | 8.545 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9774 | 0.81145 | 16.594 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9774 | 0.81348 | 16.392 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98629 | 0.89455 | 9.174 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98431 | 0.89884 | 8.547 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98533 | 0.90526 | 8.007 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98248 | 0.82007 | 16.241 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98248 | 0.89801 | 8.447 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98415 | 0.82522 | 15.892 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98374 | 0.82755 | 15.619 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98526 | 0.90026 | 8.5 | Yes
Active | 2025W1-N11-WVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9836 | 0.82672 | 15.688 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97118 | 0.8447 | 12.649 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97118 | 0.85108 | 12.011 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97118 | 0.86814 | 10.304 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97118 | 0.87057 | 10.061 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9848 | 0.87225 | 11.254 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9836 | 0.86786 | 11.574 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97146 | 0.83527 | 13.619 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97146 | 0.85062 | 12.084 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97766 | 0.87321 | 10.445 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96331 | 0.83758 | 12.573 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96331 | 0.8463 | 11.701 | Yes
Active | 2025W1-N11-WVD253258 | 253258 | 09MLLCRK | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98042 | 0.87215 | 10.828 | Yes
Active | 2025W1-N11-WVD253266 | 253266 | 09HAAS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98346 | 0.87741 | 10.605 | Yes
Active | 2025W1-N11-WVD253268 | 253268 | 09FURNAS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98365 | 0.88221 | 10.144 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9829 | 0.82594 | 15.697 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98277 | 0.82405 | 15.872 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98179 | 0.82414 | 15.766 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98307 | 0.82016 | 16.291 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96874 | 0.77077 | 19.796 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96874 | 0.78338 | 18.536 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96874 | 0.79303 | 17.571 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96874 | 0.79944 | 16.93 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96874 | 0.8147 | 15.403 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96874 | 0.81574 | 15.3 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96874 | 0.81991 | 14.883 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98574 | 0.79468 | 19.107 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98297 | 0.82388 | 15.909 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9833 | 0.82407 | 15.923 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98291 | 0.82473 | 15.818 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98022 | 0.81953 | 16.069 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98174 | 0.81953 | 16.221 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97979 | 0.81086 | 16.893 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97979 | 0.81909 | 16.07 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98472 | 0.79062 | 19.41 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97163 | 0.76942 | 20.22 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97163 | 0.77747 | 19.416 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97163 | 0.80283 | 16.88 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97163 | 0.82297 | 14.865 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97971 | 0.87946 | 10.025 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97834 | 0.7874 | 19.095 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98565 | 0.82078 | 16.487 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98204 | 0.82328 | 15.876 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97534 | 0.77876 | 19.657 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97534 | 0.7829 | 19.243 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98531 | 0.81071 | 17.461 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97783 | 0.80845 | 16.939 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97783 | 0.81569 | 16.214 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98202 | 0.81958 | 16.244 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98382 | 0.82497 | 15.885 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98234 | 0.82321 | 15.913 | Yes
Active | 2025W1-N11-WVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.82244 | 15.973 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97084 | 0.84495 | 12.589 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97084 | 0.85135 | 11.948 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97084 | 0.86827 | 10.257 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97084 | 0.87074 | 10.01 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98435 | 0.87243 | 11.192 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98314 | 0.86803 | 11.511 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9711 | 0.83556 | 13.554 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9711 | 0.8509 | 12.02 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97729 | 0.87334 | 10.395 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.963 | 0.83784 | 12.516 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.963 | 0.84653 | 11.647 | Yes
Active | 2025W1-N11-WVD253284 | 253284 | 09SMCRP | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97997 | 0.87224 | 10.773 | Yes
Active | 2025W1-N11-WVD253310 | 253310 | 09CLAY | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.92359 | 8.13 | Yes
Active | 2025W1-N11-WVD253311 | 253311 | AC1-085 MAIN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.9236 | 8.129 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.8801 | 10.844 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98768 | 0.87872 | 10.896 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98739 | 0.87771 | 10.968 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98703 | 0.88304 | 10.399 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97702 | 0.83276 | 14.426 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97702 | 0.83758 | 13.944 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97702 | 0.8587 | 11.832 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97702 | 0.85926 | 11.776 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97702 | 0.86201 | 11.501 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97702 | 0.87017 | 10.685 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97702 | 0.87424 | 10.278 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99017 | 0.85803 | 13.214 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99042 | 0.88917 | 10.125 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99052 | 0.88898 | 10.154 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98822 | 0.87905 | 10.917 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.87505 | 11.134 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98692 | 0.87526 | 11.166 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98439 | 0.86817 | 11.622 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98439 | 0.87009 | 11.43 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98875 | 0.85346 | 13.529 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97759 | 0.82328 | 15.431 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97759 | 0.83696 | 14.064 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97759 | 0.86316 | 11.443 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97759 | 0.8717 | 10.589 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98306 | 0.85858 | 12.448 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99033 | 0.87799 | 11.234 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98798 | 0.8783 | 10.968 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9703 | 0.82564 | 14.466 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9703 | 0.83426 | 13.604 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98588 | 0.86017 | 12.571 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98166 | 0.86539 | 11.627 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98166 | 0.86662 | 11.504 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98643 | 0.88284 | 10.359 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99029 | 0.8889 | 10.14 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98711 | 0.87747 | 10.964 | Yes
Active | 2025W1-N11-WVD253373 | 253373 | 09KISER | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98695 | 0.87712 | 10.983 | Yes
Active | 2025W1-N11-WVD253374 | 253374 | AE2-206_MAIN | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9866 | 0.87529 | 11.132 | Yes
Active | 2025W1-N11-WVD253374 | 253374 | AE2-206_MAIN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97052 | 0.8345 | 13.601 | Yes
Active | 2025W1-N11-WVD253389 | 253389 | 09LYNCHB | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99847 | 0.9141 | 8.437 | Yes
Active | 2025W1-N11-WVD253389 | 253389 | 09LYNCHB | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99885 | 0.90981 | 8.904 | Yes
Active | 2025W1-N11-WVD253389 | 253389 | 09LYNCHB | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99508 | 0.9117 | 8.338 | Yes
Active | 2025W1-N11-WVD253390 | 253390 | AE2-221_MAIN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9985 | 0.91414 | 8.436 | Yes
Active | 2025W1-N11-WVD253390 | 253390 | AE2-221_MAIN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99888 | 0.90985 | 8.903 | Yes
Active | 2025W1-N11-WVD253390 | 253390 | AE2-221_MAIN | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99512 | 0.91174 | 8.337 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9865 | 0.84224 | 14.426 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9863 | 0.84061 | 14.569 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98546 | 0.84106 | 14.439 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98645 | 0.83464 | 15.181 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96597 | 0.77178 | 19.42 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96597 | 0.79286 | 17.312 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96597 | 0.80719 | 15.879 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96597 | 0.8241 | 14.187 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96597 | 0.82908 | 13.69 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96597 | 0.82941 | 13.656 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96597 | 0.83294 | 13.303 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98936 | 0.80041 | 18.895 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98554 | 0.83728 | 14.826 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98586 | 0.83752 | 14.834 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98646 | 0.84229 | 14.417 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98349 | 0.83654 | 14.696 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98455 | 0.83589 | 14.866 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98204 | 0.82747 | 15.457 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98204 | 0.82979 | 15.225 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98997 | 0.8025 | 18.747 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96749 | 0.7714 | 19.608 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96749 | 0.78111 | 18.638 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96749 | 0.80606 | 16.143 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96749 | 0.83214 | 13.535 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98069 | 0.88763 | 9.306 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97907 | 0.82097 | 15.809 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98919 | 0.84272 | 14.647 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9857 | 0.8397 | 14.6 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97552 | 0.78285 | 19.267 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97552 | 0.79389 | 18.163 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.83053 | 16.118 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99171 | 0.91006 | 8.165 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98045 | 0.82538 | 15.507 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98045 | 0.82686 | 15.359 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9884 | 0.90276 | 8.564 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98482 | 0.8336 | 15.122 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98651 | 0.83854 | 14.797 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.986 | 0.84002 | 14.598 | Yes
Active | 2025W1-N11-WVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98587 | 0.83927 | 14.66 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.89741 | 10.833 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.89637 | 10.937 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.89624 | 10.909 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.89167 | 11.38 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0046 | 0.85648 | 14.813 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0046 | 0.85903 | 14.558 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0046 | 0.87575 | 12.886 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0046 | 0.8823 | 12.231 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0046 | 0.88609 | 11.852 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0046 | 0.89512 | 10.949 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0046 | 0.89642 | 10.819 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0075 | 0.87747 | 13.004 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0054 | 0.89424 | 11.116 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.89441 | 11.116 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.89248 | 11.232 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.88162 | 11.65 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.89166 | 11.302 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.88341 | 11.971 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.88956 | 11.356 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.87017 | 13.697 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.003 | 0.8469 | 15.613 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.85488 | 14.814 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1.003 | 0.88617 | 11.685 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.003 | 0.89733 | 10.57 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.86497 | 13.596 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.89223 | 11.519 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.89532 | 10.99 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99765 | 0.85402 | 14.363 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99765 | 0.85893 | 13.873 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.88027 | 12.403 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.88318 | 11.928 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.88857 | 11.389 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.89096 | 11.371 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.89521 | 11.068 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.89578 | 10.977 | Yes
Active | 2025W1-N11-WVD270372 | 270372 | AD1-106 TAP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.89519 | 11.028 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0028 | 0.90962 | 9.32 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0028 | 0.9147 | 8.813 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.9242 | 8.294 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0031 | 0.90176 | 10.131 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.91374 | 8.933 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99604 | 0.90691 | 8.913 | Yes
Active | 2025W1-N11-WVD270495 | 270495 | AE1-146 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99604 | 0.91343 | 8.26 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90378 | 9.653 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.90267 | 9.738 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99958 | 0.90211 | 9.746 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99999 | 0.9006 | 9.938 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99719 | 0.86094 | 13.625 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99719 | 0.86665 | 13.054 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99719 | 0.88671 | 11.048 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99719 | 0.88875 | 10.844 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99719 | 0.89336 | 10.383 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99719 | 0.90228 | 9.491 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99719 | 0.90408 | 9.311 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.88259 | 11.917 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.9034 | 9.695 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.90346 | 9.703 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99959 | 0.90051 | 9.908 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99565 | 0.89378 | 10.187 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99909 | 0.8989 | 10.019 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99749 | 0.8924 | 10.509 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99749 | 0.8947 | 10.279 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.87765 | 12.361 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99554 | 0.84928 | 14.626 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99554 | 0.86368 | 13.186 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99554 | 0.89143 | 10.411 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99554 | 0.90192 | 9.362 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9958 | 0.88375 | 11.205 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.90176 | 10.006 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99987 | 0.90207 | 9.78 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98648 | 0.85613 | 13.036 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98648 | 0.86442 | 12.206 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.88349 | 11.356 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99663 | 0.89177 | 10.486 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99663 | 0.89349 | 10.314 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99927 | 0.90013 | 9.914 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.90395 | 9.673 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99982 | 0.90203 | 9.779 | Yes
Active | 2025W1-N11-WVD270584 | 270584 | AE1-091_POI | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99974 | 0.90158 | 9.816 | Yes
Active | 2025W1-N11-WVD276816 | 276816 | AF1-078_MAIN | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9866 | 0.87529 | 11.132 | Yes
Active | 2025W1-N11-WVD276816 | 276816 | AF1-078_MAIN | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97052 | 0.83451 | 13.601 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9904 | 0.90565 | 8.475 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98808 | 0.89469 | 9.34 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98691 | 0.80408 | 18.283 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98862 | 0.9074 | 8.122 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9875 | 0.80324 | 18.426 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.8045 | 18.189 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.79427 | 19.402 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9867 | 0.88793 | 9.878 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96359 | 0.73623 | 22.737 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96359 | 0.75317 | 21.042 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96359 | 0.76661 | 19.698 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96359 | 0.77044 | 19.315 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96359 | 0.78805 | 17.554 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96359 | 0.8782 | 8.539 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9915 | 0.76477 | 22.673 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.90718 | 8.339 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98403 | 0.90059 | 8.344 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9859 | 0.79609 | 18.981 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98635 | 0.79652 | 18.983 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98917 | 0.90254 | 8.662 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98969 | 0.90627 | 8.342 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98977 | 0.90626 | 8.35 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.80546 | 18.166 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98358 | 0.79818 | 18.54 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98358 | 0.89545 | 8.813 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98737 | 0.90047 | 8.69 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99018 | 0.90645 | 8.374 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98523 | 0.7968 | 18.843 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98255 | 0.78642 | 19.614 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98255 | 0.80123 | 18.132 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99148 | 0.76659 | 22.489 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97013 | 0.73586 | 23.427 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97013 | 0.76658 | 20.355 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97013 | 0.76985 | 20.029 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97013 | 0.80346 | 16.667 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98467 | 0.87144 | 11.323 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.75016 | 23.546 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98777 | 0.90596 | 8.181 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.7915 | 19.955 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98569 | 0.80053 | 18.516 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98622 | 0.7671 | 21.912 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98622 | 0.76796 | 21.826 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.79828 | 19.732 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99559 | 0.90614 | 8.945 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98023 | 0.78398 | 19.625 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98023 | 0.79787 | 18.236 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99025 | 0.88391 | 10.633 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98466 | 0.90288 | 8.178 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98466 | 0.90288 | 8.178 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.9051 | 8.448 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9867 | 0.88793 | 9.878 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.89784 | 9.114 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98895 | 0.89837 | 9.057 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.79273 | 19.338 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98611 | 0.89651 | 8.96 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98734 | 0.79803 | 18.931 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9872 | 0.8027 | 18.45 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98906 | 0.89186 | 9.72 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98837 | 0.89955 | 8.882 | Yes
Active | 2025W1-N11-WVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98703 | 0.80165 | 18.539 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.997 | 0.91695 | 8.005 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.997 | 0.91695 | 8.006 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99658 | 0.90787 | 8.871 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9942 | 0.89651 | 9.769 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99288 | 0.7989 | 19.397 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.90894 | 8.534 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99351 | 0.79807 | 19.544 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.79948 | 19.288 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99453 | 0.78897 | 20.557 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.88817 | 10.396 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96917 | 0.73344 | 23.573 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96917 | 0.74911 | 22.006 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96917 | 0.76161 | 20.756 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96917 | 0.76629 | 20.288 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96917 | 0.78282 | 18.634 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96917 | 0.87193 | 9.724 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96917 | 0.87878 | 9.038 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99762 | 0.76202 | 23.56 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99674 | 0.90952 | 8.722 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98441 | 0.89555 | 8.886 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99175 | 0.79058 | 20.117 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99175 | 0.91065 | 8.11 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99225 | 0.79102 | 20.123 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.90463 | 9.067 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99584 | 0.90855 | 8.729 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99591 | 0.90855 | 8.736 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.80055 | 19.243 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99642 | 0.91322 | 8.32 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98949 | 0.79324 | 19.625 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98949 | 0.8968 | 9.269 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.9024 | 9.103 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99634 | 0.90877 | 8.757 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.79153 | 19.962 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99115 | 0.9077 | 8.344 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98846 | 0.78124 | 20.722 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98846 | 0.79549 | 19.297 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.76249 | 23.495 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97593 | 0.73307 | 24.287 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97593 | 0.76124 | 21.47 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97593 | 0.7669 | 20.904 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97593 | 0.79761 | 17.832 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99071 | 0.87175 | 11.896 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.74614 | 24.492 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99432 | 0.90935 | 8.496 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.78707 | 21.005 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99524 | 0.91325 | 8.198 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99154 | 0.79523 | 19.631 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99165 | 0.76201 | 22.964 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99165 | 0.76249 | 22.916 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.79258 | 20.892 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0015 | 0.90733 | 9.417 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98588 | 0.77874 | 20.714 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98588 | 0.79194 | 19.394 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99708 | 0.91684 | 8.024 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99607 | 0.88492 | 11.115 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99542 | 0.91262 | 8.281 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9868 | 0.90088 | 8.592 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9868 | 0.90088 | 8.592 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.90733 | 8.84 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.91182 | 8.32 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.90966 | 8.089 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99056 | 0.90966 | 8.089 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.88817 | 10.396 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.89954 | 9.551 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.90011 | 9.491 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.91481 | 8.114 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.78736 | 20.476 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99212 | 0.89768 | 9.444 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99333 | 0.79258 | 20.075 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99534 | 0.91192 | 8.341 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99319 | 0.79753 | 19.566 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99515 | 0.89313 | 10.203 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.90135 | 9.306 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99567 | 0.9144 | 8.128 | Yes
Active | 2025W1-N11-WVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99301 | 0.79644 | 19.657 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99997 | 0.91947 | 8.05 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99997 | 0.91947 | 8.05 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99955 | 0.91037 | 8.918 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99718 | 0.89897 | 9.821 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.80119 | 19.464 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99731 | 0.91156 | 8.576 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.80041 | 19.607 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.80176 | 19.355 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99741 | 0.79135 | 20.606 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.89108 | 10.43 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97177 | 0.73532 | 23.645 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97177 | 0.75138 | 22.038 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97177 | 0.76409 | 20.767 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97177 | 0.76839 | 20.338 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97177 | 0.7852 | 18.656 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97177 | 0.79423 | 17.754 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97177 | 0.87438 | 9.738 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97177 | 0.88111 | 9.066 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.76362 | 23.701 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.91203 | 8.768 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98702 | 0.89759 | 8.943 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.79305 | 20.17 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99475 | 0.91338 | 8.137 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99524 | 0.79348 | 20.176 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99826 | 0.90711 | 9.115 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99881 | 0.91105 | 8.776 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99888 | 0.91105 | 8.783 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.80282 | 19.318 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99934 | 0.91569 | 8.365 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99239 | 0.79543 | 19.696 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99239 | 0.89933 | 9.306 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99638 | 0.90489 | 9.149 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99931 | 0.91127 | 8.804 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.79383 | 20.026 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9941 | 0.91032 | 8.378 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99136 | 0.78357 | 20.779 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99136 | 0.79799 | 19.337 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.76461 | 23.589 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97858 | 0.73495 | 24.364 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97858 | 0.76387 | 21.471 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97858 | 0.76851 | 21.007 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97858 | 0.80021 | 17.838 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99364 | 0.8741 | 11.954 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99426 | 0.74843 | 24.583 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99704 | 0.91135 | 8.569 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.78921 | 21.099 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99821 | 0.91579 | 8.242 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.79753 | 19.698 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.76454 | 23.027 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99481 | 0.76518 | 22.963 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.79512 | 20.955 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0047 | 0.91024 | 9.443 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.78117 | 20.765 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98882 | 0.79457 | 19.425 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.91936 | 8.069 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99921 | 0.88734 | 11.187 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99835 | 0.91513 | 8.323 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98977 | 0.90338 | 8.639 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98977 | 0.90338 | 8.639 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9987 | 0.90983 | 8.887 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99795 | 0.91427 | 8.368 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.91182 | 8.132 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.91182 | 8.132 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99538 | 0.89108 | 10.43 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99803 | 0.90207 | 9.596 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.998 | 0.90264 | 9.536 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99893 | 0.91735 | 8.158 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.78978 | 20.527 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99505 | 0.90035 | 9.47 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.79502 | 20.128 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99831 | 0.91446 | 8.386 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99616 | 0.79986 | 19.629 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.89565 | 10.248 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.90387 | 9.352 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99865 | 0.91694 | 8.171 | Yes
Active | 2025W1-N11-WVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.79877 | 19.72 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.91359 | 8.241 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.996 | 0.91359 | 8.241 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.90422 | 9.136 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9932 | 0.89274 | 10.046 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.79161 | 20.014 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99495 | 0.9136 | 8.134 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.90493 | 8.805 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.7909 | 20.152 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99125 | 0.79227 | 19.898 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99347 | 0.7819 | 21.157 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.88417 | 10.698 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.91207 | 8.09 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96731 | 0.72651 | 24.08 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96731 | 0.74171 | 22.561 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96731 | 0.75419 | 21.312 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96731 | 0.75923 | 20.808 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96731 | 0.77577 | 19.154 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96731 | 0.87406 | 9.326 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99658 | 0.75576 | 24.082 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99572 | 0.90597 | 8.975 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98421 | 0.89284 | 9.137 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.91145 | 8.086 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.7835 | 20.712 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99062 | 0.90718 | 8.345 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.78394 | 20.719 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.90092 | 9.334 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99483 | 0.90497 | 8.986 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.90497 | 8.993 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99183 | 0.79325 | 19.857 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.9098 | 8.564 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98828 | 0.78604 | 20.223 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98828 | 0.89277 | 9.55 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99236 | 0.89866 | 9.371 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.90521 | 9.011 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.78437 | 20.566 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99003 | 0.90414 | 8.589 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98733 | 0.7742 | 21.313 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98733 | 0.78836 | 19.897 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99631 | 0.7555 | 24.082 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9743 | 0.72613 | 24.817 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9743 | 0.75384 | 22.045 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9743 | 0.76053 | 21.377 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9743 | 0.79042 | 18.388 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.8672 | 12.247 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98969 | 0.7388 | 25.09 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.9057 | 8.748 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.77991 | 21.623 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.90981 | 8.438 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99037 | 0.78795 | 20.241 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99021 | 0.75463 | 23.558 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99021 | 0.75515 | 23.506 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.78512 | 21.528 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.9034 | 9.699 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98458 | 0.77175 | 21.282 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98458 | 0.78488 | 19.97 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.9135 | 8.257 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99503 | 0.88051 | 11.452 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.90909 | 8.53 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98688 | 0.89853 | 8.835 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98688 | 0.89853 | 8.835 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.90372 | 9.099 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.90841 | 8.559 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98934 | 0.90607 | 8.327 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98934 | 0.90607 | 8.327 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.88417 | 10.698 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.89572 | 9.829 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.89631 | 9.767 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.91143 | 8.349 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99101 | 0.78031 | 21.07 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99101 | 0.8938 | 9.721 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99224 | 0.78548 | 20.676 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99429 | 0.90844 | 8.585 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.79037 | 20.173 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99411 | 0.88906 | 10.505 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.89755 | 9.58 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99463 | 0.91099 | 8.364 | Yes
Active | 2025W1-N11-WVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.78929 | 20.262 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.91358 | 8.241 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.91358 | 8.241 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.90421 | 9.136 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.89272 | 10.046 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99175 | 0.7916 | 20.015 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.91359 | 8.134 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.90492 | 8.805 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99241 | 0.79088 | 20.153 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.79225 | 19.898 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99346 | 0.78189 | 21.157 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.88416 | 10.698 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99296 | 0.91205 | 8.09 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9673 | 0.7265 | 24.081 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9673 | 0.74169 | 22.561 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9673 | 0.75418 | 21.312 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9673 | 0.75922 | 20.808 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9673 | 0.77576 | 19.155 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9673 | 0.87404 | 9.326 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99657 | 0.75575 | 24.082 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99571 | 0.90595 | 8.975 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9842 | 0.89283 | 9.137 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99229 | 0.91143 | 8.086 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99061 | 0.78349 | 20.713 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99061 | 0.90716 | 8.345 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99112 | 0.78392 | 20.72 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99425 | 0.90091 | 9.334 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.90496 | 8.986 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99489 | 0.90496 | 8.993 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.79324 | 19.858 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99542 | 0.90978 | 8.564 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98826 | 0.78603 | 20.224 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98826 | 0.89276 | 9.55 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.89864 | 9.371 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.90519 | 9.011 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.78436 | 20.567 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99002 | 0.90413 | 8.589 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.77418 | 21.313 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98731 | 0.78835 | 19.897 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.75548 | 24.082 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97429 | 0.72611 | 24.817 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97429 | 0.75383 | 22.045 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97429 | 0.76051 | 21.377 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97429 | 0.79041 | 18.388 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98966 | 0.86718 | 12.248 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98968 | 0.73878 | 25.09 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.90569 | 8.748 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.77989 | 21.623 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99418 | 0.9098 | 8.438 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99036 | 0.78794 | 20.242 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.75462 | 23.558 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9902 | 0.75513 | 23.507 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.7851 | 21.528 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.90339 | 9.699 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98457 | 0.77174 | 21.282 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98457 | 0.78487 | 19.97 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99605 | 0.91349 | 8.257 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99502 | 0.8805 | 11.452 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.90908 | 8.53 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98687 | 0.89852 | 8.835 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98687 | 0.89852 | 8.835 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.90371 | 9.099 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.9084 | 8.559 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98933 | 0.90605 | 8.327 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98933 | 0.90606 | 8.327 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99114 | 0.88416 | 10.698 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.89571 | 9.829 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.8963 | 9.767 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.91142 | 8.349 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.991 | 0.78029 | 21.07 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.991 | 0.89379 | 9.721 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99223 | 0.78546 | 20.677 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.90843 | 8.585 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99208 | 0.79035 | 20.173 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.88905 | 10.505 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.89753 | 9.58 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99462 | 0.91098 | 8.364 | Yes
Active | 2025W1-N11-WVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9919 | 0.78927 | 20.262 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.91338 | 8.243 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.91338 | 8.243 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.90401 | 9.138 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.993 | 0.89252 | 10.048 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99157 | 0.79138 | 20.019 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99476 | 0.9134 | 8.136 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.90472 | 8.807 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99223 | 0.79066 | 20.157 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.79203 | 19.903 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99328 | 0.78167 | 21.161 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99096 | 0.88395 | 10.7 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99278 | 0.91186 | 8.092 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96712 | 0.72629 | 24.082 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96712 | 0.74149 | 22.563 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96712 | 0.75397 | 21.315 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96712 | 0.75901 | 20.811 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96712 | 0.77554 | 19.158 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96712 | 0.87384 | 9.328 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99639 | 0.75554 | 24.086 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99552 | 0.90576 | 8.977 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98402 | 0.89263 | 9.139 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.91124 | 8.088 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.78326 | 20.717 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99043 | 0.90697 | 8.346 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.7837 | 20.724 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99407 | 0.90071 | 9.336 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99463 | 0.90476 | 8.988 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.90476 | 8.995 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99164 | 0.79302 | 19.862 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99524 | 0.90959 | 8.565 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98808 | 0.78581 | 20.228 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98808 | 0.89256 | 9.552 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.89844 | 9.373 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99512 | 0.905 | 9.012 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98984 | 0.78414 | 20.57 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98984 | 0.90393 | 8.591 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98713 | 0.77397 | 21.317 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98713 | 0.78812 | 19.901 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.75527 | 24.085 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9741 | 0.72591 | 24.819 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9741 | 0.75362 | 22.048 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9741 | 0.7603 | 21.38 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9741 | 0.79018 | 18.392 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98948 | 0.86698 | 12.25 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.73858 | 25.092 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.90549 | 8.75 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99594 | 0.77967 | 21.627 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.9096 | 8.44 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99017 | 0.78772 | 20.246 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.75441 | 23.561 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99002 | 0.75492 | 23.51 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.78488 | 21.532 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.90319 | 9.701 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98438 | 0.77152 | 21.286 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98438 | 0.78465 | 19.974 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.91329 | 8.258 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99483 | 0.88029 | 11.454 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.90888 | 8.532 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98669 | 0.89832 | 8.837 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98669 | 0.89832 | 8.837 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.90351 | 9.101 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99381 | 0.9082 | 8.56 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98914 | 0.90586 | 8.329 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.90586 | 8.328 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99096 | 0.88395 | 10.7 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.89551 | 9.831 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99378 | 0.8961 | 9.769 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.91123 | 8.351 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.78007 | 21.074 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99082 | 0.89359 | 9.723 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.78524 | 20.681 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.90823 | 8.586 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9919 | 0.79013 | 20.177 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99392 | 0.88885 | 10.507 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99315 | 0.89733 | 9.582 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99444 | 0.91079 | 8.365 | Yes
Active | 2025W1-N11-WVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99172 | 0.78905 | 20.266 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.91225 | 8.252 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.91225 | 8.252 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99435 | 0.90287 | 9.148 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.89136 | 10.06 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99053 | 0.7901 | 20.043 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.91226 | 8.146 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99175 | 0.90358 | 8.817 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.78939 | 20.18 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.79075 | 19.926 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99225 | 0.78041 | 21.184 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.88279 | 10.713 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99174 | 0.91072 | 8.101 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96605 | 0.72512 | 24.093 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96605 | 0.74029 | 22.576 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96605 | 0.75275 | 21.33 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96605 | 0.75778 | 20.827 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96605 | 0.77429 | 19.176 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96605 | 0.87266 | 9.339 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99536 | 0.75432 | 24.104 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.90462 | 8.987 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98297 | 0.89147 | 9.15 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99107 | 0.9101 | 8.097 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98939 | 0.782 | 20.739 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98939 | 0.90583 | 8.356 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9899 | 0.78244 | 20.746 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99304 | 0.89956 | 9.347 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.90362 | 8.998 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99367 | 0.90362 | 9.005 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9906 | 0.79174 | 19.886 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9942 | 0.90845 | 8.575 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98704 | 0.78454 | 20.25 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98704 | 0.8914 | 9.564 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.89729 | 9.384 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.90385 | 9.023 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9888 | 0.78287 | 20.593 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9888 | 0.90279 | 8.601 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98609 | 0.77272 | 21.337 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98609 | 0.78685 | 19.924 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.75405 | 24.104 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97304 | 0.72474 | 24.831 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97304 | 0.7524 | 22.064 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97304 | 0.75907 | 21.397 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97304 | 0.78891 | 18.413 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98844 | 0.86578 | 12.265 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98846 | 0.73738 | 25.107 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.90435 | 8.76 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.77842 | 21.649 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99296 | 0.90847 | 8.449 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98913 | 0.78645 | 20.269 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.75319 | 23.579 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98898 | 0.7537 | 23.527 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.78362 | 21.556 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99917 | 0.90205 | 9.712 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98334 | 0.77028 | 21.306 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98334 | 0.78338 | 19.995 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99484 | 0.91216 | 8.268 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9938 | 0.87912 | 11.468 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.90774 | 8.542 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98564 | 0.89717 | 8.848 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98564 | 0.89717 | 8.848 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.90237 | 9.112 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.90707 | 8.57 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9881 | 0.90472 | 8.339 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9881 | 0.90472 | 8.338 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.88279 | 10.713 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99278 | 0.89436 | 9.842 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.89494 | 9.78 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9937 | 0.91009 | 8.36 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98978 | 0.77882 | 21.096 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98978 | 0.89243 | 9.735 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99101 | 0.78398 | 20.703 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.9071 | 8.596 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.78886 | 20.201 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99288 | 0.88769 | 10.52 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99212 | 0.89618 | 9.593 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9934 | 0.90965 | 8.375 | Yes
Active | 2025W1-N11-WVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99068 | 0.78778 | 20.29 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99459 | 0.91205 | 8.254 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99459 | 0.91205 | 8.254 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99416 | 0.90266 | 9.15 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99178 | 0.89115 | 10.062 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99034 | 0.78987 | 20.047 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99353 | 0.91206 | 8.147 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.90337 | 8.819 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.991 | 0.78916 | 20.185 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98983 | 0.79052 | 19.931 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99206 | 0.78018 | 21.188 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.88257 | 10.716 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99155 | 0.91052 | 8.103 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96586 | 0.72491 | 24.095 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96586 | 0.74007 | 22.578 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96586 | 0.75253 | 21.332 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96586 | 0.75756 | 20.83 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96586 | 0.77406 | 19.18 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96586 | 0.87244 | 9.342 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99517 | 0.7541 | 24.107 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.90441 | 8.989 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98278 | 0.89126 | 9.152 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99089 | 0.9099 | 8.099 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9892 | 0.78177 | 20.743 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9892 | 0.90562 | 8.358 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98971 | 0.78221 | 20.75 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99285 | 0.89936 | 9.349 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99341 | 0.90341 | 9 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.90341 | 9.007 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99041 | 0.79151 | 19.89 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.90824 | 8.577 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98685 | 0.78431 | 20.254 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98685 | 0.89119 | 9.566 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.89708 | 9.386 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9939 | 0.90365 | 9.025 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98861 | 0.78264 | 20.597 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98861 | 0.90258 | 8.603 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9859 | 0.77249 | 21.341 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9859 | 0.78662 | 19.928 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.75383 | 24.107 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97285 | 0.72453 | 24.833 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97285 | 0.75218 | 22.067 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97285 | 0.75885 | 21.4 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97285 | 0.78868 | 18.417 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98825 | 0.86557 | 12.268 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98827 | 0.73717 | 25.11 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.90414 | 8.762 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99472 | 0.77819 | 21.653 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.90826 | 8.451 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98894 | 0.78622 | 20.273 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98879 | 0.75297 | 23.582 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98879 | 0.75348 | 23.53 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99898 | 0.78339 | 21.56 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99898 | 0.90184 | 9.714 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98315 | 0.77005 | 21.309 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98315 | 0.78315 | 19.999 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99465 | 0.91195 | 8.27 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.87891 | 11.47 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99297 | 0.90753 | 8.544 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.89696 | 8.849 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.89696 | 8.849 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9933 | 0.90216 | 9.114 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.90686 | 8.572 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98791 | 0.90451 | 8.34 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98791 | 0.90451 | 8.34 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.88257 | 10.716 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99259 | 0.89415 | 9.844 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.89473 | 9.783 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99351 | 0.90989 | 8.362 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.77859 | 21.1 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98959 | 0.89222 | 9.737 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.78375 | 20.707 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99287 | 0.90689 | 8.598 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.78863 | 20.205 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.88747 | 10.522 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.89597 | 9.595 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99322 | 0.90945 | 8.377 | Yes
Active | 2025W1-N11-WVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99049 | 0.78755 | 20.294 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.91227 | 8.252 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.91227 | 8.252 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.90289 | 9.148 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.89139 | 10.06 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.79013 | 20.042 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99374 | 0.91229 | 8.145 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99177 | 0.9036 | 8.817 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99121 | 0.78941 | 20.18 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.79078 | 19.926 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.78043 | 21.183 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.88281 | 10.713 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.91074 | 8.101 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96607 | 0.72514 | 24.093 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96607 | 0.74031 | 22.576 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96607 | 0.75278 | 21.329 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96607 | 0.75781 | 20.827 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96607 | 0.77431 | 19.176 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96607 | 0.87268 | 9.339 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99538 | 0.75434 | 24.104 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.90464 | 8.987 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98299 | 0.89149 | 9.15 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.91012 | 8.097 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98941 | 0.78203 | 20.738 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98941 | 0.90585 | 8.356 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.78246 | 20.746 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.89959 | 9.347 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99362 | 0.90364 | 8.998 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.90364 | 9.005 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.79176 | 19.885 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99422 | 0.90847 | 8.575 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98706 | 0.78456 | 20.25 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98706 | 0.89142 | 9.564 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.89732 | 9.383 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99411 | 0.90388 | 9.023 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.7829 | 20.592 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98882 | 0.90281 | 8.601 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.77274 | 21.337 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98611 | 0.78688 | 19.923 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.75408 | 24.103 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97306 | 0.72476 | 24.83 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97306 | 0.75243 | 22.064 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97306 | 0.7591 | 21.397 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97306 | 0.78893 | 18.413 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98846 | 0.86581 | 12.265 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.73741 | 25.107 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.90437 | 8.76 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99493 | 0.77844 | 21.649 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.90849 | 8.449 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.78647 | 20.268 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.989 | 0.75321 | 23.578 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.989 | 0.75373 | 23.527 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99919 | 0.78364 | 21.555 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99919 | 0.90207 | 9.712 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98336 | 0.7703 | 21.305 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98336 | 0.78341 | 19.995 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.91218 | 8.268 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.87914 | 11.468 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.90776 | 8.542 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.89719 | 8.847 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.89719 | 8.847 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.90239 | 9.111 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.90709 | 8.57 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98812 | 0.90474 | 8.338 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98812 | 0.90474 | 8.338 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.88281 | 10.713 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.89438 | 9.842 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.89496 | 9.78 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.91011 | 8.36 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9898 | 0.77884 | 21.096 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9898 | 0.89245 | 9.734 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.784 | 20.703 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.90712 | 8.596 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99088 | 0.78888 | 20.2 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.88771 | 10.519 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99214 | 0.8962 | 9.593 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.90967 | 8.375 | Yes
Active | 2025W1-N11-WVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9907 | 0.7878 | 20.289 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.91227 | 8.252 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.91227 | 8.252 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.90289 | 9.148 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99198 | 0.89139 | 10.06 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.79012 | 20.042 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99374 | 0.91229 | 8.145 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99177 | 0.9036 | 8.817 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99121 | 0.78941 | 20.18 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.79078 | 19.926 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.78043 | 21.183 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.88281 | 10.713 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99176 | 0.91074 | 8.101 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96607 | 0.72514 | 24.093 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96607 | 0.74031 | 22.576 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96607 | 0.75278 | 21.329 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96607 | 0.75781 | 20.827 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96607 | 0.77431 | 19.176 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96607 | 0.87268 | 9.339 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99538 | 0.75434 | 24.104 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.90464 | 8.987 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98299 | 0.89149 | 9.15 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.91012 | 8.097 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98941 | 0.78203 | 20.738 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98941 | 0.90585 | 8.356 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98992 | 0.78246 | 20.746 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99306 | 0.89958 | 9.347 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99362 | 0.90364 | 8.998 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99369 | 0.90364 | 9.005 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.79176 | 19.885 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99422 | 0.90847 | 8.575 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98706 | 0.78456 | 20.25 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98706 | 0.89142 | 9.564 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.89731 | 9.383 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.90388 | 9.023 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98882 | 0.78289 | 20.592 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98882 | 0.90281 | 8.601 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.77274 | 21.337 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98611 | 0.78688 | 19.923 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.75408 | 24.103 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97306 | 0.72476 | 24.83 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97306 | 0.75243 | 22.064 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97306 | 0.7591 | 21.397 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97306 | 0.78893 | 18.413 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98846 | 0.8658 | 12.265 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.73741 | 25.107 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99197 | 0.90437 | 8.76 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99493 | 0.77844 | 21.649 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.90849 | 8.449 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.78647 | 20.268 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.989 | 0.75321 | 23.578 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.989 | 0.75373 | 23.527 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99919 | 0.78364 | 21.555 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99919 | 0.90207 | 9.712 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98336 | 0.7703 | 21.305 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98336 | 0.78341 | 19.995 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.91218 | 8.268 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.87914 | 11.468 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.90776 | 8.542 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.89719 | 8.847 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.89719 | 8.847 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.90239 | 9.111 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99279 | 0.90709 | 8.57 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98812 | 0.90474 | 8.339 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98812 | 0.90474 | 8.338 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.88281 | 10.713 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.89438 | 9.842 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.89496 | 9.78 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.91011 | 8.36 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9898 | 0.77884 | 21.096 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9898 | 0.89245 | 9.734 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.784 | 20.703 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.90712 | 8.596 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99088 | 0.78888 | 20.2 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.88771 | 10.519 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99214 | 0.8962 | 9.593 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.90967 | 8.375 | Yes
Active | 2025W1-N11-WVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9907 | 0.7878 | 20.289 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98223 | 0.89971 | 8.252 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97744 | 0.88329 | 9.415 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97886 | 0.79604 | 18.283 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97901 | 0.79236 | 18.665 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97786 | 0.79487 | 18.299 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98125 | 0.78259 | 19.865 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97568 | 0.87699 | 9.869 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96058 | 0.7335 | 22.708 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96058 | 0.74889 | 21.169 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96058 | 0.75696 | 20.362 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96058 | 0.76542 | 19.516 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96058 | 0.7771 | 18.348 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98314 | 0.7609 | 22.223 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9824 | 0.90103 | 8.137 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9778 | 0.89683 | 8.097 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97673 | 0.78305 | 19.369 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97738 | 0.78362 | 19.376 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98089 | 0.89635 | 8.454 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98142 | 0.90012 | 8.13 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9815 | 0.90013 | 8.137 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97897 | 0.79692 | 18.205 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97549 | 0.78994 | 18.555 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97549 | 0.88735 | 8.814 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97913 | 0.89419 | 8.493 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98198 | 0.90028 | 8.17 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97665 | 0.78743 | 18.922 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.974 | 0.77643 | 19.757 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.974 | 0.78791 | 18.609 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98293 | 0.76012 | 22.28 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96596 | 0.73314 | 23.282 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96596 | 0.75409 | 21.187 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96596 | 0.76717 | 19.879 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96596 | 0.78897 | 17.699 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97574 | 0.86327 | 11.247 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97457 | 0.74446 | 23.011 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98228 | 0.78804 | 19.423 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97772 | 0.79268 | 18.504 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97565 | 0.75375 | 22.19 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97565 | 0.75584 | 21.981 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98603 | 0.78718 | 19.886 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98603 | 0.8955 | 9.053 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97084 | 0.77145 | 19.939 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97084 | 0.78177 | 18.907 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98164 | 0.87801 | 10.363 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9813 | 0.89893 | 8.237 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97568 | 0.87699 | 9.869 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98027 | 0.89028 | 8.999 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98022 | 0.89083 | 8.938 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97799 | 0.78028 | 19.77 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97799 | 0.88611 | 9.187 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97878 | 0.78548 | 19.331 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97869 | 0.79199 | 18.67 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98063 | 0.88443 | 9.62 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9798 | 0.89272 | 8.707 | Yes
Active | 2025W1-N11-WVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97845 | 0.79068 | 18.776 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.91612 | 8.853 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.90476 | 9.753 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.80788 | 19.308 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.91729 | 8.515 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.80707 | 19.452 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.80844 | 19.2 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.79803 | 20.451 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.89686 | 10.358 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97707 | 0.74243 | 23.464 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97707 | 0.75848 | 21.859 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97707 | 0.77108 | 20.599 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97707 | 0.77528 | 20.179 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97707 | 0.79192 | 18.515 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97707 | 0.80098 | 17.608 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97707 | 0.88044 | 9.663 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97707 | 0.88715 | 8.992 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.77038 | 23.536 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.91774 | 8.707 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.9018 | 8.902 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99987 | 0.7997 | 20.016 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99987 | 0.91904 | 8.082 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.80014 | 20.022 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.91287 | 9.049 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.91678 | 8.713 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.91678 | 8.72 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.80951 | 19.159 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.92138 | 8.307 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99757 | 0.80217 | 19.54 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99757 | 0.90519 | 9.238 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.91065 | 9.084 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.91699 | 8.743 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99922 | 0.80052 | 19.87 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99922 | 0.91602 | 8.32 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.79031 | 20.618 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99649 | 0.80464 | 19.185 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.77151 | 23.41 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98383 | 0.74207 | 24.176 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98383 | 0.77083 | 21.3 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98383 | 0.77526 | 20.857 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98383 | 0.80684 | 17.699 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99876 | 0.88008 | 11.868 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99943 | 0.75554 | 24.389 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.91736 | 8.495 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.79596 | 20.933 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.92147 | 8.184 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99964 | 0.80423 | 19.541 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99998 | 0.77152 | 22.847 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99998 | 0.77211 | 22.787 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0098 | 0.80186 | 20.79 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0098 | 0.91599 | 9.377 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.7879 | 20.607 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99397 | 0.8012 | 19.277 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.92503 | 8.012 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.89329 | 11.095 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.92083 | 8.264 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99224 | 0.90624 | 8.6 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99224 | 0.90624 | 8.6 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.91556 | 8.823 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.91995 | 8.31 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99847 | 0.91771 | 8.076 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99847 | 0.91771 | 8.076 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.89686 | 10.358 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.90785 | 9.529 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.90841 | 9.47 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.004 | 0.92302 | 8.101 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.79646 | 20.371 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.90612 | 9.405 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.80168 | 19.974 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.92015 | 8.327 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.80653 | 19.474 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.90148 | 10.175 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.90964 | 9.286 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.92261 | 8.114 | Yes
Active | 2025W1-N11-WVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.80544 | 19.565 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0034 | 0.90512 | 9.826 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0034 | 0.9104 | 9.298 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0034 | 0.92224 | 8.114 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0086 | 0.92447 | 8.414 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0083 | 0.92059 | 8.768 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0036 | 0.89675 | 10.685 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.90945 | 9.415 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99587 | 0.90198 | 9.388 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.90902 | 8.685 | Yes
Active | 2025W1-N11-WVD288663 | 288663 | 05FIN DATAZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.9235 | 8.196 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0037 | 0.9049 | 9.883 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0037 | 0.91021 | 9.352 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0037 | 0.92212 | 8.161 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92435 | 8.467 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.92047 | 8.821 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0039 | 0.89647 | 10.747 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90926 | 9.468 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99613 | 0.90172 | 9.441 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.90881 | 8.732 | Yes
Active | 2025W1-N11-WVD288672 | 288672 | 05N.FINDLAY2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0058 | 0.92339 | 8.244 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.002 | 0.89988 | 10.214 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.90532 | 9.669 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.002 | 0.91766 | 8.436 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0078 | 0.91992 | 8.784 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.91607 | 9.132 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0022 | 0.8911 | 11.108 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.90439 | 9.779 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.92389 | 8.063 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99382 | 0.89634 | 9.748 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.9038 | 9.002 | Yes
Active | 2025W1-N11-WVD288681 | 288681 | 05NEWLIBR_BP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.91904 | 8.529 | Yes
Active | 2025W1-N11-WVD288691 | 288691 | 05WHIPPLEDTC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0004 | 0.91642 | 8.393 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98684 | 0.89773 | 8.91 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98735 | 0.80869 | 17.866 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98746 | 0.80382 | 18.364 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.80712 | 17.923 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.79323 | 19.734 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98313 | 0.88691 | 9.622 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9718 | 0.74811 | 22.369 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9718 | 0.76154 | 21.026 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9718 | 0.76747 | 20.433 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9718 | 0.77896 | 19.284 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9718 | 0.78771 | 18.409 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9718 | 0.79904 | 17.276 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9718 | 0.88203 | 8.977 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9718 | 0.88636 | 8.544 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9914 | 0.77643 | 21.497 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98485 | 0.79275 | 19.209 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98559 | 0.79344 | 19.215 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98942 | 0.90784 | 8.158 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98746 | 0.80958 | 17.788 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9841 | 0.80244 | 18.166 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9841 | 0.89846 | 8.564 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98763 | 0.90558 | 8.205 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98503 | 0.79933 | 18.57 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98286 | 0.78765 | 19.521 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98286 | 0.79895 | 18.391 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.77313 | 21.755 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97679 | 0.74774 | 22.905 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97679 | 0.764 | 21.279 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97679 | 0.78309 | 19.369 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97679 | 0.79926 | 17.753 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98453 | 0.87534 | 10.919 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98243 | 0.75658 | 22.586 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.80038 | 19.048 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98621 | 0.80526 | 18.095 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98257 | 0.76302 | 21.955 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98257 | 0.76571 | 21.686 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99298 | 0.7976 | 19.539 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99298 | 0.90433 | 8.865 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97905 | 0.78135 | 19.771 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97905 | 0.79131 | 18.775 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98994 | 0.88992 | 10.002 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98313 | 0.88691 | 9.622 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98859 | 0.90121 | 8.739 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.90176 | 8.678 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98678 | 0.79037 | 19.641 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98678 | 0.89637 | 9.041 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98719 | 0.79557 | 19.162 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98714 | 0.80353 | 18.361 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98905 | 0.89553 | 9.353 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98816 | 0.90396 | 8.419 | Yes
Active | 2025W1-N11-WVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.80203 | 18.483 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98751 | 0.90342 | 8.409 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98517 | 0.89224 | 9.294 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98415 | 0.80401 | 18.015 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98593 | 0.9052 | 8.073 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98466 | 0.80307 | 18.16 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98355 | 0.80429 | 17.926 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98536 | 0.79424 | 19.112 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98405 | 0.88608 | 9.797 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96026 | 0.73501 | 22.526 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96026 | 0.7534 | 20.686 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96026 | 0.76742 | 19.284 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96026 | 0.76993 | 19.033 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96026 | 0.78806 | 17.22 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98874 | 0.76217 | 22.657 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9877 | 0.9047 | 8.3 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98375 | 0.90125 | 8.251 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98311 | 0.79613 | 18.698 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98355 | 0.79655 | 18.7 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9863 | 0.90027 | 8.603 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98679 | 0.90387 | 8.292 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.90387 | 8.298 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98426 | 0.80537 | 17.89 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98098 | 0.79832 | 18.266 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98098 | 0.89399 | 8.699 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98441 | 0.898 | 8.642 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.90396 | 8.335 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98241 | 0.79679 | 18.562 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97969 | 0.78653 | 19.315 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97969 | 0.80187 | 17.781 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98881 | 0.76605 | 22.276 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96686 | 0.73467 | 23.219 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96686 | 0.76743 | 19.943 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96686 | 0.76778 | 19.907 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96686 | 0.80409 | 16.277 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.86917 | 11.251 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9835 | 0.75035 | 23.315 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98556 | 0.90473 | 8.083 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.7903 | 19.804 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98298 | 0.80055 | 18.244 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98398 | 0.76794 | 21.605 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98398 | 0.76917 | 21.481 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.79896 | 19.422 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99318 | 0.90486 | 8.832 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97745 | 0.78406 | 19.34 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97745 | 0.79855 | 17.89 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98711 | 0.8821 | 10.501 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9823 | 0.90096 | 8.134 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9823 | 0.90096 | 8.134 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98667 | 0.90273 | 8.395 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98405 | 0.88608 | 9.797 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98613 | 0.89555 | 9.058 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9861 | 0.89608 | 9.002 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98325 | 0.79275 | 19.049 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98325 | 0.8947 | 8.855 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98451 | 0.79803 | 18.648 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98436 | 0.80253 | 18.184 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9862 | 0.88973 | 9.648 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98551 | 0.89724 | 8.827 | Yes
Active | 2025W1-N11-WVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9842 | 0.80149 | 18.271 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99474 | 0.91272 | 8.202 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99125 | 0.89934 | 9.192 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.80703 | 18.418 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9916 | 0.80383 | 18.778 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.80634 | 18.414 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99384 | 0.79375 | 20.009 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9856 | 0.88597 | 9.963 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97439 | 0.74368 | 23.071 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97439 | 0.75823 | 21.616 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97439 | 0.76706 | 20.732 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97439 | 0.77585 | 19.854 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97439 | 0.78813 | 18.626 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97439 | 0.79846 | 17.593 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97439 | 0.88128 | 9.311 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97439 | 0.88636 | 8.802 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9956 | 0.77232 | 22.328 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.91426 | 8.065 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.90895 | 8.057 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98935 | 0.79423 | 19.512 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98999 | 0.79482 | 19.517 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99344 | 0.90944 | 8.4 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99397 | 0.91327 | 8.07 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99404 | 0.91327 | 8.077 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.80825 | 18.314 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98788 | 0.80087 | 18.701 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98788 | 0.9004 | 8.748 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99163 | 0.90722 | 8.441 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.91352 | 8.099 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98916 | 0.79825 | 19.091 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98664 | 0.78679 | 19.986 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98664 | 0.79907 | 18.758 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.77062 | 22.457 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.74331 | 23.673 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98004 | 0.76454 | 21.549 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98004 | 0.7785 | 20.154 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98004 | 0.80073 | 17.93 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98853 | 0.87652 | 11.2 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98726 | 0.75386 | 23.34 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.79796 | 19.684 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.80346 | 18.655 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98875 | 0.7643 | 22.445 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98875 | 0.76602 | 22.274 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.79776 | 20.047 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99823 | 0.90832 | 8.991 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98442 | 0.78248 | 20.193 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98442 | 0.79343 | 19.098 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99402 | 0.89083 | 10.32 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99386 | 0.91207 | 8.179 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9856 | 0.88597 | 9.963 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99287 | 0.90348 | 8.939 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99282 | 0.90404 | 8.878 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99061 | 0.79142 | 19.919 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99061 | 0.89959 | 9.102 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99138 | 0.79671 | 19.466 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.80341 | 18.786 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99319 | 0.89742 | 9.577 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.90581 | 8.654 | Yes
Active | 2025W1-N11-WVD288718 | 288718 | 05GILES | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.80208 | 18.896 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99623 | 0.9139 | 8.233 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99623 | 0.9139 | 8.233 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9958 | 0.90454 | 9.126 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.89304 | 10.038 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.79204 | 19.995 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99517 | 0.91389 | 8.128 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99326 | 0.90534 | 8.792 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99265 | 0.79132 | 20.133 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99148 | 0.79268 | 19.879 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99368 | 0.78233 | 21.135 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.88456 | 10.685 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99324 | 0.91241 | 8.082 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96755 | 0.72692 | 24.063 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96755 | 0.74227 | 22.528 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96755 | 0.75477 | 21.278 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96755 | 0.75966 | 20.789 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96755 | 0.7762 | 19.135 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96755 | 0.87442 | 9.313 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99683 | 0.75594 | 24.089 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.90628 | 8.966 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98431 | 0.893 | 9.131 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.91178 | 8.079 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.78394 | 20.692 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99086 | 0.90752 | 8.334 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99137 | 0.78438 | 20.699 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.90124 | 9.325 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99505 | 0.90528 | 8.977 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99513 | 0.90529 | 8.984 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99209 | 0.79369 | 19.839 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.91009 | 8.555 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9885 | 0.78645 | 20.205 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9885 | 0.89312 | 9.538 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99259 | 0.89898 | 9.361 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99554 | 0.90552 | 9.002 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99025 | 0.78479 | 20.546 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99025 | 0.90446 | 8.579 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98753 | 0.77461 | 21.292 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98753 | 0.78879 | 19.874 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99659 | 0.75592 | 24.067 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97452 | 0.72654 | 24.798 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97452 | 0.75444 | 22.008 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97452 | 0.76072 | 21.38 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97452 | 0.79089 | 18.364 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98988 | 0.8675 | 12.237 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.73936 | 25.067 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99337 | 0.90593 | 8.744 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99638 | 0.78034 | 21.605 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99442 | 0.91013 | 8.429 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9906 | 0.78839 | 20.222 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.75521 | 23.534 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99055 | 0.75574 | 23.48 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.78565 | 21.504 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.90386 | 9.684 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98482 | 0.77219 | 21.262 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98482 | 0.78534 | 19.948 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99629 | 0.91381 | 8.249 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.88088 | 11.443 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9946 | 0.90939 | 8.52 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98694 | 0.89865 | 8.828 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98694 | 0.89865 | 8.828 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.90404 | 9.09 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99422 | 0.9087 | 8.552 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.90631 | 8.319 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9895 | 0.90632 | 8.318 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.88456 | 10.685 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99424 | 0.89605 | 9.819 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.89664 | 9.757 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99516 | 0.91175 | 8.341 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.78074 | 21.049 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99123 | 0.89415 | 9.708 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99247 | 0.78592 | 20.656 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.90876 | 8.576 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99233 | 0.79079 | 20.154 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99434 | 0.88941 | 10.493 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.89788 | 9.57 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.91131 | 8.355 | Yes
Active | 2025W1-N11-WVD288721 | 288721 | 05MACY | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99214 | 0.78971 | 20.243 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.85634 | 13.461 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98977 | 0.84841 | 14.136 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9894 | 0.85214 | 13.726 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97667 | 0.80727 | 16.94 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97667 | 0.81045 | 16.622 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97667 | 0.81562 | 16.105 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97667 | 0.82735 | 14.932 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97667 | 0.83112 | 14.555 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97667 | 0.83999 | 13.668 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97667 | 0.84067 | 13.6 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99376 | 0.83468 | 15.907 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99094 | 0.85659 | 13.435 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9884 | 0.85101 | 13.739 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98825 | 0.84679 | 14.145 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98569 | 0.83611 | 14.958 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98569 | 0.84373 | 14.196 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.82799 | 16.433 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97973 | 0.80544 | 17.429 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97973 | 0.80697 | 17.276 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97973 | 0.83534 | 14.439 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97973 | 0.83833 | 14.14 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.9028 | 8.354 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98477 | 0.81328 | 17.149 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.85001 | 14.37 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99013 | 0.85371 | 13.642 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97903 | 0.80648 | 17.254 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97903 | 0.8109 | 16.813 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99149 | 0.84112 | 15.037 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97864 | 0.82359 | 15.505 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97864 | 0.83042 | 14.823 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98926 | 0.84786 | 14.14 | Yes
Active | 2025W1-N11-WVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.84645 | 14.247 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98358 | 0.89876 | 8.482 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98127 | 0.88761 | 9.367 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98012 | 0.79715 | 18.297 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9818 | 0.90031 | 8.149 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98068 | 0.79628 | 18.44 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97955 | 0.79753 | 18.202 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98142 | 0.78742 | 19.4 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97994 | 0.88097 | 9.897 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95654 | 0.72989 | 22.665 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95654 | 0.74766 | 20.888 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95654 | 0.76101 | 19.553 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95654 | 0.7639 | 19.264 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95654 | 0.78129 | 17.525 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9848 | 0.75678 | 22.802 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98378 | 0.90015 | 8.363 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96355 | 0.87643 | 8.713 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97908 | 0.78925 | 18.983 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97953 | 0.78967 | 18.986 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98234 | 0.89559 | 8.676 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98285 | 0.89926 | 8.359 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98292 | 0.89926 | 8.366 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98026 | 0.7986 | 18.165 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9769 | 0.79149 | 18.541 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9769 | 0.88881 | 8.809 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98048 | 0.89336 | 8.713 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98339 | 0.89942 | 8.397 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97837 | 0.78992 | 18.845 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97563 | 0.77971 | 19.592 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97563 | 0.79453 | 18.111 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98484 | 0.76008 | 22.476 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96306 | 0.72954 | 23.352 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96306 | 0.76109 | 20.198 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96306 | 0.7619 | 20.116 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96306 | 0.79677 | 16.629 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97775 | 0.86411 | 11.364 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97939 | 0.74466 | 23.473 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98151 | 0.90001 | 8.15 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98442 | 0.7845 | 19.992 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97891 | 0.79365 | 18.526 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97989 | 0.7615 | 21.839 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97989 | 0.76244 | 21.745 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98915 | 0.79201 | 19.714 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98915 | 0.89976 | 8.938 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97336 | 0.77731 | 19.605 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97336 | 0.79123 | 18.212 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98318 | 0.87709 | 10.609 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97694 | 0.89485 | 8.209 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97694 | 0.89485 | 8.209 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98273 | 0.8981 | 8.464 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97994 | 0.88097 | 9.897 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.89081 | 9.136 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98214 | 0.89135 | 9.079 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97925 | 0.78592 | 19.333 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97925 | 0.88958 | 8.967 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98052 | 0.79116 | 18.936 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98037 | 0.79574 | 18.464 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98225 | 0.88485 | 9.739 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98155 | 0.89253 | 8.902 | Yes
Active | 2025W1-N11-WVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98021 | 0.7947 | 18.551 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99041 | 0.90573 | 8.468 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98809 | 0.89474 | 9.335 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98693 | 0.80431 | 18.262 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98864 | 0.90747 | 8.117 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98751 | 0.80347 | 18.404 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9864 | 0.80473 | 18.167 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.7945 | 19.38 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.88801 | 9.871 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96359 | 0.73638 | 22.721 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96359 | 0.75342 | 21.017 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96359 | 0.7669 | 19.669 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96359 | 0.77065 | 19.294 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96359 | 0.78828 | 17.531 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96359 | 0.87835 | 8.524 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99152 | 0.76484 | 22.668 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99058 | 0.90724 | 8.335 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98428 | 0.90094 | 8.334 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98591 | 0.79632 | 18.959 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98636 | 0.79675 | 18.961 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98918 | 0.90262 | 8.656 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.90633 | 8.337 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98977 | 0.90633 | 8.345 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98711 | 0.8057 | 18.141 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98362 | 0.79845 | 18.517 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98362 | 0.89558 | 8.804 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98738 | 0.90053 | 8.685 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.9065 | 8.369 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98524 | 0.79703 | 18.821 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98256 | 0.78665 | 19.591 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98256 | 0.80148 | 18.108 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99151 | 0.76679 | 22.471 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97012 | 0.73601 | 23.411 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97012 | 0.76687 | 20.325 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97012 | 0.76993 | 20.02 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97012 | 0.8037 | 16.642 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98467 | 0.87151 | 11.316 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.7504 | 23.526 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98788 | 0.90621 | 8.167 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.79171 | 19.935 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98571 | 0.80076 | 18.495 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98627 | 0.76739 | 21.889 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98627 | 0.76824 | 21.803 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99564 | 0.79857 | 19.707 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99564 | 0.90626 | 8.938 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98024 | 0.78421 | 19.603 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98024 | 0.79811 | 18.213 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99021 | 0.88403 | 10.618 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98475 | 0.90302 | 8.173 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98475 | 0.90302 | 8.173 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.90517 | 8.443 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.88801 | 9.871 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98899 | 0.8979 | 9.109 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98896 | 0.89844 | 9.052 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98612 | 0.79296 | 19.316 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98612 | 0.89658 | 8.954 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98735 | 0.79826 | 18.909 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98721 | 0.80293 | 18.428 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98907 | 0.89194 | 9.713 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98838 | 0.89962 | 8.876 | Yes
Active | 2025W1-N11-WVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98704 | 0.80187 | 18.517 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99366 | 0.90718 | 8.648 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.89576 | 9.543 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99002 | 0.80067 | 18.935 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.90918 | 8.269 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.79956 | 19.107 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98949 | 0.8011 | 18.839 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99177 | 0.79029 | 20.148 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.8867 | 10.184 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96752 | 0.73479 | 23.273 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96752 | 0.75063 | 21.689 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96752 | 0.76291 | 20.46 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96752 | 0.76796 | 19.956 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96752 | 0.78414 | 18.338 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96752 | 0.87223 | 9.529 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96752 | 0.87895 | 8.857 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99468 | 0.76354 | 23.114 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99382 | 0.90876 | 8.506 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98415 | 0.89815 | 8.6 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98883 | 0.7918 | 19.704 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98934 | 0.79227 | 19.708 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99238 | 0.90396 | 8.842 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99292 | 0.9078 | 8.511 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99299 | 0.9078 | 8.518 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99014 | 0.80229 | 18.784 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.91245 | 8.11 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98671 | 0.79497 | 19.174 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98671 | 0.89614 | 9.057 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99053 | 0.90176 | 8.878 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.90802 | 8.541 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98826 | 0.79312 | 19.515 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98826 | 0.90671 | 8.156 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.78257 | 20.304 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98562 | 0.79662 | 18.9 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.76396 | 23.056 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97404 | 0.73442 | 23.963 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97404 | 0.76224 | 21.18 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97404 | 0.76863 | 20.542 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97404 | 0.79869 | 17.535 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98777 | 0.87159 | 11.617 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98807 | 0.74748 | 24.059 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.909 | 8.262 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.78916 | 20.485 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98872 | 0.79701 | 19.171 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98883 | 0.76316 | 22.567 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98883 | 0.76334 | 22.549 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99845 | 0.79411 | 20.434 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99845 | 0.90628 | 9.217 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98321 | 0.77987 | 20.334 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98321 | 0.79282 | 19.039 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.88476 | 10.833 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.91188 | 8.063 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98624 | 0.9027 | 8.354 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98624 | 0.9027 | 8.354 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9928 | 0.90661 | 8.62 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99213 | 0.91105 | 8.108 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98854 | 0.8867 | 10.184 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.89886 | 9.326 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99208 | 0.89941 | 9.266 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9893 | 0.78859 | 20.071 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9893 | 0.89676 | 9.254 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99045 | 0.79387 | 19.658 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99242 | 0.91109 | 8.133 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99031 | 0.79903 | 19.128 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99224 | 0.8926 | 9.964 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99149 | 0.9007 | 9.079 | Yes
Active | 2025W1-N11-WVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99012 | 0.79791 | 19.221 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98986 | 0.82267 | 16.719 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.81682 | 17.321 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98902 | 0.82066 | 16.836 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99381 | 0.80528 | 18.853 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98688 | 0.89798 | 8.889 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97358 | 0.76325 | 21.033 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97358 | 0.77409 | 19.949 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97358 | 0.77796 | 19.562 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97358 | 0.79227 | 18.132 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97358 | 0.79716 | 17.642 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97358 | 0.80509 | 16.849 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97358 | 0.80935 | 16.423 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97358 | 0.88981 | 8.378 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99358 | 0.79479 | 19.879 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98721 | 0.80403 | 18.318 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.988 | 0.80483 | 18.317 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.82344 | 16.66 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9868 | 0.81635 | 17.044 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9868 | 0.90675 | 8.005 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.81094 | 17.679 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9864 | 0.79937 | 18.703 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9864 | 0.81075 | 17.565 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.78846 | 20.384 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97803 | 0.76288 | 21.515 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97803 | 0.77415 | 20.387 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97803 | 0.79927 | 17.876 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97803 | 0.80837 | 16.966 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98786 | 0.88681 | 10.105 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98464 | 0.77108 | 21.356 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.81431 | 17.908 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98877 | 0.81925 | 16.952 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98314 | 0.77503 | 20.811 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98314 | 0.77807 | 20.507 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.80978 | 18.38 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99359 | 0.9102 | 8.338 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98113 | 0.79268 | 18.844 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98113 | 0.80227 | 17.885 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9921 | 0.90022 | 9.188 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98688 | 0.89798 | 8.889 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.91047 | 8.081 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.91098 | 8.025 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.80191 | 18.783 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98974 | 0.90405 | 8.568 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98971 | 0.80724 | 18.247 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98972 | 0.81659 | 17.313 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99154 | 0.90425 | 8.729 | Yes
Active | 2025W1-N11-WVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98942 | 0.81495 | 17.447 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98841 | 0.82625 | 16.215 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98864 | 0.82039 | 16.825 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98766 | 0.82425 | 16.342 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99255 | 0.80901 | 18.354 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.90032 | 8.607 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97186 | 0.76754 | 20.432 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97186 | 0.77808 | 19.379 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97186 | 0.78167 | 19.02 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97186 | 0.79639 | 17.548 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97186 | 0.80073 | 17.114 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97186 | 0.80875 | 16.311 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97186 | 0.81288 | 15.898 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97186 | 0.89085 | 8.101 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99199 | 0.7995 | 19.249 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98584 | 0.8076 | 17.823 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98663 | 0.8084 | 17.822 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98862 | 0.82697 | 16.165 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98541 | 0.82009 | 16.532 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98663 | 0.81422 | 17.241 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98531 | 0.80329 | 18.202 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98531 | 0.81446 | 17.085 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99066 | 0.79277 | 19.788 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97619 | 0.76718 | 20.901 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97619 | 0.77783 | 19.836 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97619 | 0.80378 | 17.241 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97619 | 0.81173 | 16.446 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98652 | 0.88832 | 9.82 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98317 | 0.77525 | 20.793 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99187 | 0.81815 | 17.372 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98734 | 0.82293 | 16.441 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98121 | 0.77887 | 20.233 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98121 | 0.78195 | 19.926 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99177 | 0.81349 | 17.828 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99177 | 0.91043 | 8.134 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97962 | 0.79643 | 18.319 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97962 | 0.80596 | 17.366 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99049 | 0.90126 | 8.923 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.90032 | 8.607 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98848 | 0.80562 | 18.286 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98848 | 0.90472 | 8.376 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98832 | 0.8108 | 17.752 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.82019 | 16.815 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.90501 | 8.506 | Yes
Active | 2025W1-N11-WVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98804 | 0.81856 | 16.948 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0078 | 0.91512 | 9.272 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.9151 | 9.285 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.9114 | 9.542 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.90645 | 10.064 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99791 | 0.87752 | 12.039 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99791 | 0.8801 | 11.781 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99791 | 0.88459 | 11.332 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99791 | 0.88653 | 11.138 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99791 | 0.89712 | 10.079 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99791 | 0.8972 | 10.071 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99791 | 0.90233 | 9.558 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0096 | 0.90341 | 10.618 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.90885 | 9.775 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.90907 | 9.778 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.91491 | 9.265 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.90885 | 9.706 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99669 | 0.88344 | 11.326 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99669 | 0.88789 | 10.881 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.89511 | 11.223 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99838 | 0.87386 | 12.452 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99838 | 0.87962 | 11.875 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99838 | 0.90563 | 9.275 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99838 | 0.90675 | 9.162 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.88352 | 11.925 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0098 | 0.90974 | 10.007 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.91344 | 9.389 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9988 | 0.8774 | 12.14 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9988 | 0.88038 | 11.842 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.89939 | 10.661 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.90007 | 10.156 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0016 | 0.90402 | 9.76 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.9056 | 10.04 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0073 | 0.90994 | 9.737 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.91283 | 9.418 | Yes
Active | 2025W1-N11-WVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.91289 | 9.406 | Yes
Active | 2025W1-N11-WVD288875 | 288875 | 05LAMMER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99326 | 0.91231 | 8.095 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97963 | 0.89758 | 8.205 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97477 | 0.88075 | 9.402 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97637 | 0.7971 | 17.927 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97648 | 0.79374 | 18.274 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97534 | 0.79597 | 17.937 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97837 | 0.78426 | 19.41 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9745 | 0.87735 | 9.715 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9562 | 0.73303 | 22.317 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9562 | 0.7491 | 20.71 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9562 | 0.75782 | 19.838 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9562 | 0.7655 | 19.07 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9562 | 0.77818 | 17.802 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98058 | 0.76082 | 21.976 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97983 | 0.89876 | 8.107 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97549 | 0.89501 | 8.047 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97435 | 0.78504 | 18.931 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97496 | 0.78557 | 18.939 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97828 | 0.89422 | 8.407 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97882 | 0.89791 | 8.091 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97889 | 0.89792 | 8.097 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97648 | 0.79789 | 17.858 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97302 | 0.79108 | 18.193 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97302 | 0.88559 | 8.742 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97665 | 0.89227 | 8.439 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9794 | 0.898 | 8.14 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97419 | 0.78882 | 18.537 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97143 | 0.77811 | 19.332 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97143 | 0.7895 | 18.193 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9806 | 0.7609 | 21.969 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96153 | 0.73265 | 22.888 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96153 | 0.75501 | 20.653 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96153 | 0.76642 | 19.512 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96153 | 0.79001 | 17.153 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97307 | 0.86174 | 11.133 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97163 | 0.74541 | 22.622 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97972 | 0.78944 | 19.028 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97525 | 0.79385 | 18.14 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97326 | 0.75547 | 21.78 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97326 | 0.75748 | 21.578 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98388 | 0.78894 | 19.495 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98388 | 0.89428 | 8.96 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96824 | 0.77333 | 19.491 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96824 | 0.78367 | 18.457 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97918 | 0.87628 | 10.29 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9787 | 0.89674 | 8.196 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9745 | 0.87735 | 9.715 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97776 | 0.88846 | 8.93 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97771 | 0.889 | 8.871 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97534 | 0.78213 | 19.321 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97534 | 0.88456 | 9.078 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97627 | 0.78734 | 18.893 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97616 | 0.79335 | 18.281 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97808 | 0.88276 | 9.532 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97729 | 0.89079 | 8.649 | Yes
Active | 2025W1-N11-WVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97594 | 0.79211 | 18.383 | Yes
Active | 2025W1-N11-WVD288963 | 288963 | 05MARKLE SW | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9902 | 0.88464 | 10.556 | Yes
Active | 2025W1-N11-WVD288970 | 288970 | 05MCNUTT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98962 | 0.90086 | 8.876 | Yes
Active | 2025W1-N11-WVD288975 | 288975 | 05GANGWER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99144 | 0.87967 | 11.178 | Yes
Active | 2025W1-N11-WVD288975 | 288975 | 05GANGWER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98985 | 0.9073 | 8.255 | Yes
Active | 2025W1-N11-WVD288990 | 288990 | 05HATHAWAYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99463 | 0.88249 | 11.214 | Yes
Active | 2025W1-N11-WVD288990 | 288990 | 05HATHAWAYSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9929 | 0.91249 | 8.041 | Yes
Active | 2025W1-N11-WVD288999 | 288999 | 05HATCH SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99662 | 0.88495 | 11.167 | Yes
Active | 2025W1-N11-WVD288999 | 288999 | 05HATCH SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99492 | 0.91398 | 8.094 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0058 | 0.90709 | 9.868 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0058 | 0.90748 | 9.829 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0058 | 0.91805 | 8.772 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0058 | 0.92332 | 8.245 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0103 | 0.92386 | 8.639 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0082 | 0.92699 | 8.12 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.01 | 0.91727 | 9.274 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0066 | 0.90166 | 10.492 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.90523 | 10.134 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.91326 | 9.424 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0044 | 0.90593 | 9.846 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.90934 | 9.506 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0088 | 0.92473 | 8.406 | Yes
Active | 2025W1-N11-WVD289097 | 289097 | 05REDRUN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.92706 | 8.084 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98926 | 0.84234 | 14.692 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98868 | 0.83388 | 15.48 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98799 | 0.83856 | 14.943 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9741 | 0.78874 | 18.536 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9741 | 0.79618 | 17.792 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9741 | 0.798 | 17.61 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9741 | 0.81259 | 16.151 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9741 | 0.81492 | 15.918 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.9741 | 0.82578 | 14.832 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.9741 | 0.82708 | 14.702 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99236 | 0.818 | 17.437 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98931 | 0.84277 | 14.655 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98656 | 0.83667 | 14.989 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98673 | 0.83212 | 15.461 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98436 | 0.8208 | 16.356 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98436 | 0.82971 | 15.464 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.81151 | 17.952 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97764 | 0.78843 | 18.921 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97764 | 0.79146 | 18.618 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97764 | 0.82192 | 15.571 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97764 | 0.82202 | 15.562 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.89518 | 9.027 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98329 | 0.79536 | 18.792 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99225 | 0.83531 | 15.694 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98837 | 0.83944 | 14.893 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97902 | 0.79237 | 18.666 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97902 | 0.79645 | 18.258 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99096 | 0.82791 | 16.305 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97806 | 0.80846 | 16.96 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97806 | 0.81648 | 16.158 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99131 | 0.91013 | 8.117 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98831 | 0.83368 | 15.463 | Yes
Active | 2025W1-N11-WVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98796 | 0.83198 | 15.597 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98308 | 0.90159 | 8.149 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98015 | 0.88935 | 9.08 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97991 | 0.80595 | 17.396 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98019 | 0.80436 | 17.583 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97911 | 0.80567 | 17.343 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98096 | 0.79563 | 18.533 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97958 | 0.88463 | 9.496 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95692 | 0.73663 | 22.028 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95692 | 0.75466 | 20.225 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95692 | 0.76806 | 18.886 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95692 | 0.77173 | 18.519 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95692 | 0.78951 | 16.741 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98413 | 0.76463 | 21.95 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98325 | 0.90255 | 8.07 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97861 | 0.79746 | 18.115 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97906 | 0.79788 | 18.118 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98179 | 0.89837 | 8.342 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98229 | 0.90187 | 8.042 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98236 | 0.90188 | 8.049 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98001 | 0.80698 | 17.304 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97673 | 0.80016 | 17.657 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97673 | 0.8911 | 8.563 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98008 | 0.89638 | 8.37 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98282 | 0.90179 | 8.103 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97802 | 0.79858 | 17.945 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97529 | 0.78839 | 18.69 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97529 | 0.80111 | 17.418 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.76765 | 21.689 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9626 | 0.73627 | 22.634 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9626 | 0.76632 | 19.629 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9626 | 0.76994 | 19.266 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9626 | 0.80279 | 15.982 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97675 | 0.86768 | 10.907 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97703 | 0.75149 | 22.554 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98313 | 0.79903 | 18.409 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97882 | 0.80266 | 17.616 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97888 | 0.76756 | 21.132 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97888 | 0.76846 | 21.043 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98871 | 0.80015 | 18.855 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98871 | 0.90158 | 8.712 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97285 | 0.78537 | 18.748 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97285 | 0.79716 | 17.569 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98271 | 0.88101 | 10.169 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98217 | 0.90075 | 8.143 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97958 | 0.88463 | 9.496 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98157 | 0.89353 | 8.803 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98153 | 0.89405 | 8.748 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97876 | 0.79408 | 18.468 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97876 | 0.89127 | 8.749 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.79936 | 18.068 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97988 | 0.80384 | 17.605 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98171 | 0.88808 | 9.363 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.981 | 0.89539 | 8.561 | Yes
Active | 2025W1-N11-WVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97972 | 0.8028 | 17.691 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98767 | 0.90287 | 8.481 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98724 | 0.90195 | 8.529 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98656 | 0.90064 | 8.593 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98775 | 0.90322 | 8.452 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98201 | 0.85801 | 12.4 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98201 | 0.86684 | 11.517 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98201 | 0.87417 | 10.783 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98201 | 0.8873 | 9.47 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98201 | 0.90128 | 8.073 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98882 | 0.88202 | 10.68 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98857 | 0.90621 | 8.235 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98866 | 0.90615 | 8.251 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.90139 | 8.591 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9853 | 0.89745 | 8.785 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98635 | 0.89897 | 8.738 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98471 | 0.8926 | 9.211 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98471 | 0.89395 | 9.076 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98794 | 0.87836 | 10.958 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98184 | 0.84652 | 13.532 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98184 | 0.86662 | 11.522 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98184 | 0.89128 | 9.056 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98184 | 0.90008 | 8.176 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98356 | 0.89453 | 8.902 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98909 | 0.90378 | 8.531 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98731 | 0.90149 | 8.582 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96455 | 0.85151 | 11.305 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96455 | 0.86251 | 10.205 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98371 | 0.87899 | 10.472 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98352 | 0.89122 | 9.23 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98352 | 0.893 | 9.052 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98715 | 0.90299 | 8.416 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98871 | 0.90632 | 8.239 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98695 | 0.9012 | 8.575 | Yes
Active | 2025W1-N11-WVD290024 | 290024 | 05GOMER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98687 | 0.9009 | 8.597 | Yes
Active | 2025W1-N11-WVD290048 | 290048 | 05DUNTONLAKE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98032 | 0.87092 | 10.94 | Yes
Active | 2025W1-N11-WVD290048 | 290048 | 05DUNTONLAKE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97859 | 0.89844 | 8.015 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99972 | 0.85806 | 14.165 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99938 | 0.85435 | 14.503 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.85501 | 14.383 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.84305 | 15.72 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98597 | 0.80535 | 18.062 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98597 | 0.81288 | 17.309 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98597 | 0.81331 | 17.267 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98597 | 0.81854 | 16.744 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98597 | 0.83054 | 15.544 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98597 | 0.83542 | 15.055 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98597 | 0.84062 | 14.536 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.83713 | 16.52 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99767 | 0.84461 | 15.305 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.84513 | 15.299 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99961 | 0.85819 | 14.142 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99737 | 0.85127 | 14.61 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.87946 | 12.269 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99596 | 0.81321 | 18.275 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99596 | 0.82321 | 17.275 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.82767 | 17.258 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.80495 | 18.335 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9883 | 0.80743 | 18.087 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9883 | 0.84047 | 14.783 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9883 | 0.84306 | 14.524 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.91531 | 8.475 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.81132 | 18.301 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.85062 | 15.182 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99897 | 0.85526 | 14.371 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99162 | 0.80975 | 18.187 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99162 | 0.81446 | 17.716 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.84199 | 15.829 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9918 | 0.83199 | 15.981 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9918 | 0.83849 | 15.331 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.84112 | 15.699 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99905 | 0.84683 | 15.222 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99888 | 0.85285 | 14.603 | Yes
Active | 2025W1-N11-WVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9987 | 0.8522 | 14.651 | Yes
Active | 2025W1-N11-WVD290172 | 290172 | 05HUGUENARD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98455 | 0.87283 | 11.172 | Yes
Active | 2025W1-N11-WVD290172 | 290172 | 05HUGUENARD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96599 | 0.88501 | 8.099 | Yes
Active | 2025W1-N11-WVD290208 | 290208 | 05BECKWITH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99465 | 0.8801 | 11.454 | Yes
Active | 2025W1-N11-WVD290208 | 290208 | 05BECKWITH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99287 | 0.91205 | 8.083 | Yes
Active | 2025W1-N11-WVD290208 | 290208 | 05BECKWITH | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97412 | 0.89376 | 8.036 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98985 | 0.82265 | 16.72 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.8168 | 17.322 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98901 | 0.82065 | 16.836 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9938 | 0.80526 | 18.854 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.89796 | 8.89 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97357 | 0.76323 | 21.034 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97357 | 0.77407 | 19.95 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97357 | 0.77795 | 19.562 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97357 | 0.79225 | 18.132 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97357 | 0.79714 | 17.643 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97357 | 0.80507 | 16.849 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97357 | 0.80933 | 16.424 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97357 | 0.88979 | 8.378 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99356 | 0.79477 | 19.88 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98719 | 0.80401 | 18.318 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98799 | 0.80482 | 18.317 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99003 | 0.82342 | 16.66 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98678 | 0.81634 | 17.045 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98678 | 0.90673 | 8.005 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98773 | 0.81093 | 17.68 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.79935 | 18.704 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98639 | 0.81073 | 17.565 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99228 | 0.78844 | 20.384 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97802 | 0.76286 | 21.515 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97802 | 0.77414 | 20.388 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97802 | 0.79925 | 17.877 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97802 | 0.80835 | 16.967 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98785 | 0.88679 | 10.106 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98462 | 0.77106 | 21.357 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.81429 | 17.908 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98876 | 0.81924 | 16.952 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98313 | 0.77501 | 20.812 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98313 | 0.77805 | 20.508 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.80977 | 18.381 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99358 | 0.91019 | 8.338 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98111 | 0.79267 | 18.844 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98111 | 0.80226 | 17.886 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99208 | 0.9002 | 9.188 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.89796 | 8.89 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99127 | 0.91045 | 8.081 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.91097 | 8.025 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.80189 | 18.783 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98973 | 0.90404 | 8.568 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98969 | 0.80722 | 18.247 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98971 | 0.81657 | 17.314 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99153 | 0.90424 | 8.729 | Yes
Active | 2025W1-N11-WVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98941 | 0.81493 | 17.447 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99641 | 0.91403 | 8.238 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99641 | 0.91403 | 8.238 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.90466 | 9.132 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.89318 | 10.042 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.7921 | 20.006 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.91404 | 8.131 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.90537 | 8.801 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.79138 | 20.144 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99165 | 0.79275 | 19.89 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99388 | 0.78238 | 21.15 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.88462 | 10.694 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99337 | 0.9125 | 8.087 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96773 | 0.72696 | 24.077 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96773 | 0.74217 | 22.556 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96773 | 0.75466 | 21.307 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96773 | 0.7597 | 20.803 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96773 | 0.77625 | 19.148 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96773 | 0.87451 | 9.322 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.75622 | 24.076 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.90641 | 8.971 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98462 | 0.89328 | 9.134 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99271 | 0.91188 | 8.083 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.78398 | 20.705 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99103 | 0.90762 | 8.341 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99154 | 0.78442 | 20.712 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.90136 | 9.331 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99523 | 0.90541 | 8.982 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.90541 | 8.989 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99223 | 0.79374 | 19.849 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.91023 | 8.56 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98868 | 0.78652 | 20.216 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98868 | 0.89322 | 9.546 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.8991 | 9.367 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99572 | 0.90565 | 9.007 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99044 | 0.78486 | 20.558 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99044 | 0.90458 | 8.586 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98773 | 0.77467 | 21.306 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98773 | 0.78884 | 19.889 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99672 | 0.75596 | 24.076 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97471 | 0.72657 | 24.814 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97471 | 0.75431 | 22.04 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97471 | 0.76099 | 21.372 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97471 | 0.7909 | 18.38 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99008 | 0.86765 | 12.242 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.73925 | 25.085 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99358 | 0.90614 | 8.744 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99654 | 0.78039 | 21.615 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99459 | 0.91025 | 8.434 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99077 | 0.78844 | 20.234 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.7551 | 23.552 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99062 | 0.75561 | 23.5 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.7856 | 21.52 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.90385 | 9.695 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98498 | 0.77223 | 21.276 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98498 | 0.78536 | 19.962 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.91394 | 8.253 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99543 | 0.88096 | 11.447 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99479 | 0.90952 | 8.527 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.89897 | 8.832 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.89897 | 8.832 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99512 | 0.90416 | 9.095 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.90885 | 8.555 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.9065 | 8.324 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.90651 | 8.323 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.88462 | 10.694 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.89617 | 9.825 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99438 | 0.89675 | 9.763 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99533 | 0.91187 | 8.346 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99141 | 0.78079 | 21.063 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99141 | 0.89425 | 9.717 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99265 | 0.78596 | 20.669 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.90888 | 8.581 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9925 | 0.79085 | 20.165 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.88951 | 10.501 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99375 | 0.89799 | 9.576 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99504 | 0.91143 | 8.36 | Yes
Active | 2025W1-N11-WVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.78977 | 20.254 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99798 | 0.91642 | 8.156 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.82294 | 17.198 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99589 | 0.82218 | 17.371 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99495 | 0.82364 | 17.131 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99728 | 0.81147 | 18.581 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99383 | 0.90333 | 9.051 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97807 | 0.76273 | 21.534 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97807 | 0.77335 | 20.472 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97807 | 0.78069 | 19.738 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97807 | 0.79208 | 18.599 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97807 | 0.80435 | 17.372 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97807 | 0.80548 | 17.259 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97807 | 0.81134 | 16.673 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97807 | 0.8916 | 8.647 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97807 | 0.89327 | 8.48 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99899 | 0.7977 | 20.128 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99407 | 0.81283 | 18.123 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.81339 | 18.117 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.825 | 17.035 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99147 | 0.81537 | 17.61 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99147 | 0.90816 | 8.331 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99386 | 0.81529 | 17.857 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.79981 | 19.121 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99102 | 0.81288 | 17.813 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99748 | 0.78849 | 20.899 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98303 | 0.76216 | 22.088 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98303 | 0.77807 | 20.496 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98303 | 0.80183 | 18.12 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98303 | 0.81706 | 16.597 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.89376 | 10.181 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.77065 | 22.044 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99909 | 0.81472 | 18.436 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99364 | 0.81906 | 17.458 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99069 | 0.77972 | 21.097 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.78125 | 20.944 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99944 | 0.81188 | 18.756 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99944 | 0.91473 | 8.471 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98889 | 0.79984 | 18.905 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98889 | 0.81137 | 17.752 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.90374 | 9.389 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99383 | 0.90333 | 9.051 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.91536 | 8.215 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99748 | 0.91586 | 8.162 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99484 | 0.80944 | 18.54 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99484 | 0.91062 | 8.422 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99565 | 0.81523 | 18.042 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99557 | 0.82154 | 17.403 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.90858 | 8.887 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99684 | 0.91653 | 8.031 | Yes
Active | 2025W1-N11-WVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.82036 | 17.502 | Yes
Active | 2025W1-N11-WVD290246 | 290246 | 05S.TIFFN_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.92321 | 8.164 | Yes
Active | 2025W1-N11-WVD290246 | 290246 | 05S.TIFFN_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0052 | 0.91676 | 8.842 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98484 | 0.8868 | 9.805 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98484 | 0.89347 | 9.137 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98484 | 0.89633 | 8.852 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98484 | 0.9024 | 8.245 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9902 | 0.90858 | 8.162 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98378 | 0.90033 | 8.345 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98934 | 0.90792 | 8.142 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99029 | 0.89947 | 9.082 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98743 | 0.88636 | 10.107 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98743 | 0.88925 | 9.817 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98944 | 0.89118 | 9.826 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98948 | 0.89077 | 9.87 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98948 | 0.89621 | 9.326 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99096 | 0.91063 | 8.034 | Yes
Active | 2025W1-N11-WVD290252 | 290252 | 05SALTCRK SS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98922 | 0.90845 | 8.077 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99944 | 0.91888 | 8.056 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99944 | 0.91888 | 8.056 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99902 | 0.90977 | 8.926 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99666 | 0.89838 | 9.828 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.80048 | 19.482 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.91096 | 8.582 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.7997 | 19.625 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99479 | 0.80105 | 19.374 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99688 | 0.79065 | 20.623 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.89048 | 10.438 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97123 | 0.73458 | 23.664 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97123 | 0.75062 | 22.061 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97123 | 0.76334 | 20.788 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97123 | 0.76769 | 20.354 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97123 | 0.78451 | 18.672 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97123 | 0.87374 | 9.749 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97123 | 0.88046 | 9.076 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.763 | 23.711 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99918 | 0.91144 | 8.775 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98702 | 0.89761 | 8.941 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99422 | 0.79235 | 20.187 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99422 | 0.9128 | 8.143 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99471 | 0.79278 | 20.193 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.90651 | 9.122 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99828 | 0.91046 | 8.782 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99836 | 0.91046 | 8.79 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99548 | 0.8021 | 19.337 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99882 | 0.9151 | 8.371 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.79471 | 19.715 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99185 | 0.89871 | 9.315 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99586 | 0.9043 | 9.156 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99878 | 0.91068 | 8.81 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99357 | 0.79313 | 20.044 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99357 | 0.90973 | 8.384 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99083 | 0.78287 | 20.796 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99083 | 0.79727 | 19.356 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99997 | 0.76391 | 23.606 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97805 | 0.73421 | 24.384 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97805 | 0.76312 | 21.493 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97805 | 0.76789 | 21.016 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97805 | 0.79949 | 17.856 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99312 | 0.8735 | 11.962 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.74767 | 24.604 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99647 | 0.91068 | 8.579 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99966 | 0.7885 | 21.116 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99768 | 0.9152 | 8.248 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.79682 | 19.716 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99426 | 0.7638 | 23.046 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99426 | 0.76444 | 22.982 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.79438 | 20.975 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0041 | 0.90962 | 9.45 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98829 | 0.78048 | 20.781 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98829 | 0.79387 | 19.442 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99952 | 0.91877 | 8.074 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9987 | 0.88671 | 11.199 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99782 | 0.91454 | 8.329 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98962 | 0.9032 | 8.642 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98962 | 0.9032 | 8.642 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99817 | 0.90924 | 8.894 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99742 | 0.91369 | 8.373 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.91118 | 8.138 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.91119 | 8.138 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99486 | 0.89048 | 10.438 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.90148 | 9.603 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99748 | 0.90205 | 9.543 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.91677 | 8.164 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.78909 | 20.544 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99452 | 0.89975 | 9.477 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99578 | 0.79432 | 20.146 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99779 | 0.91387 | 8.392 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99563 | 0.79915 | 19.648 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.89504 | 10.256 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99686 | 0.90327 | 9.359 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99813 | 0.91636 | 8.177 | Yes
Active | 2025W1-N11-WVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99545 | 0.79807 | 19.739 | Yes
Active | 2025W1-N11-WVD290306 | 290306 | 05W.WATERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.91587 | 8.084 | Yes
Active | 2025W1-N11-WVD290306 | 290306 | 05W.WATERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99671 | 0.91653 | 8.017 | Yes
Active | 2025W1-N11-WVD290306 | 290306 | 05W.WATERT | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9982 | 0.91782 | 8.038 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.83378 | 15.351 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98809 | 0.83211 | 15.598 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98738 | 0.83266 | 15.472 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98864 | 0.8236 | 16.504 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98765 | 0.9069 | 8.074 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97295 | 0.77143 | 20.153 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97295 | 0.78304 | 18.992 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97295 | 0.79089 | 18.206 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97295 | 0.80127 | 17.169 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97295 | 0.81805 | 15.49 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97295 | 0.82011 | 15.284 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97295 | 0.82155 | 15.14 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97295 | 0.88755 | 8.54 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99014 | 0.80688 | 18.326 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98712 | 0.8255 | 16.162 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9874 | 0.8259 | 16.15 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98792 | 0.82692 | 16.099 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98009 | 0.81759 | 16.251 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98666 | 0.82519 | 16.147 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98512 | 0.81463 | 17.049 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98512 | 0.82807 | 15.705 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.7974 | 19.212 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9776 | 0.77064 | 20.696 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9776 | 0.78981 | 18.779 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9776 | 0.8111 | 16.65 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9776 | 0.83112 | 14.648 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98707 | 0.89504 | 9.203 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98473 | 0.78007 | 20.465 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9902 | 0.82292 | 16.729 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98654 | 0.83091 | 15.563 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98428 | 0.79134 | 19.294 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98428 | 0.79164 | 19.264 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9911 | 0.82179 | 16.931 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98355 | 0.81355 | 16.999 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98355 | 0.82593 | 15.762 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.89478 | 9.529 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98765 | 0.9069 | 8.074 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.8222 | 16.508 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98802 | 0.82732 | 16.07 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9879 | 0.83156 | 15.634 | Yes
Active | 2025W1-N11-WVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98779 | 0.83061 | 15.719 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.91402 | 8.238 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.91402 | 8.238 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99597 | 0.90465 | 9.132 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.89317 | 10.042 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99215 | 0.79209 | 20.007 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99534 | 0.91403 | 8.131 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.90536 | 8.802 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99282 | 0.79137 | 20.144 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99165 | 0.79274 | 19.89 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99387 | 0.78237 | 21.15 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99155 | 0.88461 | 10.694 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99336 | 0.91249 | 8.087 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96772 | 0.72695 | 24.077 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96772 | 0.74216 | 22.556 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96772 | 0.75465 | 21.307 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96772 | 0.75969 | 20.803 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96772 | 0.77624 | 19.148 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96772 | 0.8745 | 9.322 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99698 | 0.75621 | 24.077 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.9064 | 8.971 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98461 | 0.89327 | 9.134 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.91187 | 8.083 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.78397 | 20.705 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99102 | 0.90761 | 8.341 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99153 | 0.78441 | 20.712 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.90135 | 9.331 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99522 | 0.9054 | 8.982 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99529 | 0.9054 | 8.989 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99223 | 0.79373 | 19.849 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.91022 | 8.56 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98867 | 0.78651 | 20.216 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98867 | 0.89321 | 9.546 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.89909 | 9.367 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99571 | 0.90564 | 9.007 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.78485 | 20.559 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99043 | 0.90457 | 8.586 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98772 | 0.77466 | 21.306 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98772 | 0.78883 | 19.889 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.75595 | 24.076 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9747 | 0.72656 | 24.814 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9747 | 0.7543 | 22.04 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9747 | 0.76098 | 21.372 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9747 | 0.79089 | 18.381 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.86764 | 12.243 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99009 | 0.73924 | 25.085 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99357 | 0.90613 | 8.745 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99653 | 0.78038 | 21.615 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99458 | 0.91024 | 8.435 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99076 | 0.78843 | 20.234 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99061 | 0.75509 | 23.552 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99061 | 0.7556 | 23.501 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.78559 | 21.52 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.90384 | 9.695 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98498 | 0.77222 | 21.276 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98498 | 0.78535 | 19.962 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.91393 | 8.253 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99542 | 0.88095 | 11.447 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.90952 | 8.527 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.89896 | 8.832 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98728 | 0.89896 | 8.832 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.90415 | 9.095 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9944 | 0.90884 | 8.555 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.9065 | 8.324 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98974 | 0.9065 | 8.323 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99155 | 0.88461 | 10.694 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.89616 | 9.825 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.89674 | 9.763 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.91186 | 8.346 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99141 | 0.78078 | 21.063 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99141 | 0.89424 | 9.717 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99264 | 0.78595 | 20.669 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.90887 | 8.581 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.79084 | 20.165 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.8895 | 10.501 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99374 | 0.89798 | 9.576 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99503 | 0.91142 | 8.36 | Yes
Active | 2025W1-N11-WVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99231 | 0.78976 | 20.254 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99641 | 0.91404 | 8.238 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99641 | 0.91403 | 8.238 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99599 | 0.90467 | 9.132 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99361 | 0.89319 | 10.042 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.79211 | 20.006 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99536 | 0.91405 | 8.131 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99339 | 0.90538 | 8.801 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99283 | 0.79139 | 20.144 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99166 | 0.79276 | 19.89 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99389 | 0.78239 | 21.149 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.88463 | 10.693 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.91251 | 8.087 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96774 | 0.72697 | 24.077 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96774 | 0.74217 | 22.556 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96774 | 0.75467 | 21.307 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96774 | 0.75971 | 20.803 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96774 | 0.77626 | 19.148 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96774 | 0.87452 | 9.322 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.75623 | 24.076 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99613 | 0.90641 | 8.971 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98463 | 0.89329 | 9.133 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99272 | 0.91189 | 8.083 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99104 | 0.78399 | 20.705 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99104 | 0.90762 | 8.341 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99154 | 0.78443 | 20.712 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.90137 | 9.331 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99524 | 0.90542 | 8.982 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.90542 | 8.989 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99224 | 0.79375 | 19.849 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99584 | 0.91024 | 8.56 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98869 | 0.78653 | 20.216 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98869 | 0.89323 | 9.546 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99277 | 0.89911 | 9.367 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99572 | 0.90565 | 9.007 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99045 | 0.78487 | 20.558 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99045 | 0.90459 | 8.585 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.77468 | 21.306 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98774 | 0.78885 | 19.889 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99673 | 0.75597 | 24.076 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97472 | 0.72658 | 24.814 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97472 | 0.75432 | 22.04 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97472 | 0.761 | 21.372 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97472 | 0.79091 | 18.38 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99008 | 0.86766 | 12.242 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99011 | 0.73926 | 25.085 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.90614 | 8.744 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99655 | 0.7804 | 21.615 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9946 | 0.91026 | 8.434 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99078 | 0.78845 | 20.233 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99062 | 0.75511 | 23.552 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99062 | 0.75562 | 23.5 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.78561 | 21.519 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.90385 | 9.695 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98499 | 0.77224 | 21.275 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98499 | 0.78537 | 19.962 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99648 | 0.91394 | 8.253 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99544 | 0.88097 | 11.447 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.90953 | 8.526 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89898 | 8.831 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89898 | 8.831 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99512 | 0.90417 | 9.095 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.90886 | 8.555 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98975 | 0.90651 | 8.324 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98975 | 0.90652 | 8.323 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99156 | 0.88463 | 10.693 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99442 | 0.89618 | 9.825 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.89676 | 9.763 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99533 | 0.91188 | 8.345 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.7808 | 21.063 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99142 | 0.89425 | 9.717 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99265 | 0.78597 | 20.668 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.90889 | 8.581 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99251 | 0.79086 | 20.164 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99452 | 0.88952 | 10.5 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99376 | 0.898 | 9.576 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99504 | 0.91144 | 8.36 | Yes
Active | 2025W1-N11-WVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99232 | 0.78978 | 20.254 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9789 | 0.88681 | 9.21 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98154 | 0.80827 | 17.327 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98176 | 0.80371 | 17.806 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98065 | 0.80683 | 17.382 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98474 | 0.79348 | 19.126 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97913 | 0.88593 | 9.32 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96358 | 0.74596 | 21.762 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96358 | 0.76005 | 20.354 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96358 | 0.76666 | 19.692 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96358 | 0.7774 | 18.618 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96358 | 0.78711 | 17.647 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96358 | 0.88168 | 8.191 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9855 | 0.77477 | 21.073 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97928 | 0.79306 | 18.622 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97999 | 0.79372 | 18.627 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98346 | 0.90335 | 8.011 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98167 | 0.80909 | 17.258 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97834 | 0.80215 | 17.619 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97834 | 0.8946 | 8.374 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98183 | 0.90133 | 8.05 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97935 | 0.79923 | 18.012 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97677 | 0.78801 | 18.876 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97677 | 0.79915 | 17.761 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9851 | 0.7726 | 21.25 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96856 | 0.7456 | 22.296 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96856 | 0.76331 | 20.525 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96856 | 0.78047 | 18.808 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96856 | 0.79867 | 16.988 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97838 | 0.87176 | 10.662 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97627 | 0.75612 | 22.015 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9849 | 0.80037 | 18.453 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98045 | 0.80496 | 17.549 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97681 | 0.7634 | 21.341 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97681 | 0.76598 | 21.082 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98755 | 0.7981 | 18.945 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98755 | 0.90106 | 8.649 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97329 | 0.78187 | 19.141 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97329 | 0.79192 | 18.137 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98416 | 0.88614 | 9.802 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97913 | 0.88593 | 9.32 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98285 | 0.89755 | 8.529 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9828 | 0.89808 | 8.472 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98113 | 0.7907 | 19.043 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98113 | 0.89289 | 8.824 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98151 | 0.79578 | 18.572 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98146 | 0.80344 | 17.803 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9832 | 0.89176 | 9.144 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98235 | 0.89979 | 8.257 | Yes
Active | 2025W1-N11-WVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9812 | 0.80198 | 17.922 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99148 | 0.89448 | 9.7 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99148 | 0.8979 | 9.358 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99148 | 0.91017 | 8.131 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99801 | 0.9128 | 8.521 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.90791 | 8.983 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99256 | 0.88878 | 10.379 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99256 | 0.89664 | 9.593 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9943 | 0.90638 | 8.792 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98729 | 0.89263 | 9.466 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89664 | 9.065 | Yes
Active | 2025W1-N11-WVD290353 | 290353 | 05TARHE | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.91283 | 8.252 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98715 | 0.89757 | 8.958 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98781 | 0.80873 | 17.908 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98792 | 0.80394 | 18.398 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9868 | 0.80719 | 17.962 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.79338 | 19.76 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98354 | 0.88708 | 9.646 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97231 | 0.74806 | 22.425 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97231 | 0.76163 | 21.068 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97231 | 0.76772 | 20.459 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97231 | 0.77902 | 19.329 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97231 | 0.78798 | 18.433 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97231 | 0.7993 | 17.302 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97231 | 0.88234 | 8.997 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97231 | 0.88669 | 8.563 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99189 | 0.77625 | 21.564 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98533 | 0.79297 | 19.236 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98607 | 0.79365 | 19.242 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98989 | 0.90811 | 8.178 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98792 | 0.80962 | 17.83 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98455 | 0.80247 | 18.207 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98455 | 0.89875 | 8.58 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9881 | 0.90586 | 8.223 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9855 | 0.79939 | 18.611 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98328 | 0.78773 | 19.555 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98328 | 0.79907 | 18.422 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9912 | 0.7731 | 21.81 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97734 | 0.74769 | 22.965 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97734 | 0.7643 | 21.304 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97734 | 0.78301 | 19.432 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97734 | 0.79958 | 17.775 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98498 | 0.87556 | 10.942 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98294 | 0.75657 | 22.637 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99133 | 0.80039 | 19.093 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98667 | 0.80529 | 18.138 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98319 | 0.76324 | 21.995 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98319 | 0.76588 | 21.731 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99356 | 0.79776 | 19.58 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99356 | 0.90478 | 8.877 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97957 | 0.78153 | 19.804 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97957 | 0.79154 | 18.803 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99042 | 0.89015 | 10.027 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98354 | 0.88708 | 9.646 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98908 | 0.90154 | 8.754 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98902 | 0.90209 | 8.693 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98722 | 0.79056 | 19.667 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98722 | 0.89672 | 9.05 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98766 | 0.79576 | 19.19 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9876 | 0.80364 | 18.396 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98952 | 0.89582 | 9.371 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98863 | 0.90425 | 8.438 | Yes
Active | 2025W1-N11-WVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98733 | 0.80215 | 18.518 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.91443 | 8.222 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99665 | 0.91443 | 8.222 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99622 | 0.90508 | 9.114 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99384 | 0.89358 | 10.026 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99241 | 0.79276 | 19.965 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.9144 | 8.119 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99371 | 0.90591 | 8.779 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.79204 | 20.103 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9919 | 0.7934 | 19.85 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.78305 | 21.105 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.88515 | 10.67 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99367 | 0.91295 | 8.072 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.968 | 0.72759 | 24.04 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.968 | 0.74301 | 22.499 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.968 | 0.75553 | 21.247 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.968 | 0.76036 | 20.764 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.968 | 0.77692 | 19.108 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.968 | 0.86804 | 9.996 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.968 | 0.87501 | 9.299 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99726 | 0.75653 | 24.073 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99637 | 0.90682 | 8.955 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98468 | 0.89348 | 9.12 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.993 | 0.91231 | 8.069 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99129 | 0.78467 | 20.662 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99129 | 0.90806 | 8.323 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9918 | 0.7851 | 20.669 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.90178 | 9.313 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99547 | 0.90582 | 8.965 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99555 | 0.90582 | 8.972 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99252 | 0.79442 | 19.81 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99606 | 0.91062 | 8.544 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98893 | 0.78716 | 20.177 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98893 | 0.89368 | 9.525 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99301 | 0.89952 | 9.349 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99597 | 0.90606 | 8.991 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99068 | 0.78551 | 20.517 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99068 | 0.905 | 8.567 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98795 | 0.77532 | 21.262 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98795 | 0.78952 | 19.843 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99703 | 0.75661 | 24.041 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97496 | 0.72721 | 24.774 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97496 | 0.75521 | 21.975 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97496 | 0.76132 | 21.363 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97496 | 0.79163 | 18.333 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99029 | 0.86808 | 12.221 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99049 | 0.74009 | 25.04 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99378 | 0.90642 | 8.735 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99681 | 0.78105 | 21.576 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99484 | 0.91066 | 8.418 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.78911 | 20.192 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.75597 | 23.505 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99102 | 0.75651 | 23.451 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.78642 | 21.473 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0011 | 0.90446 | 9.669 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98525 | 0.77291 | 21.234 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98525 | 0.78607 | 19.918 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.91433 | 8.238 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99574 | 0.88146 | 11.428 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.90992 | 8.509 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89912 | 8.818 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98729 | 0.89912 | 8.818 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99536 | 0.90458 | 9.078 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99463 | 0.90922 | 8.541 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9899 | 0.90682 | 8.308 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9899 | 0.90682 | 8.308 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99185 | 0.88515 | 10.67 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99466 | 0.89661 | 9.806 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99463 | 0.89719 | 9.744 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.91227 | 8.33 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99165 | 0.78146 | 21.019 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99165 | 0.89472 | 9.694 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.78664 | 20.626 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99494 | 0.90929 | 8.565 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99275 | 0.79151 | 20.124 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99476 | 0.88997 | 10.479 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.89843 | 9.557 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99529 | 0.91184 | 8.345 | Yes
Active | 2025W1-N11-WVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.79043 | 20.214 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97713 | 0.89477 | 8.236 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9722 | 0.8778 | 9.44 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97384 | 0.79343 | 18.041 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97396 | 0.79001 | 18.395 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97281 | 0.7923 | 18.052 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97594 | 0.78051 | 19.543 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97175 | 0.87405 | 9.77 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95391 | 0.72991 | 22.4 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95391 | 0.74579 | 20.812 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95391 | 0.75434 | 19.957 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95391 | 0.76212 | 19.179 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95391 | 0.7745 | 17.941 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97807 | 0.75753 | 22.055 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97732 | 0.89598 | 8.134 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97292 | 0.89214 | 8.078 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97179 | 0.7812 | 19.059 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97241 | 0.78174 | 19.067 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97578 | 0.8914 | 8.438 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97631 | 0.89512 | 8.12 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97639 | 0.89513 | 8.126 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97395 | 0.79424 | 17.971 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97048 | 0.78743 | 18.305 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97048 | 0.88268 | 8.78 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97411 | 0.88939 | 8.472 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97689 | 0.89523 | 8.166 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97165 | 0.78512 | 18.653 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9689 | 0.7744 | 19.45 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9689 | 0.78576 | 18.314 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97805 | 0.75747 | 22.058 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95927 | 0.72954 | 22.972 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95927 | 0.75153 | 20.774 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.95927 | 0.76318 | 19.609 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95927 | 0.78629 | 17.298 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97056 | 0.85868 | 11.188 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96928 | 0.74202 | 22.726 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9772 | 0.78577 | 19.143 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97272 | 0.79018 | 18.254 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97071 | 0.75188 | 21.883 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97071 | 0.7539 | 21.681 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9813 | 0.78518 | 19.613 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9813 | 0.89129 | 9.002 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96569 | 0.76957 | 19.612 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96569 | 0.77987 | 18.582 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97664 | 0.87333 | 10.331 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9762 | 0.89395 | 8.225 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97175 | 0.87405 | 9.77 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97523 | 0.88555 | 8.968 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97518 | 0.8861 | 8.908 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97285 | 0.77834 | 19.451 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97285 | 0.88159 | 9.126 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97374 | 0.78352 | 19.022 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97364 | 0.78962 | 18.402 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97556 | 0.87981 | 9.575 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97476 | 0.88792 | 8.684 | Yes
Active | 2025W1-N11-WVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97341 | 0.78838 | 18.503 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.86308 | 14.04 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.86237 | 14.204 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.8626 | 14.121 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0048 | 0.85383 | 15.099 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99302 | 0.80746 | 18.556 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99302 | 0.81771 | 17.531 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99302 | 0.82321 | 16.98 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99302 | 0.83513 | 15.789 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99302 | 0.84864 | 14.438 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99302 | 0.84927 | 14.375 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99302 | 0.85156 | 14.146 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.99302 | 0.91142 | 8.16 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0061 | 0.84204 | 16.409 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.85577 | 14.772 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.85615 | 14.759 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.85985 | 14.348 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99578 | 0.84564 | 15.013 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.85733 | 14.586 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.84258 | 15.81 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.8539 | 14.677 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.8306 | 17.433 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99559 | 0.80604 | 18.955 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99559 | 0.81971 | 17.588 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99559 | 0.84596 | 14.963 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99559 | 0.85935 | 13.624 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.92223 | 8.247 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.8142 | 18.687 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.85451 | 15.188 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.86019 | 14.251 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.8221 | 17.848 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.82347 | 17.71 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.85105 | 15.503 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.84418 | 15.61 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0003 | 0.85438 | 14.59 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.85251 | 15.111 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0043 | 0.85751 | 14.679 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.86171 | 14.249 | Yes
Active | 2025W1-N11-WVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0041 | 0.86086 | 14.325 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98984 | 0.90702 | 8.281 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98608 | 0.89295 | 9.313 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98635 | 0.80184 | 18.451 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98664 | 0.79863 | 18.801 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9855 | 0.80102 | 18.448 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98869 | 0.78878 | 19.991 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98191 | 0.88214 | 9.977 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9684 | 0.73834 | 23.006 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9684 | 0.75365 | 21.475 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9684 | 0.76265 | 20.575 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.9684 | 0.77062 | 19.777 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9684 | 0.78314 | 18.526 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.9684 | 0.87575 | 9.265 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.9684 | 0.88066 | 8.773 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99076 | 0.76629 | 22.447 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.90846 | 8.155 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98488 | 0.90356 | 8.132 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98444 | 0.78945 | 19.499 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98507 | 0.79002 | 19.505 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9885 | 0.90369 | 8.482 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98904 | 0.9075 | 8.154 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98911 | 0.90751 | 8.16 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98649 | 0.80295 | 18.355 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98298 | 0.79569 | 18.729 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98298 | 0.89474 | 8.825 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98669 | 0.90149 | 8.521 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9896 | 0.90772 | 8.188 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98423 | 0.7932 | 19.103 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9816 | 0.78197 | 19.963 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9816 | 0.79403 | 18.756 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99052 | 0.76551 | 22.501 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97401 | 0.73797 | 23.604 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97401 | 0.76014 | 21.387 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97401 | 0.77239 | 20.162 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97401 | 0.79557 | 17.844 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98346 | 0.87061 | 11.285 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98261 | 0.74939 | 23.322 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98983 | 0.79316 | 19.666 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98516 | 0.79833 | 18.684 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98399 | 0.76003 | 22.396 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98399 | 0.76174 | 22.225 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99375 | 0.79316 | 20.059 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99375 | 0.90322 | 9.053 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97909 | 0.77766 | 20.143 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97909 | 0.78848 | 19.062 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98918 | 0.88511 | 10.407 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98892 | 0.9063 | 8.262 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98191 | 0.88214 | 9.977 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98792 | 0.8977 | 9.022 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98787 | 0.89826 | 8.961 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98556 | 0.78657 | 19.899 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98556 | 0.89389 | 9.167 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98642 | 0.79185 | 19.458 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98632 | 0.79821 | 18.81 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98826 | 0.89176 | 9.651 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98743 | 0.9001 | 8.734 | Yes
Active | 2025W1-N11-WVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98608 | 0.79692 | 18.916 | Yes
Active | 2025W1-N11-WVD290505 | 290505 | 05IRON TRI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0057 | 0.92048 | 8.521 | Yes
Active | 2025W1-N11-WVD290505 | 290505 | 05IRON TRI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0057 | 0.92536 | 8.033 | Yes
Active | 2025W1-N11-WVD290505 | 290505 | 05IRON TRI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.006 | 0.91345 | 9.251 | Yes
Active | 2025W1-N11-WVD290505 | 290505 | 05IRON TRI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.92432 | 8.163 | Yes
Active | 2025W1-N11-WVD290505 | 290505 | 05IRON TRI | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.91833 | 8.172 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98315 | 0.90303 | 8.012 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9785 | 0.88682 | 9.168 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97999 | 0.80594 | 17.405 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98007 | 0.80273 | 17.734 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97895 | 0.80482 | 17.413 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9817 | 0.79329 | 18.84 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97867 | 0.88432 | 9.435 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95954 | 0.74055 | 21.898 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95954 | 0.75706 | 20.247 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95954 | 0.76621 | 19.332 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95954 | 0.77363 | 18.59 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95954 | 0.78701 | 17.252 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.95954 | 0.87774 | 8.18 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98409 | 0.76876 | 21.532 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97805 | 0.79427 | 18.378 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97863 | 0.79479 | 18.383 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98182 | 0.89974 | 8.207 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98011 | 0.80671 | 17.34 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9767 | 0.79988 | 17.682 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9767 | 0.89152 | 8.518 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98032 | 0.89799 | 8.233 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97786 | 0.79771 | 18.015 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9751 | 0.78703 | 18.807 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9751 | 0.79851 | 17.659 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98424 | 0.7692 | 21.504 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96477 | 0.74017 | 22.461 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96477 | 0.7634 | 20.137 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96477 | 0.77423 | 19.055 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96477 | 0.79894 | 16.584 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97667 | 0.86839 | 10.828 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97485 | 0.75357 | 22.128 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98329 | 0.79829 | 18.5 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97891 | 0.80269 | 17.622 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97703 | 0.76413 | 21.289 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97703 | 0.76612 | 21.091 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98755 | 0.79799 | 18.956 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98755 | 0.90028 | 8.727 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97199 | 0.78237 | 18.962 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97199 | 0.79282 | 17.917 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98279 | 0.88245 | 10.034 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98223 | 0.90219 | 8.004 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97867 | 0.88432 | 9.435 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98137 | 0.8943 | 8.707 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98133 | 0.89483 | 8.65 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97886 | 0.79123 | 18.762 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97886 | 0.89062 | 8.824 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97986 | 0.79652 | 18.333 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97976 | 0.80231 | 17.744 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98164 | 0.8888 | 9.284 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98089 | 0.89652 | 8.437 | Yes
Active | 2025W1-N11-WVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97954 | 0.8011 | 17.844 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.86525 | 13.549 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.86195 | 13.843 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99989 | 0.86213 | 13.775 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.85084 | 15.008 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98768 | 0.81445 | 17.324 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98768 | 0.82081 | 16.688 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98768 | 0.8219 | 16.578 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98768 | 0.82193 | 16.575 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98768 | 0.83875 | 14.894 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98768 | 0.84351 | 14.418 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98768 | 0.84765 | 14.003 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0031 | 0.84559 | 15.75 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99884 | 0.85261 | 14.623 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99923 | 0.85308 | 14.614 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.8653 | 13.531 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99861 | 0.85859 | 14.002 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.89375 | 11.099 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.81669 | 18.083 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99752 | 0.82663 | 17.089 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.83604 | 16.501 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98976 | 0.81404 | 17.571 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98976 | 0.8154 | 17.436 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98976 | 0.84874 | 14.102 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98976 | 0.85067 | 13.908 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.92026 | 8.102 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99563 | 0.82007 | 17.556 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.85806 | 14.518 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.86257 | 13.749 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99276 | 0.81789 | 17.487 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99276 | 0.82257 | 17.019 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.84916 | 15.173 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99326 | 0.84027 | 15.299 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99326 | 0.84638 | 14.688 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99907 | 0.84908 | 15 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.85468 | 14.536 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99987 | 0.86029 | 13.958 | Yes
Active | 2025W1-N11-WVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.85977 | 13.994 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.90632 | 8.496 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.89549 | 9.349 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.80426 | 18.348 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98945 | 0.90814 | 8.131 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98837 | 0.80345 | 18.492 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98727 | 0.80469 | 18.258 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98917 | 0.79448 | 19.469 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98756 | 0.8886 | 9.896 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96457 | 0.73677 | 22.78 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96457 | 0.75329 | 21.128 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96457 | 0.76657 | 19.8 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96457 | 0.77076 | 19.38 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96457 | 0.7883 | 17.627 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96457 | 0.8786 | 8.597 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99233 | 0.76573 | 22.66 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99143 | 0.90796 | 8.347 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98388 | 0.9001 | 8.378 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98677 | 0.7963 | 19.048 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98723 | 0.79673 | 19.05 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.90325 | 8.679 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99059 | 0.90702 | 8.356 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99067 | 0.90702 | 8.365 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98806 | 0.80559 | 18.247 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98433 | 0.7982 | 18.612 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98433 | 0.89594 | 8.839 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98828 | 0.90125 | 8.702 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99105 | 0.90723 | 8.382 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.79697 | 18.914 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98346 | 0.78661 | 19.684 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98346 | 0.80136 | 18.21 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.76694 | 22.533 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97113 | 0.73639 | 23.473 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97113 | 0.76655 | 20.458 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97113 | 0.77074 | 20.039 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97113 | 0.80361 | 16.751 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98561 | 0.8722 | 11.341 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.75029 | 23.605 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9882 | 0.90587 | 8.234 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99189 | 0.79177 | 20.012 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98652 | 0.80072 | 18.58 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9869 | 0.76705 | 21.985 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9869 | 0.76793 | 21.897 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9963 | 0.7982 | 19.81 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9963 | 0.90664 | 8.966 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98113 | 0.78423 | 19.689 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98113 | 0.79804 | 18.309 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99137 | 0.88448 | 10.689 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98522 | 0.90331 | 8.191 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98522 | 0.90331 | 8.191 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99049 | 0.90585 | 8.463 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98756 | 0.8886 | 9.896 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98985 | 0.89858 | 9.126 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98982 | 0.89912 | 9.069 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98699 | 0.79295 | 19.404 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98699 | 0.89723 | 8.976 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98821 | 0.79824 | 18.998 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98807 | 0.80291 | 18.516 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98993 | 0.89257 | 9.736 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98924 | 0.9003 | 8.895 | Yes
Active | 2025W1-N11-WVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98791 | 0.80185 | 18.605 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96518 | 0.88505 | 8.013 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96455 | 0.88425 | 8.03 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96397 | 0.8832 | 8.077 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96407 | 0.88186 | 8.221 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.94849 | 0.82914 | 11.935 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94849 | 0.82928 | 11.921 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.94849 | 0.85484 | 9.365 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96584 | 0.85431 | 11.154 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96415 | 0.88373 | 8.042 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96427 | 0.88375 | 8.052 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96523 | 0.88505 | 8.018 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96283 | 0.88109 | 8.173 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96386 | 0.88241 | 8.146 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96214 | 0.86652 | 9.562 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96214 | 0.8791 | 8.304 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96266 | 0.8525 | 11.016 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94334 | 0.83026 | 11.309 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.94334 | 0.85823 | 8.511 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96485 | 0.88397 | 8.087 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96449 | 0.8363 | 12.82 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96449 | 0.88197 | 8.253 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9607 | 0.86532 | 9.539 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9607 | 0.87796 | 8.274 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96355 | 0.88187 | 8.168 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96455 | 0.88406 | 8.05 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96438 | 0.88382 | 8.055 | Yes
Active | 2025W1-N11-WVD290607 | 290607 | 05SORENSN_RM | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96433 | 0.88359 | 8.074 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95725 | 0.8756 | 8.165 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95689 | 0.80941 | 14.747 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95675 | 0.80838 | 14.837 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95593 | 0.80862 | 14.731 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95663 | 0.80174 | 15.489 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95763 | 0.87344 | 8.419 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93005 | 0.71319 | 21.686 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93005 | 0.75997 | 17.008 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93005 | 0.79657 | 13.348 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.93005 | 0.79924 | 13.081 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.93005 | 0.80356 | 12.649 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95958 | 0.74415 | 21.543 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95579 | 0.80423 | 15.156 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95579 | 0.87404 | 8.175 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95607 | 0.80446 | 15.161 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95689 | 0.80995 | 14.693 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95422 | 0.80432 | 14.99 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95422 | 0.86319 | 9.103 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.955 | 0.80351 | 15.149 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.955 | 0.87098 | 8.402 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9524 | 0.78534 | 16.706 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9524 | 0.79536 | 15.705 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96166 | 0.75637 | 20.529 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9267 | 0.71313 | 21.357 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9267 | 0.74926 | 17.744 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9267 | 0.78744 | 13.926 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94985 | 0.85325 | 9.66 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95438 | 0.85293 | 10.145 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96001 | 0.82363 | 13.637 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95614 | 0.80692 | 14.922 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9699 | 0.80604 | 16.387 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9699 | 0.88026 | 8.964 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95078 | 0.78246 | 16.832 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95078 | 0.7935 | 15.728 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95859 | 0.86822 | 9.038 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95763 | 0.87344 | 8.419 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95532 | 0.80094 | 15.438 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95532 | 0.86309 | 9.223 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9567 | 0.80548 | 15.122 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9565 | 0.80784 | 14.866 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95789 | 0.87393 | 8.396 | Yes
Active | 2025W1-N11-WVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9564 | 0.80714 | 14.926 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95789 | 0.87579 | 8.21 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95751 | 0.80896 | 14.855 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9574 | 0.80793 | 14.947 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95657 | 0.8082 | 14.837 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95731 | 0.80123 | 15.608 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95824 | 0.87354 | 8.47 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93066 | 0.71363 | 21.703 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.93066 | 0.76008 | 17.058 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93066 | 0.7695 | 16.116 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93066 | 0.79599 | 13.467 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.93066 | 0.79868 | 13.199 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96028 | 0.74414 | 21.614 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95643 | 0.80369 | 15.274 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95643 | 0.87503 | 8.14 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95671 | 0.80393 | 15.278 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95751 | 0.80951 | 14.799 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95485 | 0.80386 | 15.099 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95485 | 0.86414 | 9.071 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95563 | 0.803 | 15.263 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95563 | 0.87197 | 8.366 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95303 | 0.78598 | 16.706 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95303 | 0.79476 | 15.827 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96242 | 0.75645 | 20.597 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.92781 | 0.71356 | 21.424 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.92781 | 0.74928 | 17.853 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.92781 | 0.75362 | 17.419 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.92781 | 0.78809 | 13.971 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95087 | 0.85372 | 9.715 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96057 | 0.82306 | 13.751 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95675 | 0.80643 | 15.032 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96075 | 0.75517 | 20.558 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96075 | 0.77066 | 19.008 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97012 | 0.80544 | 16.468 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97012 | 0.88076 | 8.936 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95142 | 0.7831 | 16.832 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95142 | 0.7929 | 15.852 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95925 | 0.86834 | 9.091 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95824 | 0.87354 | 8.47 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95598 | 0.8004 | 15.558 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95598 | 0.86407 | 9.191 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95735 | 0.80497 | 15.238 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95715 | 0.80739 | 14.976 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95856 | 0.87413 | 8.443 | Yes
Active | 2025W1-N11-WVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95705 | 0.80668 | 15.037 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95798 | 0.87658 | 8.141 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95762 | 0.81057 | 14.704 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9575 | 0.80957 | 14.793 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95668 | 0.80979 | 14.689 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95739 | 0.80295 | 15.444 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95836 | 0.87442 | 8.394 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.93086 | 0.77041 | 16.045 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.93086 | 0.79777 | 13.309 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.93086 | 0.8004 | 13.046 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.93086 | 0.80426 | 12.66 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95655 | 0.80542 | 15.113 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95683 | 0.80565 | 15.117 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95761 | 0.8111 | 14.651 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95498 | 0.80551 | 14.947 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95574 | 0.80469 | 15.106 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95316 | 0.79653 | 15.663 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95101 | 0.85482 | 9.619 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95503 | 0.85379 | 10.124 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96071 | 0.82473 | 13.598 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95687 | 0.80808 | 14.879 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96062 | 0.7716 | 18.902 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97008 | 0.8067 | 16.338 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95158 | 0.79471 | 15.687 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95932 | 0.86921 | 9.011 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95836 | 0.87442 | 8.394 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95609 | 0.80215 | 15.394 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95745 | 0.80667 | 15.078 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95725 | 0.80902 | 14.823 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95864 | 0.87494 | 8.371 | Yes
Active | 2025W1-N11-WVD290621 | 290621 | 05MARYSVL_RF | 765 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95715 | 0.80833 | 14.882 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.91563 | 8.035 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.91563 | 8.035 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99556 | 0.90652 | 8.903 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99319 | 0.89517 | 9.802 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99184 | 0.79712 | 19.472 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.90746 | 8.572 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99248 | 0.79631 | 19.617 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99132 | 0.79771 | 19.361 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.78722 | 20.628 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.88685 | 10.43 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.968 | 0.73169 | 23.631 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.968 | 0.74727 | 22.073 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.968 | 0.75979 | 20.822 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.968 | 0.76451 | 20.349 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.968 | 0.78107 | 18.693 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.968 | 0.87042 | 9.758 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.968 | 0.8773 | 9.07 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99659 | 0.7604 | 23.619 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99571 | 0.90818 | 8.753 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98342 | 0.89422 | 8.919 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99072 | 0.78884 | 20.188 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99072 | 0.90934 | 8.138 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99122 | 0.78928 | 20.194 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.90328 | 9.1 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99482 | 0.90721 | 8.761 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99489 | 0.90721 | 8.768 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.79876 | 19.316 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9954 | 0.9119 | 8.35 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98845 | 0.79147 | 19.698 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98845 | 0.89542 | 9.303 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.90104 | 9.135 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.90743 | 8.788 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99012 | 0.78976 | 20.036 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99012 | 0.90639 | 8.373 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98743 | 0.7795 | 20.793 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98743 | 0.79375 | 19.368 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99639 | 0.76073 | 23.566 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9748 | 0.73132 | 24.348 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9748 | 0.75943 | 21.537 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9748 | 0.76525 | 20.955 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9748 | 0.79586 | 17.894 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.87033 | 11.936 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98998 | 0.74432 | 24.566 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99328 | 0.90801 | 8.527 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.78528 | 21.083 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99421 | 0.91193 | 8.228 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9905 | 0.79344 | 19.706 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99055 | 0.7602 | 23.035 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99055 | 0.7607 | 22.985 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.79076 | 20.97 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.90595 | 9.451 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98482 | 0.77701 | 20.781 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98482 | 0.79022 | 19.46 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99605 | 0.91553 | 8.052 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99504 | 0.88349 | 11.155 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.91129 | 8.312 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.986 | 0.89979 | 8.621 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.986 | 0.89979 | 8.621 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9947 | 0.90599 | 8.871 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.9105 | 8.349 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98951 | 0.90832 | 8.119 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98951 | 0.90833 | 8.118 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99115 | 0.88685 | 10.43 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99403 | 0.89819 | 9.584 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.89876 | 9.524 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99493 | 0.9135 | 8.143 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99109 | 0.78562 | 20.547 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99109 | 0.89633 | 9.476 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9923 | 0.79083 | 20.147 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99431 | 0.9106 | 8.371 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99216 | 0.79577 | 19.639 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.89174 | 10.239 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.89999 | 9.339 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99465 | 0.91308 | 8.157 | Yes
Active | 2025W1-N11-WVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99198 | 0.79468 | 19.73 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0018 | 0.90777 | 9.4 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.91287 | 8.891 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0065 | 0.92633 | 8.02 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0062 | 0.92248 | 8.374 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.002 | 0.89983 | 10.22 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.91191 | 9.012 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9949 | 0.905 | 8.99 | Yes
Active | 2025W1-N11-WVD290656 | 290656 | 05INVISIONSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.91161 | 8.33 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97937 | 0.88732 | 9.204 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98168 | 0.80743 | 17.425 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98192 | 0.80293 | 17.899 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9808 | 0.80603 | 17.477 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98488 | 0.7927 | 19.218 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97904 | 0.8853 | 9.374 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96403 | 0.74532 | 21.871 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96403 | 0.75933 | 20.47 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96403 | 0.76605 | 19.798 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96403 | 0.77674 | 18.729 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96403 | 0.78653 | 17.75 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96403 | 0.8775 | 8.653 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96403 | 0.88156 | 8.247 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98568 | 0.77395 | 21.173 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97944 | 0.79231 | 18.713 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98015 | 0.79297 | 18.718 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98362 | 0.90318 | 8.044 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98182 | 0.80828 | 17.354 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97847 | 0.8013 | 17.717 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97847 | 0.89439 | 8.409 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98199 | 0.90115 | 8.084 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97949 | 0.79838 | 18.111 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9769 | 0.78709 | 18.981 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9769 | 0.79829 | 17.861 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98527 | 0.77176 | 21.351 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96904 | 0.74496 | 22.408 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96904 | 0.76274 | 20.631 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96904 | 0.77983 | 18.922 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96904 | 0.79814 | 17.09 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97855 | 0.87144 | 10.711 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97646 | 0.75523 | 22.122 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98507 | 0.79947 | 18.56 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98059 | 0.8041 | 17.649 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97706 | 0.76265 | 21.44 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97706 | 0.7652 | 21.186 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98774 | 0.79726 | 19.048 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98774 | 0.90091 | 8.683 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97351 | 0.78111 | 19.239 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97351 | 0.79119 | 18.232 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98433 | 0.88587 | 9.846 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97904 | 0.8853 | 9.374 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98301 | 0.89734 | 8.567 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98296 | 0.89787 | 8.509 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98128 | 0.78994 | 19.134 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98128 | 0.89272 | 8.855 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98166 | 0.79503 | 18.664 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98162 | 0.80265 | 17.897 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98337 | 0.89154 | 9.183 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98252 | 0.89961 | 8.291 | Yes
Active | 2025W1-N11-WVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98135 | 0.80119 | 18.016 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92266 | 8.018 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92266 | 8.018 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.91361 | 8.88 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.90221 | 9.784 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.80504 | 19.367 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.9148 | 8.541 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99935 | 0.80423 | 19.511 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99819 | 0.8056 | 19.259 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.79516 | 20.512 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99824 | 0.89435 | 10.388 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97471 | 0.73922 | 23.549 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97471 | 0.75542 | 21.929 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97471 | 0.76812 | 20.66 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97471 | 0.77227 | 20.245 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97471 | 0.78902 | 18.569 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97471 | 0.79815 | 17.656 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97471 | 0.87783 | 9.689 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97471 | 0.88455 | 9.016 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.76724 | 23.628 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.91523 | 8.735 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98827 | 0.89891 | 8.936 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99762 | 0.79685 | 20.077 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99762 | 0.91657 | 8.105 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.79729 | 20.082 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.91035 | 9.077 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.91426 | 8.74 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.91427 | 8.748 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99887 | 0.80668 | 19.219 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.91888 | 8.333 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99532 | 0.7993 | 19.601 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99532 | 0.90267 | 9.265 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99924 | 0.90812 | 9.113 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.91448 | 8.77 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99697 | 0.79766 | 19.931 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99697 | 0.91353 | 8.344 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99423 | 0.7874 | 20.682 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99423 | 0.80183 | 19.24 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.76848 | 23.491 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9815 | 0.73886 | 24.264 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9815 | 0.76789 | 21.361 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9815 | 0.77215 | 20.935 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9815 | 0.80404 | 17.745 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9965 | 0.87744 | 11.905 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99722 | 0.75247 | 24.475 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.91481 | 8.524 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.79304 | 21.003 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.91898 | 8.21 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.80138 | 19.602 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99777 | 0.76856 | 22.921 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99777 | 0.76919 | 22.859 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.79905 | 20.853 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0076 | 0.91355 | 9.403 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99171 | 0.78499 | 20.672 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99171 | 0.79838 | 19.332 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.92254 | 8.037 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.89071 | 11.131 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91834 | 8.29 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.90531 | 8.615 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.90531 | 8.615 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.91305 | 8.851 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.91744 | 8.337 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.91517 | 8.102 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99619 | 0.91518 | 8.101 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99824 | 0.89435 | 10.388 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90532 | 9.559 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90588 | 9.499 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.92053 | 8.127 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99792 | 0.79359 | 20.433 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99792 | 0.90361 | 9.432 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.79883 | 20.034 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91765 | 8.353 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99903 | 0.80369 | 19.534 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.89893 | 10.206 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.90711 | 9.315 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.92012 | 8.14 | Yes
Active | 2025W1-N11-WVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99885 | 0.8026 | 19.625 | Yes
Active | 2025W1-N11-WVD290761 | 290761 | 05KEKIONGA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99748 | 0.88173 | 11.575 | Yes
Active | 2025W1-N11-WVD290761 | 290761 | 05KEKIONGA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99571 | 0.91433 | 8.138 | Yes
Active | 2025W1-N11-WVD290761 | 290761 | 05KEKIONGA | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97691 | 0.89483 | 8.208 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99868 | 0.9178 | 8.088 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99868 | 0.9178 | 8.088 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99826 | 0.90865 | 8.961 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99589 | 0.89723 | 9.866 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.79877 | 19.575 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99596 | 0.90977 | 8.619 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99517 | 0.79801 | 19.716 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99401 | 0.79936 | 19.465 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.78897 | 20.715 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99406 | 0.88924 | 10.482 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97038 | 0.73305 | 23.733 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97038 | 0.74898 | 22.141 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97038 | 0.76165 | 20.873 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97038 | 0.76608 | 20.431 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97038 | 0.78283 | 18.755 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97038 | 0.87244 | 9.795 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97038 | 0.8792 | 9.119 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99933 | 0.76153 | 23.781 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99842 | 0.91033 | 8.809 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98635 | 0.8966 | 8.975 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99343 | 0.79066 | 20.277 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99343 | 0.91166 | 8.177 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99392 | 0.79109 | 20.283 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99696 | 0.90538 | 9.158 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.90935 | 8.817 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.90935 | 8.824 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.80041 | 19.428 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99806 | 0.91402 | 8.404 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99106 | 0.79304 | 19.803 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99106 | 0.89752 | 9.354 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99508 | 0.90316 | 9.192 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99802 | 0.90957 | 8.844 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99278 | 0.79144 | 20.134 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99278 | 0.90859 | 8.419 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99004 | 0.7812 | 20.884 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99004 | 0.79556 | 19.449 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99918 | 0.7623 | 23.688 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97723 | 0.73268 | 24.455 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97723 | 0.76141 | 21.582 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97723 | 0.7664 | 21.083 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97723 | 0.79776 | 17.947 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99235 | 0.87223 | 12.012 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99288 | 0.74603 | 24.684 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.90964 | 8.609 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99889 | 0.78686 | 21.203 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99691 | 0.91411 | 8.28 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99318 | 0.79511 | 19.807 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.7621 | 23.132 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99342 | 0.76272 | 23.07 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.79264 | 21.069 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0033 | 0.90842 | 9.491 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98748 | 0.77881 | 20.867 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98748 | 0.79215 | 19.533 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99875 | 0.9177 | 8.105 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99791 | 0.88549 | 11.242 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99705 | 0.91342 | 8.363 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98893 | 0.90217 | 8.675 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98893 | 0.90217 | 8.675 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9974 | 0.90812 | 8.928 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99666 | 0.91261 | 8.405 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.91012 | 8.17 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.91012 | 8.17 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99406 | 0.88924 | 10.482 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99674 | 0.90032 | 9.642 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9967 | 0.90089 | 9.581 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99763 | 0.91568 | 8.195 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99374 | 0.7874 | 20.634 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99374 | 0.89856 | 9.518 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.79262 | 20.237 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99701 | 0.91277 | 8.424 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99485 | 0.79746 | 19.739 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99683 | 0.89385 | 10.298 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99609 | 0.90212 | 9.396 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99735 | 0.91527 | 8.209 | Yes
Active | 2025W1-N11-WVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99467 | 0.79638 | 19.829 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99608 | 0.9157 | 8.038 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99608 | 0.9157 | 8.038 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99566 | 0.90659 | 8.907 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99329 | 0.89522 | 9.806 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.79716 | 19.478 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99329 | 0.90754 | 8.575 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.79635 | 19.623 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99142 | 0.79775 | 19.367 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99359 | 0.78727 | 20.632 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99127 | 0.88694 | 10.433 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96807 | 0.73175 | 23.632 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96807 | 0.74738 | 22.07 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96807 | 0.75989 | 20.818 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96807 | 0.76457 | 20.351 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96807 | 0.78113 | 18.695 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96807 | 0.87049 | 9.758 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96807 | 0.87736 | 9.071 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9967 | 0.76037 | 23.633 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.90824 | 8.757 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98334 | 0.89408 | 8.926 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99082 | 0.78889 | 20.193 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99082 | 0.90942 | 8.14 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99132 | 0.78933 | 20.199 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.90334 | 9.103 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.90727 | 8.764 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99499 | 0.90727 | 8.772 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99204 | 0.79881 | 19.323 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9955 | 0.91196 | 8.354 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98855 | 0.7915 | 19.704 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98855 | 0.89549 | 9.306 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99249 | 0.9011 | 9.139 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99542 | 0.90749 | 8.792 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99022 | 0.7898 | 20.041 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99022 | 0.90645 | 8.376 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98752 | 0.77955 | 20.797 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98752 | 0.7938 | 19.372 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99651 | 0.76079 | 23.572 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97488 | 0.73138 | 24.349 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97488 | 0.75955 | 21.533 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97488 | 0.76522 | 20.965 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97488 | 0.79592 | 17.895 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98979 | 0.87037 | 11.942 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99012 | 0.74443 | 24.569 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99337 | 0.90805 | 8.532 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99622 | 0.78533 | 21.09 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99431 | 0.912 | 8.232 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9906 | 0.79348 | 19.712 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99068 | 0.76031 | 23.037 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99068 | 0.76082 | 22.987 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.79083 | 20.975 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0006 | 0.90606 | 9.452 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98492 | 0.77707 | 20.785 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98492 | 0.79028 | 19.464 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99615 | 0.91559 | 8.056 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99515 | 0.88355 | 11.16 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.91135 | 8.315 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98597 | 0.89971 | 8.626 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98597 | 0.89971 | 8.626 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.90605 | 8.875 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.91056 | 8.353 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.90837 | 8.122 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98959 | 0.90837 | 8.122 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99127 | 0.88694 | 10.433 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.89825 | 9.588 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9941 | 0.89882 | 9.528 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99503 | 0.91356 | 8.147 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99118 | 0.78567 | 20.551 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99118 | 0.8964 | 9.478 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.79088 | 20.152 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99441 | 0.91066 | 8.375 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99226 | 0.79581 | 19.644 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99423 | 0.8918 | 10.243 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99348 | 0.90005 | 9.343 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.91315 | 8.16 | Yes
Active | 2025W1-N11-WVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99208 | 0.79472 | 19.735 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92265 | 8.018 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.92265 | 8.018 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.9136 | 8.881 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.90219 | 9.784 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99871 | 0.80503 | 19.368 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.91479 | 8.541 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99934 | 0.80422 | 19.512 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99818 | 0.80559 | 19.26 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.79514 | 20.513 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.89435 | 10.389 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97471 | 0.73921 | 23.55 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97471 | 0.75541 | 21.929 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97471 | 0.76811 | 20.66 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97471 | 0.77225 | 20.246 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97471 | 0.78901 | 18.57 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97471 | 0.79814 | 17.656 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97471 | 0.87782 | 9.689 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.97471 | 0.88454 | 9.016 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0035 | 0.76722 | 23.63 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.91522 | 8.735 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98825 | 0.89888 | 8.936 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99762 | 0.79684 | 20.078 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99762 | 0.91656 | 8.106 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99811 | 0.79727 | 20.083 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.91034 | 9.078 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.91425 | 8.741 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.91426 | 8.748 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.80667 | 19.22 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.91887 | 8.333 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99531 | 0.79929 | 19.602 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99531 | 0.90266 | 9.265 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99924 | 0.90811 | 9.113 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.91447 | 8.771 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99696 | 0.79764 | 19.932 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99696 | 0.91352 | 8.344 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99422 | 0.78739 | 20.683 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99422 | 0.80181 | 19.241 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.76847 | 23.493 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98149 | 0.73884 | 24.265 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98149 | 0.76788 | 21.362 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98149 | 0.77213 | 20.937 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98149 | 0.80403 | 17.746 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.87743 | 11.906 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99722 | 0.75246 | 24.476 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.9148 | 8.524 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0031 | 0.79303 | 21.004 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.91897 | 8.21 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99739 | 0.80137 | 19.603 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99777 | 0.76855 | 22.922 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99777 | 0.76917 | 22.86 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0076 | 0.79904 | 20.854 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0076 | 0.91354 | 9.403 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.78498 | 20.673 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9917 | 0.79837 | 19.333 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.92253 | 8.038 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.8907 | 11.131 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91833 | 8.29 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.90531 | 8.615 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.90531 | 8.615 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.91304 | 8.851 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.91743 | 8.337 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.91516 | 8.102 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99618 | 0.91517 | 8.102 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99823 | 0.89435 | 10.389 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90531 | 9.559 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.90587 | 9.499 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.92052 | 8.128 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99792 | 0.79358 | 20.434 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99792 | 0.9036 | 9.432 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99917 | 0.79882 | 20.035 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.91764 | 8.354 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99902 | 0.80368 | 19.535 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.89892 | 10.207 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.9071 | 9.315 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.92011 | 8.14 | Yes
Active | 2025W1-N11-WVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99885 | 0.80259 | 19.626 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99681 | 0.91447 | 8.234 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99681 | 0.91447 | 8.234 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99638 | 0.90511 | 9.128 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.994 | 0.89364 | 10.037 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99257 | 0.79261 | 19.996 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.91448 | 8.127 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99379 | 0.90582 | 8.797 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99323 | 0.79189 | 20.134 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99206 | 0.79326 | 19.88 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99428 | 0.78289 | 21.14 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.88508 | 10.688 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99378 | 0.91294 | 8.083 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96814 | 0.72742 | 24.072 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96814 | 0.74264 | 22.551 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96814 | 0.75514 | 21.3 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96814 | 0.76019 | 20.796 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96814 | 0.77674 | 19.14 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.96814 | 0.86792 | 10.022 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96814 | 0.87497 | 9.317 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99739 | 0.75671 | 24.068 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99652 | 0.90685 | 8.967 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98503 | 0.89374 | 9.129 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99311 | 0.91233 | 8.079 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99143 | 0.78448 | 20.695 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99143 | 0.90806 | 8.337 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.78492 | 20.702 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.90181 | 9.326 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99563 | 0.90586 | 8.978 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9957 | 0.90586 | 8.985 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99264 | 0.79425 | 19.839 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99624 | 0.91068 | 8.556 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98909 | 0.78703 | 20.206 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98909 | 0.89367 | 9.541 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.89955 | 9.362 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99612 | 0.90609 | 9.003 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99084 | 0.78536 | 20.548 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99084 | 0.90503 | 8.581 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98814 | 0.77517 | 21.297 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98814 | 0.78935 | 19.879 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99712 | 0.75645 | 24.067 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97512 | 0.72704 | 24.808 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97512 | 0.75479 | 22.033 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97512 | 0.76148 | 21.364 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97512 | 0.79141 | 18.371 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99048 | 0.86812 | 12.236 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9905 | 0.73972 | 25.078 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.90658 | 8.74 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.78089 | 21.605 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.995 | 0.91069 | 8.43 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99118 | 0.78894 | 20.223 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.75558 | 23.544 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99102 | 0.7561 | 23.492 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.7861 | 21.509 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0012 | 0.90429 | 9.69 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98539 | 0.77272 | 21.267 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98539 | 0.78587 | 19.952 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99687 | 0.91438 | 8.249 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.88142 | 11.441 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.90997 | 8.522 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98769 | 0.89942 | 8.827 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98769 | 0.89942 | 8.827 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99552 | 0.90461 | 9.091 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99481 | 0.9093 | 8.551 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99015 | 0.90695 | 8.32 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99015 | 0.90696 | 8.319 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99196 | 0.88508 | 10.688 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99482 | 0.89662 | 9.82 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.8972 | 9.758 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.91232 | 8.341 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99182 | 0.78129 | 21.053 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99182 | 0.8947 | 9.712 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99305 | 0.78646 | 20.659 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9951 | 0.90933 | 8.577 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9929 | 0.79136 | 20.154 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99492 | 0.88996 | 10.495 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.89844 | 9.571 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99544 | 0.91188 | 8.356 | Yes
Active | 2025W1-N11-WVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99272 | 0.79028 | 20.244 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-1_#6389_05DRESDN 138_1A_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.91357 | 8.241 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-1_#6390_05DRESDN 138_1B_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99598 | 0.91357 | 8.241 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-1_#6391_05DRESDN 138_1S_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99556 | 0.9042 | 9.136 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99317 | 0.89271 | 10.046 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99174 | 0.79159 | 20.015 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99493 | 0.91358 | 8.135 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#15953_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99296 | 0.90491 | 8.805 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.79087 | 20.153 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.79224 | 19.899 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.78188 | 21.158 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.88415 | 10.698 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17124_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99295 | 0.91204 | 8.09 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96729 | 0.72649 | 24.081 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96729 | 0.74168 | 22.561 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96729 | 0.75417 | 21.312 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96729 | 0.75921 | 20.808 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96729 | 0.77574 | 19.155 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6392_9217_SRT-A | 0.96729 | 0.87403 | 9.326 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99656 | 0.75574 | 24.083 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17561_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9957 | 0.90594 | 8.975 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#18090_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98419 | 0.89282 | 9.137 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99228 | 0.91142 | 8.086 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9906 | 0.78347 | 20.713 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9906 | 0.90715 | 8.345 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.78391 | 20.72 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#18339_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99424 | 0.9009 | 9.335 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#2748_18437_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9948 | 0.90495 | 8.986 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#2749_554_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99488 | 0.90495 | 8.993 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99181 | 0.79323 | 19.858 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6156_543_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99541 | 0.90977 | 8.564 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98825 | 0.78602 | 20.224 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98825 | 0.89275 | 9.55 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6457_16758_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99234 | 0.89863 | 9.371 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6497_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99529 | 0.90518 | 9.011 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99001 | 0.78434 | 20.567 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99001 | 0.90412 | 8.589 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9873 | 0.77417 | 21.313 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9873 | 0.78833 | 19.897 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99629 | 0.75547 | 24.082 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97428 | 0.7261 | 24.817 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97428 | 0.75382 | 22.046 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97428 | 0.7605 | 21.377 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97428 | 0.79039 | 18.388 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98965 | 0.86717 | 12.248 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.73877 | 25.09 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#721_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.90567 | 8.748 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.77988 | 21.623 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#728_584_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99417 | 0.90979 | 8.438 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99035 | 0.78793 | 20.242 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99019 | 0.75461 | 23.558 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99019 | 0.75512 | 23.507 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.78509 | 21.528 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.90338 | 9.699 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98456 | 0.77173 | 21.283 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98456 | 0.78485 | 19.97 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#770_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99604 | 0.91348 | 8.257 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.995 | 0.88049 | 11.452 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#8591_8311_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99437 | 0.90906 | 8.53 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-3_#17957_05KIBER 138_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.89851 | 8.835 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-3_#17958_05KIBER 138_2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.89851 | 8.835 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-3_#5063_05SBERWI 345_1_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99469 | 0.9037 | 9.099 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-3_#7429_05SORENS 765_3_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.90839 | 8.559 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-4_05CURLEY_CAP345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98932 | 0.90604 | 8.327 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-4_05CURLEYS 345_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98932 | 0.90605 | 8.327 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.88415 | 10.698 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99399 | 0.8957 | 9.829 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99395 | 0.89628 | 9.767 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9949 | 0.91141 | 8.349 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99099 | 0.78028 | 21.071 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99099 | 0.89378 | 9.721 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99222 | 0.78545 | 20.677 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.90842 | 8.585 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.79034 | 20.173 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99409 | 0.88904 | 10.505 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99333 | 0.89752 | 9.58 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99461 | 0.91097 | 8.364 | Yes
Active | 2025W1-N11-WVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99189 | 0.78926 | 20.263 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98982 | 0.82262 | 16.72 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98999 | 0.81677 | 17.322 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.82062 | 16.837 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99377 | 0.80523 | 18.854 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98684 | 0.89794 | 8.89 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97354 | 0.7632 | 21.034 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97354 | 0.77404 | 19.95 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97354 | 0.77792 | 19.563 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.97354 | 0.79222 | 18.133 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97354 | 0.79711 | 17.643 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.97354 | 0.80504 | 16.85 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.97354 | 0.8093 | 16.424 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7216_406223_SRT-A | 0.97354 | 0.88976 | 8.378 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99354 | 0.79474 | 19.88 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98717 | 0.80398 | 18.319 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98797 | 0.80479 | 18.318 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99 | 0.82339 | 16.661 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98676 | 0.81631 | 17.045 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98676 | 0.9067 | 8.005 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9877 | 0.8109 | 17.68 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98636 | 0.79932 | 18.704 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98636 | 0.8107 | 17.566 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99226 | 0.78841 | 20.385 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97799 | 0.76283 | 21.516 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.97799 | 0.77411 | 20.388 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.97799 | 0.79922 | 17.878 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.97799 | 0.80832 | 16.967 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98782 | 0.88677 | 10.106 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9846 | 0.77103 | 21.357 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.81426 | 17.909 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.81921 | 16.953 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98311 | 0.77498 | 20.812 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98311 | 0.77802 | 20.508 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.80974 | 18.381 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99355 | 0.91016 | 8.339 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98109 | 0.79264 | 18.845 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98109 | 0.80222 | 17.886 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99206 | 0.90017 | 9.189 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98684 | 0.89794 | 8.89 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99124 | 0.91043 | 8.081 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.91094 | 8.025 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.80186 | 18.784 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9897 | 0.90401 | 8.569 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98967 | 0.80719 | 18.248 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98968 | 0.81654 | 17.314 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9915 | 0.90421 | 8.729 | Yes
Active | 2025W1-N11-WVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98938 | 0.8149 | 17.448 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0023 | 0.91276 | 8.952 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0023 | 0.91498 | 8.73 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.92365 | 8.231 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0029 | 0.9068 | 9.609 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.91341 | 8.947 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.92147 | 8.19 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99916 | 0.91112 | 8.803 | Yes
Active | 2025W1-N11-WVD290946 | 290946 | 05CHATFLD_BP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99916 | 0.91503 | 8.412 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.92098 | 8.628 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.9203 | 8.719 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.91731 | 8.928 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91274 | 9.403 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99794 | 0.88609 | 11.185 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99794 | 0.88707 | 11.087 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99794 | 0.8914 | 10.654 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99794 | 0.90121 | 9.673 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99794 | 0.90351 | 9.443 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99794 | 0.90429 | 9.365 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99794 | 0.90913 | 8.881 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0085 | 0.91009 | 9.837 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.91496 | 9.146 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.91515 | 9.146 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.92059 | 8.626 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.91285 | 9.201 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99776 | 0.89843 | 9.934 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99776 | 0.90217 | 9.559 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.90166 | 10.468 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99771 | 0.88261 | 11.51 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99771 | 0.88651 | 11.12 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99771 | 0.91209 | 8.562 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99771 | 0.91323 | 8.449 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.89048 | 11.207 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.91523 | 9.338 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91953 | 8.726 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.88622 | 11.401 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.88889 | 11.133 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.90627 | 9.983 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.90698 | 9.539 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.91077 | 9.161 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.91205 | 9.387 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.91595 | 9.106 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.9186 | 8.825 | Yes
Active | 2025W1-N11-WVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.91851 | 8.826 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98649 | 0.84223 | 14.426 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98629 | 0.8406 | 14.569 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98545 | 0.84105 | 14.44 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98644 | 0.83462 | 15.182 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96596 | 0.77177 | 19.42 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96596 | 0.79285 | 17.312 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.96596 | 0.80717 | 15.879 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96596 | 0.82409 | 14.187 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.96596 | 0.82906 | 13.69 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96596 | 0.8294 | 13.656 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.96596 | 0.83293 | 13.303 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98935 | 0.80039 | 18.895 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98553 | 0.83727 | 14.826 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98585 | 0.83751 | 14.834 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98645 | 0.84228 | 14.417 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98348 | 0.83653 | 14.696 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98454 | 0.83588 | 14.866 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98203 | 0.82746 | 15.457 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98203 | 0.82977 | 15.225 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98996 | 0.80249 | 18.747 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96748 | 0.77139 | 19.609 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.96748 | 0.7811 | 18.638 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.96748 | 0.80605 | 16.143 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.96748 | 0.83213 | 13.535 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98068 | 0.88762 | 9.306 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97906 | 0.82096 | 15.809 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98918 | 0.84271 | 14.647 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98569 | 0.83969 | 14.6 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97551 | 0.78284 | 19.267 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97551 | 0.79388 | 18.163 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.83052 | 16.118 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9917 | 0.91005 | 8.165 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98044 | 0.82537 | 15.507 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98044 | 0.82685 | 15.359 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98839 | 0.90275 | 8.564 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98482 | 0.83359 | 15.122 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9865 | 0.83853 | 14.797 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98599 | 0.84001 | 14.598 | Yes
Active | 2025W1-N11-WVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98586 | 0.83926 | 14.66 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99671 | 0.87942 | 11.729 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99511 | 0.87307 | 12.204 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99495 | 0.87494 | 12.001 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0183 | 0.82752 | 19.08 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98386 | 0.83473 | 14.914 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98386 | 0.83656 | 14.73 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98386 | 0.8443 | 13.956 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98386 | 0.8534 | 13.046 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98386 | 0.85728 | 12.658 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98386 | 0.86178 | 12.208 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.98386 | 0.8656 | 11.826 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99911 | 0.86119 | 13.792 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99664 | 0.87946 | 11.719 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99442 | 0.87458 | 11.984 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99398 | 0.87119 | 12.279 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99131 | 0.86156 | 12.975 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99131 | 0.86743 | 12.388 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9976 | 0.85448 | 14.312 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98622 | 0.8294 | 15.682 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98622 | 0.83626 | 14.996 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.98622 | 0.85952 | 12.67 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.98622 | 0.86439 | 12.184 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.84232 | 14.825 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99915 | 0.87411 | 12.504 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.87719 | 11.883 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98318 | 0.83066 | 15.252 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98318 | 0.83545 | 14.773 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99585 | 0.86333 | 13.252 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98391 | 0.8501 | 13.381 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98391 | 0.85527 | 12.864 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.81313 | 18.761 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0007 | 0.91523 | 8.551 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99439 | 0.87198 | 12.241 | Yes
Active | 2025W1-N11-WVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99408 | 0.87099 | 12.308 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98098 | 0.85046 | 13.052 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98098 | 0.85708 | 12.391 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98098 | 0.87437 | 10.661 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.98098 | 0.87765 | 10.333 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99284 | 0.8769 | 11.594 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98762 | 0.88716 | 10.047 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9918 | 0.87274 | 11.906 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.98132 | 0.84047 | 14.085 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98132 | 0.85663 | 12.469 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98648 | 0.88108 | 10.54 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97313 | 0.84461 | 12.852 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97313 | 0.8539 | 11.923 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98834 | 0.87715 | 11.119 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98536 | 0.88494 | 10.042 | Yes
Active | 2025W1-N11-WVD291032 | 291032 | 09KTLRSVL | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98536 | 0.88508 | 10.028 | Yes
Active | 2025W1-N11-WVD313054 | 313054 | 6PLYMOUTH | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 1.0042 | 0.91623 | 8.795 | Yes
Active | 2025W1-N11-WVD314203 | 314203 | 6MACKEYS | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 1.0104 | 0.9168 | 9.359 | Yes
Active | 2025W1-N11-WVD314594 | 314594 | 6PLYMOUTH TP | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 1.0042 | 0.91624 | 8.795 | Yes
Active | 2025W1-N11-WVD314616 | 314616 | 6TRWBRDG | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 1.003 | 0.91613 | 8.688 | Yes
Active | 2025W1-N11-WVD314616 | 314616 | 6TRWBRDG | 230 | 345 | 8 | DVP_P1-2: LN 2126_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99351 | 0.91253 | 8.098 | Yes
Active | 2025W1-N11-WVD314616 | 314616 | 6TRWBRDG | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2126_SRT-A | 1.0026 | 0.91553 | 8.703 | Yes
Active | 2025W1-N11-WVD315725 | 315725 | AD1-074 MAIN | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 1.0048 | 0.91835 | 8.649 | Yes
Active | 2025W1-N11-WVD315725 | 315725 | AD1-074 MAIN | 230 | 345 | 8 | DVP_P1-2: LN 2126_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99575 | 0.91474 | 8.101 | Yes
Active | 2025W1-N11-WVD315725 | 315725 | AD1-074 MAIN | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2126_SRT-A | 1.0045 | 0.91774 | 8.673 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0104 | 0.92963 | 8.073 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0096 | 0.92678 | 8.279 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0097 | 0.92267 | 8.706 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0019 | 0.89733 | 10.457 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0019 | 0.8993 | 10.26 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0019 | 0.90306 | 9.883 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 1.0019 | 0.91322 | 8.867 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 1.0019 | 0.91447 | 8.742 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 1.0019 | 0.91459 | 8.73 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1.0019 | 0.91942 | 8.247 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0109 | 0.92058 | 9.029 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0094 | 0.92475 | 8.468 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0096 | 0.92492 | 8.468 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.008 | 0.92257 | 8.547 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0018 | 0.91056 | 9.129 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.91429 | 8.755 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0093 | 0.91276 | 9.653 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0016 | 0.89462 | 10.699 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.89872 | 10.289 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.006 | 0.90219 | 10.378 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0109 | 0.92491 | 8.6 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0098 | 0.92939 | 8.039 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0039 | 0.89818 | 10.568 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0039 | 0.90006 | 10.38 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0091 | 0.91635 | 9.276 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.91736 | 8.854 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0059 | 0.92122 | 8.469 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92205 | 8.694 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0099 | 0.92565 | 8.429 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0098 | 0.92809 | 8.171 | Yes
Active | 2025W1-N11-WVD927010 | 927010 | AC1-188 TAP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0097 | 0.92799 | 8.175 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.90925 | 9.435 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90873 | 9.466 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.90361 | 10.008 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99611 | 0.86876 | 12.735 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99611 | 0.87485 | 12.126 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99611 | 0.88004 | 11.607 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99611 | 0.88907 | 10.703 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99611 | 0.89947 | 9.664 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99611 | 0.89989 | 9.622 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99611 | 0.90082 | 9.529 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.004 | 0.89781 | 10.623 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90525 | 9.811 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90547 | 9.796 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.90157 | 10.119 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.90485 | 9.818 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.89767 | 10.482 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.90402 | 9.847 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.88684 | 11.674 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.8685 | 13.152 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1 | 0.87621 | 12.381 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 1 | 0.90027 | 9.974 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 1 | 0.90658 | 9.344 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.87341 | 12.899 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.9025 | 10.172 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.92145 | 8.124 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0025 | 0.87827 | 12.418 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.88095 | 12.15 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.89991 | 10.425 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.89735 | 10.501 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.90342 | 9.894 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.90292 | 10.045 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.90629 | 9.729 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.90878 | 9.477 | Yes
Active | 2025W1-N11-WVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0035 | 0.90826 | 9.527 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96744 | 0.80987 | 15.757 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96621 | 0.80683 | 15.938 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96614 | 0.80789 | 15.825 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96415 | 0.80495 | 15.92 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95147 | 0.76207 | 18.94 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.95147 | 0.76667 | 18.48 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.95147 | 0.77456 | 17.691 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.95147 | 0.78557 | 16.59 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.95147 | 0.794 | 15.747 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97113 | 0.78541 | 18.573 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96712 | 0.81164 | 15.548 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96745 | 0.81166 | 15.579 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96731 | 0.80951 | 15.78 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96442 | 0.80432 | 16.01 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 0.965 | 0.80309 | 16.191 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96149 | 0.79362 | 16.788 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96149 | 0.80047 | 16.102 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96957 | 0.7808 | 18.878 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9528 | 0.76037 | 19.243 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9528 | 0.76063 | 19.218 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.9528 | 0.78925 | 16.355 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.9528 | 0.79964 | 15.316 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96128 | 0.8572 | 10.408 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96023 | 0.77072 | 18.951 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97099 | 0.80389 | 16.71 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96651 | 0.80741 | 15.911 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9541 | 0.76178 | 19.232 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9541 | 0.76639 | 18.771 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96897 | 0.79497 | 17.4 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95689 | 0.78887 | 16.802 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.95689 | 0.79479 | 16.21 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95302 | 0.85267 | 10.036 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96242 | 0.80417 | 15.826 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9677 | 0.81219 | 15.551 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96552 | 0.80565 | 15.988 | Yes
Active | 2025W1-N11-WVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96528 | 0.80504 | 16.025 | Yes
Active | 2025W1-N11-WVD944230 | 944230 | AF1-091 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99739 | 0.89555 | 10.184 | Yes
Active | 2025W1-N11-WVD944530 | 944530 | AF1-118 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.98978 | 0.89248 | 9.73 | Yes
Active | 2025W1-N11-WVD946171 | 946171 | AF1-282 C | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.92362 | 8.13 | Yes
Active | 2025W1-N11-WVD946181 | 946181 | AF1-283 C | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.92363 | 8.13 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#1274_589-2_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.8492 | 15.59 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.84509 | 16.024 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#16619_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.84685 | 15.758 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.83399 | 17.326 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#16826_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.91987 | 8.305 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99014 | 0.79198 | 19.816 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99014 | 0.80182 | 18.832 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99014 | 0.80482 | 18.532 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#706_SRT-A | 0.99014 | 0.81949 | 17.065 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.99014 | 0.82196 | 16.818 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99014 | 0.82644 | 16.369 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7442_200545_SRT-A | 0.99014 | 0.83409 | 15.604 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17217_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0084 | 0.82504 | 18.34 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.8347 | 16.851 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.8353 | 16.848 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#2891_19577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.84957 | 15.559 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#6392_9217_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.8417 | 16.037 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0053 | 0.8498 | 15.555 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99796 | 0.81657 | 18.139 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99796 | 0.82663 | 17.133 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0065 | 0.81608 | 19.042 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99342 | 0.79154 | 20.188 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.99342 | 0.80007 | 19.334 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17217_SRT-A | 0.99342 | 0.82898 | 16.444 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.99342 | 0.83594 | 15.748 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0051 | 0.91168 | 9.339 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9998 | 0.7993 | 20.05 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#7216_406223_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0085 | 0.84123 | 16.724 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#730_590_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.84609 | 15.805 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99854 | 0.80174 | 19.679 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99854 | 0.80564 | 19.29 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0077 | 0.83487 | 17.28 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0077 | 0.92735 | 8.031 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99762 | 0.82237 | 17.524 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99762 | 0.83059 | 16.703 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#8424_577_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0075 | 0.92189 | 8.559 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-4_05ST.CLR_TSC138_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.91987 | 8.305 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.83164 | 17.275 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0044 | 0.92422 | 8.016 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | DAY_P1_34506_MADISON_BEATTY(AEP)_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.83723 | 16.778 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.84424 | 16.067 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | DAY_P1_34553_STUART_SPURLOCK (EKPC)_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0066 | 0.92455 | 8.21 | Yes
Active | 2025W1-N11-WVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0047 | 0.84313 | 16.157 | Yes
Active | 2025W1-N11-WVD960840 | 960840 | AF2-375 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0049 | 0.91564 | 8.926 | Yes
Active | 2025W1-N11-WVD960840 | 960840 | AF2-375 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0049 | 0.92061 | 8.429 | Yes
Active | 2025W1-N11-WVD960840 | 960840 | AF2-375 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 1.0052 | 0.90817 | 9.701 | Yes
Active | 2025W1-N11-WVD960840 | 960840 | AF2-375 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0052 | 0.91964 | 8.553 | Yes
Active | 2025W1-N11-WVD960840 | 960840 | AF2-375 TAP | 138 | 205 | 8 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99871 | 0.91321 | 8.55 | Yes

## Not Converged
PJM N-1-1 Not Converged Contingency (Winter 2030 Case)
FG # Status | FG# | Contingency 1 | Contingency 2 | Analysis Type | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2025W1-N11-WNC1 | AEP_P1-2_#734_8011_SRT-A | AEP_P1-2_#17216_SRT-A | N-1-1 Volt Drop | Yes
Active | 2025W1-N11-WNC2 | AEP_P1-2_#737_7791_SRT-A | AEP_P1-2_#17216_SRT-A | N-1-1 Volt Drop | Yes
Active | 2025W1-N11-WNC3 | AEP_P1-2_#1274_589_SRT-A | AEP_P1-2_#17216_SRT-A | N-1-1 Volt Drop | Yes
Active | 2025W1-N11-WNC4 | AEP_P1-2_#6463_16757_SRT-A | AEP_P1-2_#17216_SRT-A | N-1-1 Volt Drop | Yes
Active | 2025W1-N11-WNC5 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | N-1-1 Volt Mag | Yes

## Load Drop
PJM N-1-1 Load Drop Result (Summer 2030 Case)
FG # Status | FG# | Contingency 1 | Contingency 2 | MW Drop | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2025W1-N11-WLD1 | AP_P1-2_PE-138-035_SRT-A | AP_P1-2_PE-138-056_SRT-A | 333.87 | Yes
Active | 2025W1-N11-WLD2 | AP_P1-2_PE-138-056_SRT-A | AP_P1-2_PE-138-035_SRT-A | 333.87 | Yes
N/A | N/A | DVP_P1-2: LN 201_SRT-A | DVP_P1-2: LN 2311_SRT-A | 566.64 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 206_SRT-A | DVP_P1-2: LN 2178_SRT-A | 348.94 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2074_SRT-A | DVP_P1-2: LN 255_SRT-A | 382.88 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2088_SRT-A | DVP_P1-2: LN 255_SRT-A | 382.88 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2094_SRT-A | DVP_P1-2: LN 2227_SRT-A | 385.18 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2140_SRT-A | DVP_P1-2: LN 2251_SRT-A | 499.83 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2140_SRT-A | Base Case | 414.71 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2157_SRT-A | DVP_P1-2: LN 2297_SRT-A | 349.41 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2163_SRT-A | DVP_P1-2: LN 2246_SRT-A | 310.84 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2178_SRT-A | DVP_P1-2: LN 206_SRT-A | 348.94 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2199_SRT-A | DVP_P1-2: LN 9016_SRT-A | 375.12 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2199_SRT-A | DVP_P1-2: LN 2276_SRT-A | 332.77 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2202_SRT-A | DVP_P1-2: LN 255_SRT-A | 382.88 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2218_SRT-A | DVP_P1-2: LN 2292_SRT-A | 745.23 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2227_SRT-A | DVP_P1-2: LN 2094_SRT-A | 385.18 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2246_SRT-A | DVP_P1-2: LN 9450_SRT-A | 310.84 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2246_SRT-A | DVP_P1-2: LN 2163_SRT-A | 310.84 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2251_SRT-A | DVP_P1-2: LN 2140_SRT-A | 499.83 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2263_SRT-A | DVP_P1-2: LN 2311_SRT-A | 364.43 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2276_SRT-A | DVP_P1-2: LN 2199_SRT-A | 332.77 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2291_SRT-A | DVP_P1-3: 8WSHNGSTAR-TX#1_SRT-A | 525.7 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2292_SRT-A | DVP_P1-2: LN 2218_SRT-A | 745.23 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2292_SRT-A | DVP_P1-2: LN 9412_SRT-A | 504.82 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2297_SRT-A | DVP_P1-2: LN 2157_SRT-A | 349.41 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2298_SRT-A | DVP_P1-2: LN 255_SRT-A | 379.38 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2304_SRT-A | DVP_P1-2: LN 255_SRT-A | 362.46 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 201_SRT-A | 566.64 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 2263_SRT-A | 364.43 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 2331_SRT-A | DVP_P1-2: LN 9016_SRT-A | 339.99 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2202_SRT-A | 382.88 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2088_SRT-A | 382.88 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2074_SRT-A | 382.88 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2298_SRT-A | 379.38 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2304_SRT-A | 362.46 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 9016_SRT-A | DVP_P1-2: LN 2199_SRT-A | 375.12 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 9016_SRT-A | DVP_P1-2: LN 2331_SRT-A | 339.99 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 9412_SRT-A | DVP_P1-2: LN 2292_SRT-A | 504.83 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-2: LN 9450_SRT-A | DVP_P1-2: LN 2246_SRT-A | 310.84 | No | To be adressed through supplemental process.
N/A | N/A | DVP_P1-3: 8WSHNGSTAR-TX#1_SRT-A | DVP_P1-2: LN 2291_SRT-A | 525.7 | No | To be adressed through supplemental process.