## Winter GenDeliv
2032 RTEP PJM Generator Deliverability Result (Winter)
FG # Status | PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-W1 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 1144.7 | 1177.6 | 128.04 | 131.72 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-W2 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 1137.4 | 1164.2 | 127.23 | 130.22 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-W5 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 1005.8 | 1024.3 | 112.51 | 114.57 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-W6 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 1000.2 | 1012.7 | 111.88 | 113.27 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
N/A | Not soliciting proposals - transformer | N/A | 222103 | GRACETON | 220964 | GRACETON | 1 | 500/230 | 232 | 2168 | 2380.7 | 2391.6 | 109.81 | 110.31 | BGE_P4_GRACETON_52_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - due to offshore wind | N/A | 200051 | ROCKSPGS | 214348 | 05BRAMAH | 1 | 500 | 235/230 | 3558 | 3958.2 | 3858.5 | 111.25 | 108.45 | Base Case | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1263.4 | 1328.2 | 1344.5 | 105.13 | 106.42 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1263.4 | 1312 | 1328.1 | 103.85 | 105.12 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | Not soliciting proposals - terminal equipment limited | N/A | 200064 | PCHBTM1S | 214347 | PBN EXP | 2 | 500 | 230 | 3022 | 3183.9 | 3088.8 | 105.36 | 102.21 | BGE_P1-2_COOPER500_GRACETON_1_SRT-A | Single |  | No
N/A | Not soliciting proposals - transformer | N/A | 313440 | 8VINTHIL | 314125 | 6VINTHIL | 2 | 500/230 | 345 | 1440 | 1451.1 | 1467.3 | 100.77 | 101.9 | DVP_P4-2: H1T2114_SRT-A | Breaker |  | No
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-W3 | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1143 | 1147.9 | 1163.5 | 100.43 | 101.8 | PL_48_P42_000438_SRT-A | Breaker | 933/1079/998/1143 (SN/SE/WN/WE) | Yes
Active | Ensure to right size to the 2032 loading level | 2025W1-32GD-W4 | 208120 | SU10 | 208113 | SUSQ | 1 | 230 | 229 | 1143 | 1147.9 | 1163.5 | 100.43 | 101.8 | PL_48_P71_102649_SRT-A | Tower | 933/1079/998/1143 (SN/SE/WN/WE) | Yes
N/A | Not soliciting proposals - terminal equipment limited | N/A | 200064 | PCHBTM1S | 214347 | PBN EXP | 2 | 500 | 230 | 3022 | 3125.4 | 3026.8 | 103.42 | 100.16 | BGE_P4_GRACETON_57_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1344 | 1328.2 | 1344.4 | 98.83 | 100.03 | DVP_P4-2: H5T588_SRT-A | Breaker |  | No
N/A | Not soliciting proposals - transformer | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1344 | 1328.2 | 1344.4 | 98.83 | 100.03 | DVP_P4-2: H2T588_SRT-A | Breaker |  | No