## Winter GenDeliv
Note 1: Scenario 4 results are provided for reference at this time and also to provide guidance (for consideration part of robustness evaluations) covering the event that the NJ and DE OSW generation were delayed beyond 2032.
2032 Scenario 4 RTEP PJM Generator Deliverability Result (Winter)
FG # Status | PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1847.3 | 1863 | 133.96 | 135.1 | 765-L11216__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 1156.8 | 1191.9 | 129.4 | 133.32 | PL_48_P71_103285_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1823.8 | 1837.3 | 132.26 | 133.24 | 765-L11216__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 1149.5 | 1178.4 | 128.58 | 131.81 | PL_48_P71_103285_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1701.2 | 1715.5 | 123.37 | 124.4 | 765-L2315___-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1666.2 | 1681.9 | 120.83 | 121.96 | COMED_P4_023-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1667.4 | 1681.5 | 120.91 | 121.94 | COMED_P4_023-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1646.1 | 1658.4 | 119.37 | 120.26 | COMED_P4_023-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1645 | 1658.4 | 119.29 | 120.26 | COMED_P4_023-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4250 | 5004.5 | 97.72 | 115.07 | AEP_P1-2_#17216_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 1007.4 | 1027.9 | 112.69 | 114.98 | PL_48_P71_103319_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 1001.9 | 1016.2 | 112.07 | 113.67 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1510.6 | 1524.4 | 109.55 | 110.55 | COMED_P4_167-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1510.6 | 1524.4 | 109.54 | 110.55 | COMED_P4_167-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1487.5 | 1503.8 | 107.87 | 109.05 | COMED_P1-3_TR94_WILTO__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1465.5 | 1480.4 | 106.27 | 107.35 | COMED_P1-3_TR93_WILTO__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1263.4 | 1328.2 | 1344.3 | 105.13 | 106.41 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1451.9 | 1464.6 | 105.29 | 106.21 | COMED_P1-3_TR93_PLANO_B-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5973.9 | 6134.5 | 103.34 | 106.12 | AEP_P1-2_#709_546_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275207 | PLANO ;3M | 270630 | PLANO ; | 1 | 345/765 | 222 | 1379 | 1454.5 | 1459.5 | 105.48 | 105.84 | COMED_P1-3_TR92_COLLI_R-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1440.4 | 1453.1 | 104.46 | 105.37 | COMED_P4_112-45-BT6-7___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1263.4 | 1312 | 1327.9 | 103.85 | 105.11 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1429.3 | 1444 | 103.64 | 104.71 | COMED_P4_112-45-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3276 | 3390 | 3429.1 | 103.48 | 104.67 | AEP_P1-2_#7442_200545_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5276.5 | 5372.2 | 102.79 | 104.66 | AEP_P1-2_#701_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5276.5 | 5402.2 | 101.72 | 104.15 | AEP_P1-2_#701_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1143 | 1173.2 | 1190.2 | 102.64 | 104.13 | PL_48_P42_000438_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 1 | 230 | 229 | 1143 | 1173.2 | 1190.2 | 102.64 | 104.13 | PL_48_P71_102649_SRT-A | Tower | 933/1079/998/1143 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5221.3 | 5309.3 | 101.72 | 103.43 | EXT_P12:345:NIPS:34514:17BABCOCK:17STILLWELL:1_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5208.9 | 5290 | 101.48 | 103.06 | COMED_P1-2_345-L97008_R-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5221.3 | 5338.2 | 100.66 | 102.91 | EXT_P12:345:NIPS:34514:17BABCOCK:17STILLWELL:1_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5208.9 | 5320.3 | 100.42 | 102.57 | COMED_P1-2_345-L97008_R-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5564.3 | 5927.9 | 96.25 | 102.54 | AEP_P1-2_#707_8315_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5736.5 | 5910.8 | 99.23 | 102.25 | AEP_P1-2_#6463_16757_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 313440 | 8VINTHIL | 314125 | 6VINTHIL | 2 | 500/230 | 345 | 1440 | 1455.2 | 1471.5 | 101.05 | 102.19 | DVP_P4-2: H1T2114_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5152 | 5237.6 | 100.37 | 102.04 | AEP_P1-2_#698_1695_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5715.9 | 5881.9 | 98.87 | 101.75 | AEP_P1-2_#362_1680-2_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 1 | 500/138 | 201 | 578 | 576.1 | 587.1 | 99.67 | 101.57 | AP_P2-3_MP-500-017_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 2 | 500/138 | 201 | 578 | 576.1 | 587.1 | 99.67 | 101.57 | AP_P2-3_MP-500-016_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5152 | 5266.4 | 99.33 | 101.53 | AEP_P1-2_#698_1695_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5571.3 | 5842.3 | 96.37 | 101.06 | AEP_P1-2_#707_8315-2_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 4909 | 4838.5 | 4943.5 | 98.56 | 100.7 | Base Case | Single |  | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5090.9 | 5169 | 99.18 | 100.7 | COMED_P1-2_345-L6608__R-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4070.2 | 4152 | 4087.6 | 102.01 | 100.43 | DVP_P1-2: LN 511_SRT-W | Single |  | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5090.9 | 5197.5 | 98.15 | 100.2 | COMED_P1-2_345-L6608__R-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1344 | 1328.2 | 1344.3 | 98.83 | 100.02 | DVP_P4-2: H2T588_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1344 | 1328.2 | 1344.3 | 98.83 | 100.02 | DVP_P4-2: H5T588_SRT-A | Breaker |  | No