## N-1 Thermal
PJM N-1 Thermal Result (Winter 2030 Case)
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2025W1-N1-WT1 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 286 | 103.007 | 121.68 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N1-WT2 | 243469 | 05BEATTY | 241952 | 02DEERCREEK | 1 | 138/138 | 205/202 | 286 | 101.3986 | 116.59 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | ATSI: 292/330/324/358 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
Active | 2025W1-N1-WT3 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 113.4545 | 114.86 | Line_FB | 'AEP_P4_#7445_05MARYSV 765_B_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT4 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 112.4091 | 113.03 | Tower | '34506 34542_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT5 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 111.3182 | 111.85 | Single | 'ATSI_P1-2_OES-138-935TB_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT6 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 111.3182 | 111.85 | Line_FB | 'ATSI_P2-3_OES-138-024AT_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT7 | 208113 | SUSQ | 207972 | TOMH | 2 | 230/230 | 229/229 | 894 | 111.3535 | 111.85 | Tower | 'PL_48_P71_103285_SRT-A' | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
Active | 2025W1-N1-WT8 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 110.7273 | 110.92 | Single | 'DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT9 | 208113 | SUSQ | 207972 | TOMH | 1 | 230/230 | 229/229 | 894 | 110.5593 | 110.58 | Tower | 'PL_48_P71_103285_SRT-A' | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
Active | 2025W1-N1-WT10 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 109.1364 | 109.82 | Tower | 'ATSI_P7-1_OES-138-065T_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT11 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 109.4545 | 109.67 | Line_FB | 'DAY_GREENE_FB_GJ_I_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT12 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 108.7727 | 109.05 | Line_FB | 'DAY_GREENE_FB_GJ_H_SRT-A' | 163/200/201/220 | Yes
Removed | 2025-W1-N1-WT13 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 103.8095 | 105.87 | P2_1 | '246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
Removed | 2025-W1-N1-WT14 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 103.9683 | 105.84 | Single | 'AEP_P1-3_#11531_05GENOA 138_2_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
Removed | 2025-W1-N1-WT15 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 103.9683 | 105.84 | Line_FB | 'AEP_P4_#11531_05GENOA 69.0_64_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
Active | 2025W1-N1-WT16 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 103.0455 | 105.38 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT17 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 102.9545 | 105.04 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT18 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 102.8636 | 104.95 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 163/200/201/220 | Yes
Active | 2025-W1-N1-WT19 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138/138 | 201/201 | 343 | 97.8426 | 104.65 | Single | 'AP_P1-2_PE-138-035_SRT-A' | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025-W1-N1-WT20 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138/138 | 201/201 | 343 | 97.8426 | 104.64 | Line_FB | 'AP_P2-3_PE-138-041_SRT-A' | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025-W1-N1-WT21 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138/138 | 201/201 | 343 | 97.8426 | 104.64 | Bus | 'AP_P2-2_PE-138-009_SRT-A' | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025-W1-N1-WT22 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138/138 | 201/201 | 343 | 97.8426 | 104.44 | Line_FB | 'AP_P2-3_PE-138-043_SRT-A' | 308/376/349/445 | No | Substation Equipment Exclusion
Active | 2025W1-N1-WT23 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 96.383 | 102.54 | Single | 'AEP_P1-2_#5793_663_SRT-A' | 47/47/47/47 | Yes
Active | 2025W1-N1-WT24 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 96.383 | 102.54 | Line_FB | 'AEP_P4_#5793_05BEATTY 138_1E_SRT-A' | 47/47/47/47 | Yes
Active | 2025W1-N1-WT25 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 96.383 | 102.54 | Bus | 'AEP_P2-2_#5793_05MCCOMB 138_2_SRT-A' | 47/47/47/47 | Yes
Active | 2025W1-N1-WT26 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 102.1818 | 102.37 | Bus | 'ATSI_P2-2_OES-138-054_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT27 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 96.383 | 102.25 | P2_1 | '246663 05MCCOMB L 13.8 246662 05MCCMBEQ2 1.00 2_SRT-A' | 47/47/47/47 | Yes
Active | 2025W1-N1-WT28 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 96.5957 | 102.25 | P2_1 | '243540 05MCCOMB 138 246662 05MCCMBEQ2 1.00 2_SRT-A' | 47/47/47/47 | Yes
Active | 2025W1-N1-WT29 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 101.3636 | 100.76 | Single | 'AEP_P1-2_#7441_100545_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT30 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 101.5 | 100.72 | P2_1 | '290607 05SORENSN_RM 765 290608 05MARYSVL_RS 765 1_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT31 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 220 | 101.5 | 100.28 | P2_1 | '246999 05SORENS 765 290607 05SORENSN_RM 765 Z1_SRT-A' | 163/200/201/220 | Yes
Active | 2025W1-N1-WT32 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 286 | N/A | 100.28 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 200/242/226/286 | Yes

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Winter 2030 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
Active | 2025W1-N1-WVM1 | 208072 | SIEG | 230 | 229 | 0.91573 | 1.0111 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM2 | 207969 | TRES | 230 | 229 | 0.83805 | 1.0083 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM3 | 207967 | LOFT | 230 | 229 | 0.83309 | 1.0043 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM4 | 207966 | BWAY | 230 | 229 | 0.83663 | 1.0086 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM5 | 207963 | SLYK | 230 | 229 | 0.83683 | 1.0088 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM6 | 207960 | EPAL TR2 | 230 | 229 | 0.89082 | 1.014 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM7 | 207959 | EPAL TR1 | 230 | 229 | 0.89101 | 1.014 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVM8 | 241987 | AE2-217_POI | 138 | 202 | 0.76431 | 0.96828 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVM9 | 241952 | 02DEERCREEK | 138 | 202 | 0.89017 | 0.98156 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVM10 | 240710 | 02MELISSA | 138 | 202 | 0.73768 | 0.96433 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVM11 | 240709 | 02N TITUS | 138 | 202 | 0.73855 | 0.9644 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVM12 | 240706 | 02NATIONAL | 138 | 202 | 0.84003 | 0.97368 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVM13 | 238908 | 02LONDON | 138 | 202 | 0.80918 | 0.9713 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVM14 | 238703 | 02ESPRNG | 138 | 202 | 0.91331 | 0.97388 | 0.92 | Line_FB | ATSI_P2-3_OES-138-0208BT_SRT-A | Yes
Active | 2025W1-N1-WVM15 | 238703 | 02ESPRNG | 138 | 202 | 0.91364 | 0.97388 | 0.92 | Bus | ATSI_P2-2_OES-138-055T_SRT-A | Yes
Active | 2025W1-N1-WVM16 | 238703 | 02ESPRNG | 138 | 202 | 0.90322 | 0.97388 | 0.92 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Winter 2030 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | 2025W1-N1-WVD1 | 208072 | SIEG | 230 | 229 | 0.92259 | 1.0111 | 8.855 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD2 | 207969 | TRES | 230 | 229 | 0.84713 | 1.0083 | 16.121 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD3 | 207967 | LOFT | 230 | 229 | 0.84221 | 1.0043 | 16.206 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD4 | 207966 | BWAY | 230 | 229 | 0.84577 | 1.0086 | 16.283 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD5 | 207963 | SLYK | 230 | 229 | 0.84597 | 1.0088 | 16.28 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD6 | 207960 | EPAL TR2 | 230 | 229 | 0.89763 | 1.014 | 11.635 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD7 | 207959 | EPAL TR1 | 230 | 229 | 0.89781 | 1.014 | 11.616 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025-W1-N1-WVD8 | 247005 | 05MACOAL | 138 | 205 | 0.94257 | 1.0231 | 8.053 | P2_1 | 242855 05WYOMIN 138 247004 05GUYAND 138 1_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-N1-WVD9 | 247004 | 05GUYAND | 138 | 205 | 0.94257 | 1.0231 | 8.053 | P2_1 | 242855 05WYOMIN 138 247004 05GUYAND 138 1_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025W1-N1-WVD10 | 241987 | AE2-217_POI | 138 | 202 | 0.77332 | 0.96828 | 19.496 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVD11 | 240710 | 02MELISSA | 138 | 202 | 0.74653 | 0.96433 | 21.78 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVD12 | 240709 | 02N TITUS | 138 | 202 | 0.7474 | 0.96441 | 21.701 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVD13 | 240706 | 02NATIONAL | 138 | 202 | 0.84748 | 0.97369 | 12.621 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Active | 2025W1-N1-WVD14 | 238908 | 02LONDON | 138 | 202 | 0.81846 | 0.9713 | 15.284 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
Removed | 2025-W1-N1-WVD15 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.91835 | 1.0227 | 10.434 | Line_FB | DVP_P4-2: 2034T2126_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Removed | 2025-W1-N1-WVD16 | 314614 | 3TRWBRDG2 | 115 | 345 | 0.92088 | 1.0245 | 10.361 | Line_FB | DVP_P4-2: 2034T2126_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Removed | 2025-W1-N1-WVD17 | 314613 | 3TRWBRDG | 115 | 345 | 0.91891 | 1.0236 | 10.466 | Line_FB | DVP_P4-2: 2034T2126_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025W1-N1-WVD18 | 211951 | WEIS TP1 | 69 | 229 | 0.87472 | 0.98872 | 11.4 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD19 | 211950 | WEIS TP2 | 69 | 229 | 0.87083 | 0.98527 | 11.444 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD20 | 211949 | WEIS | 69 | 229 | 0.85921 | 0.97605 | 11.684 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD21 | 211697 | LEHI TP | 69 | 229 | 0.86096 | 0.97731 | 11.635 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD22 | 211696 | LEHI | 69 | 229 | 0.86028 | 0.97671 | 11.643 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD23 | 211611 | HIRU | 69 | 229 | 0.87405 | 0.98909 | 11.504 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD24 | 211446 | CHRI TP | 69 | 229 | 0.87606 | 0.99072 | 11.466 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD25 | 211427 | CARB | 69 | 229 | 0.87637 | 0.99077 | 11.44 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD26 | 211379 | BELT | 69 | 229 | 0.87689 | 0.9909 | 11.401 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD27 | 211377 | BELT 2 | 69 | 229 | 0.87083 | 0.98528 | 11.445 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD28 | 211376 | BELT 1 | 69 | 229 | 0.87688 | 0.9909 | 11.402 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD29 | 211366 | ASHF TP2 | 69 | 229 | 0.89978 | 0.98017 | 8.039 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD30 | 211347 | WHCE | 69 | 229 | 0.90429 | 0.98568 | 8.139 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD31 | 211346 | WHCE 2 | 69 | 229 | 0.9043 | 0.98568 | 8.138 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD32 | 211345 | WHCE 1 | 69 | 229 | 0.90446 | 0.98583 | 8.137 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD33 | 211337 | WGAT 2 | 69 | 229 | 0.87861 | 0.96383 | 8.522 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD34 | 211336 | WGAT 1 | 69 | 229 | 0.86386 | 0.95149 | 8.763 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD35 | 211273 | TREI DC | 69 | 229 | 0.90359 | 0.98361 | 8.002 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD36 | 211272 | TREI TP2 | 69 | 229 | 0.90465 | 0.9857 | 8.105 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD37 | 211270 | TREI | 69 | 229 | 0.90235 | 0.9825 | 8.015 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD38 | 211268 | TREI TP1 | 69 | 229 | 0.90359 | 0.98362 | 8.003 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD39 | 211193 | SSLA 2 | 69 | 229 | 0.90261 | 0.98337 | 8.076 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD40 | 211160 | SIEG | 69 | 229 | 0.90574 | 0.98693 | 8.119 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD41 | 211062 | PSPA TP2 | 69 | 229 | 0.89992 | 0.98032 | 8.04 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD42 | 211057 | PONO 1 | 69 | 229 | 0.86233 | 0.95018 | 8.785 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD43 | 211056 | PNWG TP2 | 69 | 229 | 0.88009 | 0.96513 | 8.504 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD44 | 211055 | PNWG TP1 | 69 | 229 | 0.86523 | 0.95266 | 8.743 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD45 | 211054 | PONO 2 | 69 | 229 | 0.87941 | 0.96456 | 8.515 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD46 | 211052 | APRF TP | 69 | 229 | 0.86238 | 0.95022 | 8.784 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD47 | 211051 | APRF | 69 | 229 | 0.862 | 0.94987 | 8.787 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD48 | 211031 | PAZI | 69 | 229 | 0.87459 | 0.98881 | 11.422 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD49 | 211030 | PAZI 2 | 69 | 229 | 0.87459 | 0.98882 | 11.423 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD50 | 211029 | PAZI 1 | 69 | 229 | 0.87325 | 0.98724 | 11.399 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD51 | 211022 | PALM 2 | 69 | 229 | 0.87625 | 0.99068 | 11.443 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD52 | 211021 | PALM 1 | 69 | 229 | 0.8734 | 0.98739 | 11.399 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD53 | 210972 | NBET 2 | 69 | 229 | 0.88274 | 0.96744 | 8.47 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD54 | 210971 | NBET 1 | 69 | 229 | 0.87056 | 0.95724 | 8.668 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD55 | 210914 | MICK TP2 | 69 | 229 | 0.90193 | 0.98366 | 8.173 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD56 | 210913 | MICK 2 | 69 | 229 | 0.90156 | 0.98334 | 8.178 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD57 | 210912 | MICK 1 | 69 | 229 | 0.90172 | 0.98349 | 8.177 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD58 | 210911 | MICK TP1 | 69 | 229 | 0.90209 | 0.98381 | 8.172 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD59 | 210829 | LIGA 1 | 69 | 229 | 0.86988 | 0.98439 | 11.451 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD60 | 210828 | LIGA 2 | 69 | 229 | 0.87077 | 0.98504 | 11.427 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD61 | 210827 | LIGA TAP | 69 | 229 | 0.87297 | 0.98697 | 11.4 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD62 | 210601 | EPAL | 69 | 229 | 0.87309 | 0.98706 | 11.397 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD63 | 210570 | DRAG 2 | 69 | 229 | 0.90458 | 0.98592 | 8.134 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD64 | 210569 | DRAG 1 | 69 | 229 | 0.90466 | 0.986 | 8.134 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD65 | 210568 | DRAG | 69 | 229 | 0.90466 | 0.986 | 8.134 | Tower | PL_60_P71_000890_SRT-A | Yes
Active | 2025W1-N1-WVD66 | 210405 | EPHA TI2 | 69 | 229 | 0.90172 | 0.98231 | 8.059 | Tower | PL_60_P71_000890_SRT-A | Yes

## N-1 Load Drop
PJM N-1 Load Drop Result (Winter 2030 Case)
FG # Status | FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
Active | N/A | DVP_P1-2: LN 2140_SRT-A | Single | 345 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P4-2: 214052_SRT-A | Line_FB | 345 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P4-2: 2094T2140_SRT-A | Line_FB | 345 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P4-2: 214042_SRT-A | Line_FB | 345 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P4-2: 221T222_SRT-A | Line_FB | 345 | 0 | 343.7 | 343.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P7-1: LN 2140-2176_SRT-A | Tower | 345 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P7-1: LN 9372-2140_SRT-W | Tower | 345 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.
Active | N/A | DVP_P7-1: LN 2140-535_SRT-A | Tower | 345, 201 | 0 | 414.7 | 414.7 | No | To be adressed through supplemental process.