8/05/2025

- TO Area update:

  - AEP:

    - AEP provided the rating updates for Beatty-BigPlain 345 kV line. Two idvs were added to the update folder: B3877_Beatty-BigPlain_sum_LL.idv; B3877_Beatty-BigPlain_win.IDV. No flowgate was removed due to the update.

    - AEP confirmed a rating update for Allen-East Lima 345 kV lines on 2032 winter case only. One idv was added to the update folder: Allen-East Lima Uprates (B3851.1_B3851.3) _2032_win_case_only.idv. No flowgate was removed.

- Scenario 4

  - PJM has added EHV conductor limits to the informational scenario 4 results.

    - 2032 Summer Scenario 4 GenDeliv Result_07-02-2025_with CL.xlsx

    - 2032 Winter Scenario 4 GenDeliv Result_07-02-2025_with CL.xlsx

    - 2032 Light Load Scenario 4 GenDeliv Result_07-02-2025_with CL.xlsx

7/28/2025

- TO Area update:

  - AEP:

    - AEP provided the rating updates for Madison – Chenoweth 345 kV line. Two idvs were added to the update folder: AF1-228_Correction_Winter.IDV; AF1-228_Correction_Summer_LL.idv. No flowgates were removed due to the update.

    - AEP provided rating updates for Tanners Creek-Miami Fort 345 kV line. Two idvs were added to the update folder: Tanners Creek - Miami Fort 345kV_Summer_LL.idv; Tanners Creek - Miami Fort 345kV_Winter.idv. The following flowgates were removed due to the update.

      - 2025-W1-GD-W197, 2025-W1-GD-W384, 2025-W1-GD-W385, 2025-W1-GD-W52, 2025-W1-GD-W207, 2025-W1-GD-W208, 2025-W1-GD-W69.

  - DOM:

    - After additional N-1-1 testing around Trowbridge, the violations have been removed:

      - 2025W1-N11-SVD315725, 2025W1-N11-SVD314616, 2025W1-N11-SVD314616, 2025W1-N11-SVD314594, 2025W1-N11-SVD314594, 2025W1-N11-SVD314203, 2025W1-N11-SVD314203, 2025W1-N11-SVD313054, 2025W1-N11-SVD313054

      - 2025W1-N11-WVM313054, 2025W1-N11-WVM313054, 2025W1-N11-WVM314203, 2025W1-N11-WVM314203, 2025W1-N11-WVM314594, 2025W1-N11-WVM314594, 2025W1-N11-WVM314616, 2025W1-N11-WVM314616, 2025W1-N11-WVM314616, 2025W1-N11-WVM314616, 2025W1-N11-WVM315725, 2025W1-N11-WVM315725, 2025W1-N11-WVM315725, 2025W1-N11-WVM315725

      - 2025W1-N11-WVD313054, 2025W1-N11-WVD314203, 2025W1-N11-WVD314594, 2025W1-N11-WVD314616, 2025W1-N11-WVD314616, 2025W1-N11-WVD314616, 2025W1-N11-WVD315725, 2025W1-N11-WVD315725,

      - 2025W1-N11-WVD315725

    - Single contingency updates for Trowbridge substation. Refer to the following file:

      - Trowbridge_Contingency_edits V2.xlsx

    - Refer to the file below for additional Dominion contingency updates:

      - DOM_Contingency_edits.xlsx

- SHORT CIRCUIT

  - Two areas of the 2030 short circuit base case posted to the 2025W1 window do not align with the posted 2030 PSSE case. These areas are the Tomhicken 230kV in PPL, and the Kraken 230kV in Dominion.

    - The Tomhicken 230kV switchyard (between Susquehanna and Harwood) can be added to the posted base case by applying the file “Tomhicken_Corr_FINAL.CHF”.  Once applied, there is no impact to the PPL breaker set, and there is no harm (over duty breakers).

    - The Kraken 230kV topology correction can be added by applying the file “Kraken_Area_Correction.CHF” and replacing the posted Dominion breaker set with “DOM_2030_R1_Corr.CHF”.  The Kraken 230kV topology correction is quite extensive and incorporates Supplemental solutions:

      - DOM-2023-0016

      - DOM-2024-0012

      - DOM-2023-0055

      - DOM-2023-0016,0053, 0055, 2024-0012-DNH

    - After applying the Kraken 230kV topology correction, 16 existing 230kV breakers become over duty. These will be handled through the Supplemental process. They are listed in 2030_Short Circuit_Results_Summary_2025W1_07-28-2025.xlsx

- Voltage Schedule Update

  - The following idevs, mainly to update the Interconnection Service Request generator scheduled voltage, have been posted in the “Model Updates” folder. There has been no material change in the posted results. No facilities were added and no facilities were removed. However, loadings on certain flowgates have changed, in most instances have decreased. (PJM confirmed that the voltage schedule impacts to the 2030 cases were negligible, therefore no change is needed for 2030 cases.)

    - voltage shedule update-2032 summer+redispatch.idv

    - voltage shedule update-2032 summer+redispatch scenario 4.idv

    - voltage shedule update-2032 winter.idv (same idv can be used for both 2032 base case and scenario 4)

    - voltage schedule update-2032 LL+redispatch.idv (same idv can be used for both 2032 base case and scenario 4)

7/21/2025

- TO Area update:

  - AEP:

    - AEP provided the impedance update and rating updates for St Johns - Olive 345 kV line involving AF2-359 tap. Three idvs were added to the update folder: Update AF2-359 POI - Summer LL Ratings.idv; Update AF2-359 POI - Winter Ratings.idv; and Update AF2-359 POI_impedance.idv. The loadings on Dumont-Stillwell 345 kV tie line (multiple flowgates) are updated.

    - AEP provided the rating idvs for Johnson Mountain-New London 138 kV line: JohnsonsMtn-NewLondon (SUM & LL).idv; JohnsonsMtn-NewLondon (WIN).idv. With the update, the following flowgates are removed:

      - 2025-W1-GD-S175 and 2025-W1-GD-S36 were removed.

    - AEP provided the rating idvs for 715 LL on a fixed shunt at AES’ Ft Recovery station: Turn off Ft Recovery cap bank_LL.idv. With the update, the following flowgates are removed:

      - 2025-W1-AEP-VM112, 2025-W1-AEP-VM113, 2025-W1-AEP-VM115, 2025-W1-AEP-VM116; 2025-W1-AEP-VD129 through VD139, 2025-W1-AEP-VD146 through 148, 2025-W1-AEP-VD151, 2025-W1-AEP-VD156, 2025-W1-AEP-VD163.

  - DOM:

    - DOM provided updated contingencies for Trowbridge substation along with an updated idv provided by PJM’s Interconnection Analysis group The corrections at Trowbridge can be found in the following files:

      - Trowbridge_Contingency_edits.xlsx

      - Trowbridge.idv

      - Trow_LockTap.idv

    - Updates were made to the fixed shunts in the 2030 & 2032 LL Cases. The corrections can be found in the following files:

      - DOM_CapBankAdjustments_LL_2030.idv

      - DOM_CapBankAdjustments_LL_2032_1.idv

      - DOM_CapBankAdjustments_LL_2032_2.idv

      - DOM_CapBankAdjustments_LL_2032_3.idv

      - DOM_CapBankAdjustments_LL_2032_4.idv

    - Removed an invalid Dominion bus contingency. Corrections can be found in the following files:

      - Dominion_Contingency_Edits_SUM_071125.xlsx

      - Dominion_Contingency_Edits_WIN_071125.xlsx

      - Dominion_Contingency_Edits_LL_071125.xlsx

    - The following flowgates have been removed:

      - 2025-W1-N1-SVD1, 2025-W1-N1-SVD2, 2025-W1-N1-SVD3, 2025-W1-N1-WVD15, 2025-W1-N1-WVD16, 2025-W1-N1-WVD17, 2025W1-N1-LLVM1NEW, 2025W1-N1-LLVM2NEW

      - PJM is evaluating impacts to N-1-1 results, which will be reflected in the next addendum.

  - First Energy:

    - Additional Line FB contingencies for Hunterstown 500 kV, Vinco 500 kV and Ringgold 230 kV.

      - Contingency Change_Hunterstown_Vinco & Ringgold line FB CON_SUM&LL.xlsx

      - Contingency Change_Hunterstown_Vinco & Ringgold line FB CON_WIN.xlsx

  - PPL:

    - Updates to Single, LineFB, and Tower Contingencies primarily impacting 715.

      - PPL 2025 FERC 715 Violation Contingency Changes.xlsx

    - The following flowgates have been removed:

      - 2025-W1-PPL-VD2, 2025-W1-PPL-VD16, 2025-W1-PPL-VD30, and 2025-W1-PPL-VD44

7/02/2025

- TO Area update:

  - APS:

    - The following two NEET contingency modification files include three Line FB CON updates for 2030 and two line FB CON updates for 2032 RTEP cases:

      - Contingency Change_NEET_06262025_2030_all_seasons.xlsx

      - Contingency Change_NEET_06262025_2032_all_seasons.xlsx

  - AEP:

    - Flowgate # 2025W1-GD-S210 is caused by the contribution from deactivated generators, therefore it is removed from competitive window.

    - AEP provided updated ratings for Genoa transformer, see Correct_Genoa_TR1_Ratings_SUM_LL.idv and Correct_Genoa_TR1_Ratings_WIN.idv. With the correction, the following flowgates will be removed:

      - 2025-W1-N1-ST9, 2025-W1-N1-ST10, and 2025-W1-N1-ST18 through ST22

      - 2025-W1-N1-WT13 through WT15

    - AEP provided updated ratings for Harrison – Zuber 138kV line, see Correct_Harrison-Zuber_138kV_Ratings_SUM_LL.idv and Correct_Harrison-Zuber_138kV_Ratings_WIN.idv. With the correction, the following flowgates will be removed:

      - 2025W1-GD-S460, 2025W1-GD-S176, 2025W1-GD-S179, and 2025W1-GD-S471

    - Per AEP, the failure of B1 at Marysville is correctly defined as the contingency “AEP_P4_#707_05MARYSV 765_B1_SRT-A”, thus the 2032 case contingency “AEP_P4_#707_05MARYSV 765_B1-2_SRT-A” will be removed. No flowgate removed.

    - AEP provided an update of the ratings for RP Mone-Maddox 345kV, see RP Mone-Maddox 345kV Winter Rating Update.idv. the following FG was removed:

      - 2025-W1-GD-W234

    - Per NextEra Energy initiated, AEP confirmed, a contingency regarding a 2nd transformer was added 'AEP_P1-3_#05VASSEL 765_2_SRT-A'. No flowgate added.

  - PEPCO / DOM

    - PEPCO provided updated conductor ratings on their end of the Tie Line from Possum – Burches Hill in the 2032 Case, the following flowgates will be removed:

      - 2025W1-32GD-S80, 2025W1-32GD-S102, and 2025W1-32GD-S116

    - DOM provided the following updates for both the 2030 & 2032 Cases that are applicable to all seasons: Updated impedance values for the Goose Creek Transformer #1, updated impedance values for the Bristers – Yeat & Yeat – Ox 500kV lines, updated ratings for the Yeat – Vint Hill 500kV line, updated impedance values for the Joshua Falls – Yeat 765kV line, updated contingencies for Kraken 230kV, and removal of a P-4 Contingency

      - DOM_Bristers_Yeat_Ox_ImpedanceCorrection.idv, DOM_Contingency Change Submission - Kraken 230kV_2030.xlsx, DOM_Contingency Change Submission - Kraken 230kV_2032.xlsx, DOM_GooseCreek_TX1_ ImpedanceCorrection_all_seasons.idv, DOM_Yeat-Vint Hill 500kV LL.idv, DOM_Yeat-Vint Hill 500kV SUM.idv, DOM_Yeat-Vint Hill 500kV WIN.idv, Dominion_Contingency_Edits_SUM_WIN_LL_062025.xlsx, Joshua Falls-Yeat-765kV line_Impedance Update_LL v2.idv, Joshua Falls-Yeat-765kV line_Impedance Update_SUM v2.idv, Joshua Falls-Yeat-765kV line_Impedance Update_WIN v2.idv

    - DOM provided the following updates for the 2032 Case: Updated ratings and impedance values for Carson – Rogers Road 500kV, Updated contingencies for only the SUM season

      - DOM_Carson-Rogers Road 500kV LL 2032.idv, DOM_Carson-Rogers Road 500kV SUM 2032.idv, DOM_Carson-Rogers Road 500kV WIN 2032.idv, Dominion_Contingency_Edits_SUM_2032_062425.xlsx

    - The following flowgates will be removed:

      - 2025W1-32GD-S88, 2025W1-32GD-S105, 2025W1-32GD-S118, 2025W1-32GD-S129, 2025W1-32GD-S142, 2025W1-32GD-S144, 2025W1-32GD-S155

    - The following flowgates have been added:

      - 2025W1-32GD-S1NEW, 2025W1-32GD-S2NEW, 2025W1-32GD-S3NEW, 2025W1-32GD-S4NEW, 2025W1-32GD-S5NEW, 2025W1-32GD-S6NEW, 2025W1-32GD-S7NEW, 2025W1-32GD-S8NEW, 2025W1-GD-LL1NEW, 2025W1-N1-LLVM1NEW, 2025W1-N1-LLVM2NEW

  - PSEG

    - PJM incorrectly labeled Hillsdale as N-1-1 Voltage Drop violations, these have been corrected and removed the following flowgate:

      - 2025W1-N11-SVD217013

    - PJM incorrectly labeled Prospect – North Pat 69kV Summer IPD violations as excluded for “Substation Equipment Exclusion”. This has been updated to be “Reliability Violations on Transmission Facilities Below 200 kV exclusion”

  - General:

    - A number of winter and light load seasonal specific contingencies were missing from the original 2032 line stuck breaker contingency files. These have been appended at the end of the file in a section called “6/30/2025 Additional contingencies”. The following flowgates have been added to the 2032 LL gen deliv results:

      - 2025W1-32GD-LL63 through 2025W1-32GD-LL76

    - The 2032 Winter P2-1 Contingency file was updated due to a Syntax error.

    - The 2030 IPD first layer contingency files are added.

    - All the changes mentioned in this document are applicable to 2032 Scenario 4 cases too.