## Light Load GenDeliv
Note 1: Scenario 4 results are provided for reference at this time and also to provide guidance (for consideration part of robustness evaluations) covering the event that the NJ and DE OSW generation were delayed beyond 2032.
2032 Scenario 4 RTEP PJM Generator Deliverability Result (Light Load)
FG # Status | PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 4215.1 | 4215.1 | 152.78 | 152.78 | DVP_P1-2: LN 563_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4767.1 | 5341 | 129.57 | 145.17 | DVP_P1-2: LN 557_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4788.9 | 5321.2 | 130.16 | 144.63 | DVP_P1-2: LN 567_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3956 | 3956 | 143.39 | 143.39 | DVP_P1-2: LN 576_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4772.7 | 5207.7 | 129.72 | 141.55 | DVP_P1-2: LN 574_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1127.6 | 1176 | 133.76 | 139.5 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1120.5 | 1162.7 | 132.91 | 137.92 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4500 | 5062.3 | 122.31 | 137.59 | DVP_P1-2: LN 567_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3506.3 | 3693.4 | 127.09 | 133.87 | DVP_P1-2: LN 582_2_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4539.5 | 4880.5 | 123.38 | 132.65 | DVP_P1-2: LN 574_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1200.4 | 1587.6 | 1587.6 | 132.26 | 132.26 | DVP_P1-2: LN 576_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1100.7 | 1453.7 | 1431.2 | 132.07 | 130.03 | DVP_P1-2: LN 567_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3357.6 | 3553.6 | 121.7 | 128.81 | DVP_P1-2: LN 2154_2_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2758.9 | 3353.4 | 3550.4 | 121.55 | 128.69 | DVP_P1-2: LN 2113_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4641.3 | 4641.3 | 126.15 | 126.15 | DVP_P1-2: LN 557_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 4302.5 | 4302.5 | 125.58 | 125.58 | DVP_P4-2: H6T563_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 4289.1 | 4289.1 | 125.19 | 125.19 | DVP_P4-2: 56372_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 5178.2 | 5779.6 | 111.89 | 124.88 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1009 | 1032.8 | 119.69 | 122.52 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 1100.7 | 1340.2 | 1345.7 | 121.75 | 122.26 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4226.8 | 4463.5 | 114.88 | 121.32 | DVP_P1-2: LN 298_2_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1003.3 | 1021.1 | 119.01 | 121.13 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3679.2 | 4214.7 | 4444.8 | 114.56 | 120.81 | DVP_P1-2: LN 298_3_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2771 | 3164.9 | 3342.8 | 114.21 | 120.63 | DVP_P2-2: SURRY B1_SRT-WL | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4073.2 | 4364 | 110.71 | 118.61 | DVP_P1-2: LN 2028_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3679.2 | 4044.4 | 4344.5 | 109.93 | 118.08 | AEP_P1-3_#1377_05J.FERR 765_1_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4599.4 | 5407.9 | 5407.9 | 117.58 | 117.58 | DVP_P1-2: LN 576_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1200.4 | 1401.1 | 1401.1 | 116.72 | 116.72 | DVP_P1-2: LN 563_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 2 | 230/500 | 345 | 1031.2 | 1148.4 | 1195.2 | 111.37 | 115.9 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 1 | 230/500 | 345 | 1038.7 | 1154.2 | 1201.2 | 111.12 | 115.64 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3956.2 | 3956.2 | 115.48 | 115.48 | DVP_P4-2: 57602_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3956.2 | 3956.2 | 115.48 | 115.48 | DVP_P4-2: WT576_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314923 | 8SEPTA | 314924 | 8SURRY | 1 | 500 | 345 | 2758.9 | 3134.9 | 3171.3 | 113.63 | 114.95 | DVP_P1-2: LN 531_SRT-L | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2909 | 3164.9 | 3342.7 | 108.8 | 114.91 | Base Case | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3672.8 | 3904.2 | 107.2 | 113.96 | DVP_P4-2: 2113T2154_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4789 | 5233 | 103.48 | 113.07 | DVP_P4-2: H2T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314923 | 8SEPTA | 314924 | 8SURRY | 1 | 500 | 345 | 2758.9 | 3046 | 3115.7 | 110.4 | 112.93 | DVP_P1-2: LN 563_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4776.8 | 5222.9 | 103.21 | 112.85 | DVP_P4-2: H1T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4599.4 | 4816.1 | 5133.2 | 104.71 | 111.61 | DVP_P1-2: LN 534_SRT-L | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1344 | 1487.9 | 1497.6 | 110.71 | 111.43 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1344 | 1487.9 | 1497.6 | 110.71 | 111.43 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 5129.2 | 5129.2 | 110.83 | 110.83 | DVP_P4-2: 557T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1055.9 | 1139 | 102.12 | 110.16 | PL_48_P42_100926_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314282 | 6CARSON | 2 | 500/230 | 345 | 1204 | 1309.4 | 1319.8 | 108.75 | 109.62 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4788.9 | 5321.1 | 98.64 | 109.6 | DVP_P4-2: 56702_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4500 | 5061.7 | 97.23 | 109.37 | DVP_P4-2: 56702_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1047.1 | 1130.4 | 101.27 | 109.32 | PL_48_P42_000438_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1047.1 | 1130.4 | 101.27 | 109.32 | PL_48_P71_102649_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1287 | 1426.5 | 1405.2 | 110.84 | 109.18 | DVP_P4-2: 56702_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1054.7 | 1128.4 | 102 | 109.13 | 208918 SUSQ 1 24.0_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1054.7 | 1128.4 | 102 | 109.13 | 208918 SUSQ 1 24.0_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1046.3 | 1126.6 | 101.19 | 108.95 | PL_48_P12_000189_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1046.3 | 1126.6 | 101.19 | 108.95 | PL_48_P11_000840_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1996.1 | 2177.2 | 99.81 | 108.86 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 2025.4 | 2174.1 | 101.27 | 108.71 | DVP_P4-2: H6T563_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1996.9 | 2166.2 | 99.84 | 108.31 | DVP_P1-2: LN 557_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1040.7 | 1119.7 | 100.65 | 108.28 | PL_40_P11_001449_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 2026.2 | 2164.2 | 101.31 | 108.21 | DVP_P4-2: H6T563_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 1035.4 | 1116.3 | 100.14 | 107.96 | PL_48_P41_102622_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1982 | 2151.1 | 99.1 | 107.56 | DVP_P1-2: LN 567_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1982.7 | 2140.8 | 99.14 | 107.04 | DVP_P1-2: LN 567_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208013 | SUMT2_B4 | 208090 | SUMT | 2 | 230 | 229 | 801 | 866 | 857.4 | 108.11 | 107.04 | PL_02_P42_001053_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3879 | 3939.1 | 4131.3 | 101.55 | 106.5 | Base Case | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4733 | 5161.1 | 97.49 | 106.3 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 2123.7 | 2123.7 | 106.18 | 106.18 | DVP_P1-2: LN 563_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 2122.9 | 2122.9 | 106.15 | 106.15 | DVP_P1-2: LN 563_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1998.1 | 2121.5 | 99.91 | 106.08 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4599.4 | 4867.7 | 4867.7 | 105.83 | 105.83 | DVP_P1-2: LN 563_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3386.4 | 3620.7 | 98.85 | 105.68 | DVP_P7-1: LN 211-228_SRT-L | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1998.9 | 2112.3 | 99.94 | 105.62 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3879 | 3836.3 | 4066 | 98.9 | 104.82 | Base Case | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3369.5 | 3576 | 98.35 | 104.38 | DVP_P7-1: LN 2024-2102_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 2086.5 | 2086.5 | 104.32 | 104.32 | DVP_P1-2: LN 576_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 2085.7 | 2085.7 | 104.29 | 104.29 | DVP_P1-2: LN 576_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3357.8 | 3563.8 | 98.01 | 104.02 | DVP_P7-1: LN 2197-2215_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3319.1 | 3553.5 | 96.88 | 103.72 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3353.3 | 3550.7 | 97.88 | 103.64 | DVP_P7-1: LN 177-2113_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3308.5 | 3550.2 | 96.57 | 103.63 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3342.9 | 3541.5 | 97.57 | 103.37 | DVP_P7-1: LN 2197-240_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 5012.9 | 5012.9 | 103.25 | 103.25 | DVP_P4-2: 557T574_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1287 | 1340.5 | 1328.1 | 104.16 | 103.19 | DVP_P4-2: G2T567_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4999.7 | 4999.7 | 102.98 | 102.98 | DVP_P4-2: 56722_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 4628 | 4762.4 | 4762.4 | 102.9 | 102.9 | DVP_P4-2: 56722_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4602.9 | 4981.4 | 94.81 | 102.6 | DVP_P4-2: G2T567_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1940.7 | 2041.7 | 97.04 | 102.08 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1940.7 | 2041.7 | 97.04 | 102.08 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1404.5 | 1404.2 | 101.85 | 101.83 | 765-L11216__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1941.5 | 2034.7 | 97.07 | 101.74 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1941.5 | 2034.7 | 97.07 | 101.74 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 4855 | 4570 | 4925.2 | 94.13 | 101.45 | DVP_P4-2: H1T574_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | No
N/A | See note 1 above | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 2000 | 1997.2 | 2029.1 | 99.86 | 101.45 | AEP_P1-2_#1375_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1254.9 | 1263.8 | 1268.1 | 100.71 | 101.06 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 2000 | 1997.9 | 2020.6 | 99.9 | 101.03 | AEP_P1-2_#1375_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1392.5 | 1391.8 | 100.98 | 100.93 | COMED_P4_023-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1392 | 1391.7 | 100.94 | 100.92 | COMED_P4_023-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 243206 | 05DUMONT | 290606 | 05DUMONT_RS | Z1 | 765 | 205 | 5001 | 4895.1 | 5045.7 | 97.88 | 100.89 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 3426 | 3245.9 | 3449 | 94.74 | 100.67 | DVP_P2-2: BASIN B7_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1246.4 | 1248.4 | 1252.7 | 100.15 | 100.5 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314923 | 8SEPTA | 314924 | 8SURRY | 1 | 500 | 345 | 2758.9 | 2709.5 | 2770.9 | 98.21 | 100.43 | DVP_P1-2: LN 576_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1384.6 | 1383.8 | 100.41 | 100.35 | 765-L11216__-S_SRT-A | Single |  | No