## Winter GenDeliv
Note 1: Scenario 4 results are provided for reference at this time and also to provide guidance (for consideration part of robustness evaluations) covering the event that the NJ and DE OSW generation were delayed beyond 2032.
2032 Scenario 4 RTEP PJM Generator Deliverability Result (Winter)
FG # Status | PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor Rating (MVA) | PJM Accepting Proposals
N/A | See note 1 above | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4250 | 5004.5 | 97.72 | 115.07 | AEP_P1-2_#17216_SRT-A | Single | 7781/7781/9842/9842 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5973.9 | 6134.5 | 103.34 | 106.12 | AEP_P1-2_#709_546_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5276.5 | 5372.2 | 102.79 | 104.66 | AEP_P1-2_#701_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5276.5 | 5402.2 | 101.72 | 104.15 | AEP_P1-2_#701_SRT-A | Single | 6249/6249/7897/7897 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5221.3 | 5309.3 | 101.72 | 103.43 | EXT_P12:345:NIPS:34514:17BABCOCK:17STILLWELL:1_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5208.9 | 5290 | 101.48 | 103.06 | COMED_P1-2_345-L97008_R-S_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5221.3 | 5338.2 | 100.66 | 102.91 | EXT_P12:345:NIPS:34514:17BABCOCK:17STILLWELL:1_SRT-A | Single | 6249/6249/7897/7897 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5208.9 | 5320.3 | 100.42 | 102.57 | COMED_P1-2_345-L97008_R-S_SRT-A | Single | 6249/6249/7897/7897 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5564.3 | 5927.9 | 96.25 | 102.54 | AEP_P1-2_#707_8315_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5736.5 | 5910.8 | 99.23 | 102.25 | AEP_P1-2_#6463_16757_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5152 | 5237.6 | 100.37 | 102.04 | AEP_P1-2_#698_1695_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5715.9 | 5881.9 | 98.87 | 101.75 | AEP_P1-2_#362_1680-2_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5152 | 5266.4 | 99.33 | 101.53 | AEP_P1-2_#698_1695_SRT-A | Single | 6249/6249/7897/7897 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5781 | 5571.3 | 5842.3 | 96.37 | 101.06 | AEP_P1-2_#707_8315-2_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 4909 | 4838.5 | 4943.5 | 98.56 | 100.7 | Base Case | Single | 6249/6249/7897/7897 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 290602 | 05DUMONT_RW | 243206 | 05DUMONT | Z1 | 765 | 205 | 5133 | 5090.9 | 5169 | 99.18 | 100.7 | COMED_P1-2_345-L6608__R-S_SRT-A | Single | within a station fence, so do not have conductor ratings | No
N/A | See note 1 above | N/A | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4070.2 | 4152 | 4087.6 | 102.01 | 100.43 | DVP_P1-2: LN 511_SRT-W | Single | 4295/4330/4996 : 4979/5022/5953 : 4849/4893/5804 | No
N/A | See note 1 above | N/A | 270644 | WILTON ; | 290602 | 05DUMONT_RW | 1 | 765 | 222/205 | 5187 | 5090.9 | 5197.5 | 98.15 | 100.2 | COMED_P1-2_345-L6608__R-S_SRT-A | Single | 6249/6249/7897/7897 MVA SN/SE/WN/WE | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1847.3 | 1863 | 133.96 | 135.1 | 765-L11216__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 1156.8 | 1191.9 | 129.4 | 133.32 | PL_48_P71_103285_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1823.8 | 1837.3 | 132.26 | 133.24 | 765-L11216__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 1149.5 | 1178.4 | 128.58 | 131.81 | PL_48_P71_103285_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1701.2 | 1715.5 | 123.37 | 124.4 | 765-L2315___-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1666.2 | 1681.9 | 120.83 | 121.96 | COMED_P4_023-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1667.4 | 1681.5 | 120.91 | 121.94 | COMED_P4_023-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1646.1 | 1658.4 | 119.37 | 120.26 | COMED_P4_023-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1645 | 1658.4 | 119.29 | 120.26 | COMED_P4_023-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 894 | 1007.4 | 1027.9 | 112.69 | 114.98 | PL_48_P71_103319_SRT-A | Tower |  | No
N/A | See note 1 above | N/A | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 894 | 1001.9 | 1016.2 | 112.07 | 113.67 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1510.6 | 1524.4 | 109.55 | 110.55 | COMED_P4_167-65-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1510.6 | 1524.4 | 109.54 | 110.55 | COMED_P4_167-65-BT4-5___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1487.5 | 1503.8 | 107.87 | 109.05 | COMED_P1-3_TR94_WILTO__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1465.5 | 1480.4 | 106.27 | 107.35 | COMED_P1-3_TR93_WILTO__-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1263.4 | 1328.2 | 1344.3 | 105.13 | 106.41 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275168 | COLLINS ;2M | 270607 | COLLINS ; | 1 | 345/765 | 222 | 1379 | 1451.9 | 1464.6 | 105.29 | 106.21 | COMED_P1-3_TR93_PLANO_B-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275207 | PLANO ;3M | 270630 | PLANO ; | 1 | 345/765 | 222 | 1379 | 1454.5 | 1459.5 | 105.48 | 105.84 | COMED_P1-3_TR92_COLLI_R-S_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275233 | WILTON ;4M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1440.4 | 1453.1 | 104.46 | 105.37 | COMED_P4_112-45-BT6-7___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1263.4 | 1312 | 1327.9 | 103.85 | 105.11 | DVP_P1-2: LN 588_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 275232 | WILTON ;3M | 270644 | WILTON ; | 1 | 345/765 | 222 | 1379 | 1429.3 | 1444 | 103.64 | 104.71 | COMED_P4_112-45-BT3-4___SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3276 | 3390 | 3429.1 | 103.48 | 104.67 | AEP_P1-2_#7442_200545_SRT-A | Single |  | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1143 | 1173.2 | 1190.2 | 102.64 | 104.13 | PL_48_P42_000438_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 208120 | SU10 | 208113 | SUSQ | 1 | 230 | 229 | 1143 | 1173.2 | 1190.2 | 102.64 | 104.13 | PL_48_P71_102649_SRT-A | Tower | 933/1079/998/1143 (SN/SE/WN/WE) | No
N/A | See note 1 above | N/A | 313440 | 8VINTHIL | 314125 | 6VINTHIL | 2 | 500/230 | 345 | 1440 | 1455.2 | 1471.5 | 101.05 | 102.19 | DVP_P4-2: H1T2114_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 1 | 500/138 | 201 | 578 | 576.1 | 587.1 | 99.67 | 101.57 | AP_P2-3_MP-500-017_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 2 | 500/138 | 201 | 578 | 576.1 | 587.1 | 99.67 | 101.57 | AP_P2-3_MP-500-016_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1344 | 1328.2 | 1344.3 | 98.83 | 100.02 | DVP_P4-2: H2T588_SRT-A | Breaker |  | No
N/A | See note 1 above | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1344 | 1328.2 | 1344.3 | 98.83 | 100.02 | DVP_P4-2: H5T588_SRT-A | Breaker |  | No