## Summary
2030 RTEP Short Circuit Result
FG # Status | Flowgate # | TO | BUS_NO | BUS | BREAKER | RATINGTYPE | Notes | DUTY_P | DUTY_A | BKR_CAPA | PJM Accepting Proposals | Reason for Exclusion | Comments
Active | 2025-W1-SC-1 | AEP | 243471 | 05BETHEL 138.kV | A | S | 40kA | 114.8 | 45919.7 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-2 | AEP | 243471 | 05BETHEL 138.kV | AA | S | 40kA | 116 | 46388.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-3 | AEP | 243471 | 05BETHEL 138.kV | D | S | 40kA | 116 | 46388.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-4 | AEP | 243471 | 05BETHEL 138.kV | E | S | 40kA | 116 | 46388.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-5 | AEP | 243471 | 05BETHEL 138.kV | F | S | 40kA | 116 | 46388.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-6 | AEP | 243471 | 05BETHEL 138.kV | TR 1 - XT1 | S | 40kA | 116 | 46388.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-7 | AEP | 243471 | 05BETHEL 138.kV | TR 2 - XT2 | S | 40kA | 116 | 46388.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-8 | AEP | 243524 | 05HESS NORTH 138.kV | 4 | S | 39kA | 106.3 | 41311.5 | 38877 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-9 | AEP | 243524 | 05HESS NORTH 138.kV | CS-XT1 | S | 40kA | 103.3 | 41311.5 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-10 | AEP | 243524 | 05HESS NORTH 138.kV | CS-XT3 | S | 40kA | 103.3 | 41311.5 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-11 | AEP | 245853 | 05HESS SOUTH 138.kV | CS-XT2 | S | 40kA | 103.2 | 41298.9 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-12 | AEP | 245853 | 05HESS SOUTH 138.kV | CS-XT4 | S | 40kA | 103.2 | 41298.9 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-13 | AEP | 243349 | 05NEW CARLI2 138.kV | TR-3 CS-XT3 | S | 40kA | 102.9 | 41142.9 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-14 | AEP | 243064 | 05NPROCT 138.kV | SWR XT3 | S | 40kA | 102.2 | 40892.3 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-15 | AEP | 243551 | 05OSU 138.kV | 102 | S | 40kA | 103.2 | 41264.3 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-16 | AEP | 243551 | 05OSU 138.kV | 103 | S | 40kA | 103.2 | 41264.3 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-17 | AEP | 243551 | 05OSU 138.kV | CS-XT4 | S | 40kA | 103.2 | 41264.3 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-18 | AEP | 243560 | 05ROBRT2 138.kV | CB-H014F2 | S | 45kA | 122.3 | 55037.3 | 45000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-19 | AEP | 243560 | 05ROBRT2 138.kV | CB-H014F5 | S | 45kA | 122.3 | 55037.3 | 45000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-20 | AEP | 243347 | 05TIDD 3-4 138.kV | CS-DD | S | 40kA | 109.7 | 43872 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025W1-SC-21 | DOM | 313742 | ALTAIR 230.kV | 20172-1 | S | 63kA | 100.6 | 63401 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-22 | DOM | 313742 | ALTAIR 230.kV | 20172-2 | S | 63kA | 100.6 | 63401 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-23 | DOM | 313742 | ALTAIR 230.kV | 226372-1 | S | 63kA | 100.6 | 63401 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-24 | DOM | 313742 | ALTAIR 230.kV | 226372-2 | S | 63kA | 100.6 | 63401 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-25 | DOM | 313859 | BELMONT 230.kV | 231112 | S | 63kA | 111.6 | 70333.9 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-26 | DOM | 313859 | BELMONT 230.kV | 2178T2286 | S | 63kA | 112.3 | 70723.6 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-27 | DOM | 313859 | BELMONT 230.kV | 2180T2286 | S | 63kA | 105.2 | 66255.8 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-28 | DOM | 313859 | BELMONT 230.kV | 2180T2311 | S | 63kA | 111.6 | 70333.9 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-29 | DOM | 314130 | BRISTERS 230.kV | H262 | S | 50kA | 107.1 | 53558.4 | 50000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-30 | DOM | 313827 | EVRGRN MILLS 230.kV | 217232 | S | 63kA | 103.1 | 64962.5 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-31 | DOM | 313827 | EVRGRN MILLS 230.kV | 218332 | S | 63kA | 105.9 | 66736.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-32 | DOM | 313827 | EVRGRN MILLS 230.kV | 221032 | S | 63kA | 102.6 | 64648.5 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-33 | DOM | 313827 | EVRGRN MILLS 230.kV | H2T2172 | S | 63kA | 103.1 | 64962.5 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-34 | DOM | 313827 | EVRGRN MILLS 230.kV | H332 | S | 63kA | 111.4 | 70202.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-35 | DOM | 313827 | EVRGRN MILLS 230.kV | H3T2183 | S | 63kA | 105.9 | 66736.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-36 | DOM | 313827 | EVRGRN MILLS 230.kV | H432 | S | 63kA | 111.4 | 70202.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-37 | DOM | 313827 | EVRGRN MILLS 230.kV | H4T2210 | S | 63kA | 102.6 | 64648.5 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-38 | DOM | 313907 | PRENTICE 230.kV | 218832 | S | 63kA | 102.8 | 64752.4 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-39 | DOM | 313907 | PRENTICE 230.kV | 229532 | S | 63kA | 102.8 | 64752.4 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-40 | DOM | 313907 | PRENTICE 230.kV | YT2295 | S | 63kA | 102.8 | 64752.4 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-41 | DOM | 313907 | PRENTICE 230.kV | ZT2188 | S | 63kA | 102.8 | 64752.4 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-42 | DOM | 313815 | SPRINGHILL 230.kV | W02 | S | 40kA | 107.1 | 42824 | 40000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-43 | DOM | 313815 | SPRINGHILL 230.kV | WT2010 | S | 40kA | 107.1 | 42824 | 40000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-44 | DOM | 313815 | SPRINGHILL 230.kV | Y02 | S | 40kA | 107.1 | 42824 | 40000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-45 | DOM | 313815 | SPRINGHILL 230.kV | YT2247 | S | 40kA | 107.1 | 42824 | 40000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-46 | DOM | 313751 | STRATUS 230.kV | 203152 | S | 63kA | 101.9 | 64224.9 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-47 | DOM | 313751 | STRATUS 230.kV | 218852 | S | 63kA | 101.9 | 64224.9 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-48 | DOM | 313751 | STRATUS 230.kV | 231052 | S | 63kA | 101.9 | 64224.9 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-49 | DOM | 313751 | STRATUS 230.kV | 231252 | S | 63kA | 101.9 | 64224.9 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-50 | DOM | 313751 | STRATUS 230.kV | 2031T2312 | S | 63kA | 101.3 | 63820.4 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-51 | DOM | 313751 | STRATUS 230.kV | 2188T2310 | S | 63kA | 101.4 | 63854.7 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-52 | DOM | 313396 | SYCOLIN 230.kV | 231652 | S | 63kA | 109.7 | 69127.2 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-53 | DOM | 313396 | SYCOLIN 230.kV | 231752 | S | 63kA | 109.7 | 69127.2 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-54 | DOM | 313396 | SYCOLIN 230.kV | 233452 | S | 63kA | 114.5 | 72121.7 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-55 | DOM | 313396 | SYCOLIN 230.kV | 233552 | S | 63kA | 114.5 | 72121.7 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-56 | DOM | 313396 | SYCOLIN 230.kV | 2316T2334 | S | 63kA | 114.5 | 72121.7 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-57 | DOM | 313396 | SYCOLIN 230.kV | 2317T2335 | S | 63kA | 114.5 | 72121.7 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-58 | DOM | 313395 | TRAPPE RK 230.kV | 226342-1 | S | 63kA | 104.2 | 65631.8 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-59 | DOM | 313395 | TRAPPE RK 230.kV | 226342-2 | S | 63kA | 104.2 | 65631.8 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-60 | DOM | 313395 | TRAPPE RK 230.kV | 231142-1 | S | 63kA | 104.2 | 65631.8 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-61 | DOM | 313395 | TRAPPE RK 230.kV | 231142-2 | S | 63kA | 104.2 | 65631.8 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-62 | DOM | 313911 | TWINCREEK 230.kV | 20312 | S | 63kA | 104.4 | 65769.8 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-63 | DOM | 313911 | TWINCREEK 230.kV | 231612 | S | 63kA | 118 | 74321.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-64 | DOM | 313911 | TWINCREEK 230.kV | 231712 | S | 63kA | 118 | 74321.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-65 | DOM | 313911 | TWINCREEK 230.kV | 203T2316 | S | 63kA | 118 | 74321.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Active | 2025W1-SC-66 | DOM | 313911 | TWINCREEK 230.kV | 2317T2320 | S | 63kA | 118 | 74321.3 | 63000 | Yes |  | Over duty violation attributed to 2024W1 solution
Removed | 2025W1-SC-67 | FE-APS | 235105 | DOUBS 500.kV | DL-57 | S | 40kA | 132.7 | 53071.1 | 40000 | Yes |  | Over duty violation attributed to 2024W1 solution
Removed | 2025W1-SC-68 | FE-APS | 235105 | DOUBS 500.kV | DL-58 | S | 40kA | 132.7 | 53071.1 | 40000 | Yes |  | Over duty violation attributed to 2024W1 solution
Removed | 2025W1-SC-69 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-1 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-70 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-2 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-71 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-3 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-72 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-4 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-73 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-5 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-74 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-7 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-75 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-8 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Removed | 2025W1-SC-76 | FE-APS | 235106 | FORT MARTIN 500.kV | FL-9 | S | 50kA | 98 | 49016.7 | 50000 | Yes |  | OD due to X/R multiplier FE reports 100.1% duty
Active | 2025-W1-SC-77 | FE-APS | 235505 | RINGGOLD 138.kV | 138 BUS TIE | T | 20.7kA | 91.5 | 18907.8 | 20675.4 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 105.5% duty
Active | 2025-W1-SC-78 | FE-APS | 235299 | BELMONT 138.kV | B-8 | S | 63kA | 85.5 | 48188.9 | 56385 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 101.8% duty
Active | 2025-W1-SC-79 | FE-ATSI | 241928 | AVON 1241928 138.kV | 4-B-107 | S | 40kA | 130.1 | 52049.4 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Removed | 2025-W1-SC-80 | FE-ATSI | 241929 | AVON 1241929 138.kV | 24-B-107 | S | 37.4kA | 142.7 | 53359.9 | 37386.7 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-81 | FE-ATSI | 241930 | AVON 1241930 138.kV | 4-B-84 | S | 40kA | 126 | 50403.8 | 40000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-82 | FE-ATSI | 241921 | EASTLK 138#1 138.kV | 46-B-18 | S | 63kA | 90.9 | 57263 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 100.5% duty
Active | 2025-W1-SC-83 | FE-ATSI | 241921 | EASTLK 138#1 138.kV | 46-B-21 | S | 63kA | 92.4 | 58228.3 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 101.5% duty
Active | 2025-W1-SC-84 | FE-ATSI | 241921 | EASTLK 138#1 138.kV | 46-B-24 | S | 63kA | 92.4 | 58228.3 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 101.5% duty
Active | 2025-W1-SC-85 | FE-ATSI | 241921 | EASTLK 138#1 138.kV | 46-B-35 | S | 63kA | 92.4 | 58228.3 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 100.1% duty
Active | 2025-W1-SC-86 | FE-ATSI | 241922 | EASTLK 138#2 138.kV | 46-B-36 | S | 63kA | 92.1 | 58005 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 100.0% duty
Active | 2025-W1-SC-87 | FE-ATSI | 241923 | EASTLK 138#3 138.kV | 46-B-32 | S | 63kA | 102.4 | 57889 | 56530.5 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-88 | FE-ATSI | 241924 | EASTLK 138#4 138.kV | 46-B-33 | S | 63kA | 92.7 | 58372.5 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 101.1% duty
Active | 2025-W1-SC-89 | FE-ATSI | 241925 | EASTLK 138#5 138.kV | 46-B-27 | S | 63kA | 89.6 | 56440.9 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 101.5% duty
Active | 2025-W1-SC-90 | FE-ATSI | 238685 | EASTLK138SYN 138.kV | 46-B(795) | S | 63kA | 97 | 61103.3 | 63000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion | OD due to X/R multiplier FE reports 101.4% duty
Active | 2025-W1-SC-91 | FE-ATSI | 238685 | EASTLK138SYN 138.kV | 46-B-45 | S | 63kA | 108.1 | 61103.3 | 56517.3 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-92 | FE-ATSI | 238685 | EASTLK138SYN 138.kV | 46-B-54 | S | 63kA | 108.1 | 61103.3 | 56517.3 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-93 | FE-ATSI | 238685 | EASTLK138SYN 138.kV | 46-B-97 | S | 63kA | 108.1 | 61103.3 | 56517.3 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-94 | FE-ATSI | 238813 | HOYTDL N 138 138.kV | 83-B-14 | S | 37.4kA | 105 | 39241.1 | 37386.7 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-95 | FE-ATSI | 238813 | HOYTDL N 138 138.kV | 83-B-18 | S | 37.4kA | 105 | 39241.1 | 37386.7 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-96 | FE-ATSI | 438813 | HOYTDL S 138 138.kV | 83-B-22 | S | 37.4kA | 103.4 | 38672 | 37386.7 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-97 | FE-ATSI | 238844 | JOHNSON 69 71.17kV | 451-B-163 | S | 31.5kA | 103.1 | 32479.6 | 31500 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | 2025-W1-SC-98 | FE-GPU | 200579 | WARREN 1 115 115.kV | NO.1 XFMR | S | 20kA | 110.1 | 22022.1 | 20000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Removed | 2025-W1-SC-99 | FE-GPU | 200579 | WARREN 1 115 115.kV | CORRY EAST | S | 20kA | 105.8 | 21162 | 20000 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Removed | 2025-W1-SC-100 | FE-GPU | 200716 | PHILIPSB 115 115.kV | WESTFALL | T | 7.3kA | 104.1 | 7606.9 | 7309.3 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
Active | N/A | DOM | 313484 | KRAKEN 230.kV | T313484 | S | 50kA | 149.7 | 74827.2 | 50000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314137 | FREDERICKSBU 230.kV | 215742 | S | 40kA | 121.3 | 48531.2 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314137 | FREDERICKSBU 230.kV | H842 | S | 40kA | 121.3 | 48531.2 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314137 | FREDERICKSBU 230.kV | XT2157 | S | 40kA | 121.3 | 48531.2 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314137 | FREDERICKSBU 230.kV | 208342 | S | 40kA | 118.5 | 47394.1 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314137 | FREDERICKSBU 230.kV | 209042 | S | 40kA | 115.5 | 46188.9 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314197 | LADYSMITH S1 230.kV | 208972-1 | S | 40kA | 115.3 | 46132.3 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314197 | LADYSMITH S1 230.kV | 208972-2 | S | 40kA | 115.3 | 46132.3 | 40000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314196 | LADYSMITH 1 230.kV | L1T2089 | S | 50kA | 110.2 | 55120.7 | 50000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | H892 | S | 63kA | 102.5 | 64588.8 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | H8T2216 | S | 63kA | 102.5 | 64588.8 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | H992 | S | 63kA | 102.5 | 64588.8 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | H9T237 | S | 63kA | 102.5 | 64588.8 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | G6BTGT | S | 63kA | 100.9 | 63571.6 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | GT92 | S | 63kA | 100.9 | 63571.6 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | 25292 | S | 63kA | 100 | 63005.2 | 63000 | No | To be addressed through supplemental process.
Active | N/A | DOM | 314074 | POSSUM POINT 230.kV | 252T2022 | S | 63kA | 100 | 63005.2 | 63000 | No | To be addressed through supplemental process.