# PJM RTEP - 2025 RTEP Proposal Window #1

PROBLEM STATEMENT & REQUIREMENTS

## Document Scope: Violations in 2030 Summer/Winter/Light Load reliability analysis; 2030 TO FERC 715 Analysis; 2030 Short Circuit Analysis; 2032 Summer/Winter/Light Load Generator Deliverability analysis (For 2032: PJM is providing all 500kV and above flowgates, plus flowgates for which PJM is soliciting solutions).

# 2025 RTEP Proposal Window #1

### Purpose of Proposal Window

PJM seeks technical solutions, also called proposals, to resolve potential reliability criteria violations on facilities identified below in accordance with all applicable planning criteria (PJM, NERC, SERC, RFC, and Local Transmission Owner criteria).

#### Criterion Applied by PJM for this Proposal Window

- 2030 Summer Baseline Thermal and Voltage N-1 Contingency Analysis

- 2030 Summer Generator Deliverability/IPD Analysis

- 2030 Summer N-1-1 Thermal and Voltage Analysis

- 2030 Winter Baseline Thermal and Voltage N-1 Contingency Analysis

- 2030 Winter Generator Deliverability/IPD Analysis

- 2030 Winter N-1-1 Thermal and Voltage Analysis

- 2030 Light Load Baseline Thermal and Voltage N-1 Contingency Analysis

- 2030 Light Load Generator Deliverability/IPD Analysis

- 2030 Winter/Summer Load Deliverability Analysis

- 2030 Short Circuit Analysis

- AEP FERC Form 715

- AMPT FERC Form 715

- ComEd FERC Form 715

- DEOK FERC Form 715

- DOM FERC Form 715

- FE FERC Form 715

- PPL FERC Form 715

- PSEG FERC Form 715

- ODEC FERC Form 715

- 2032 Summer Generator Deliverability

- 2032 Winter Generator Deliverability

- 2032 Light Load Generator Deliverability

### Terminology for Proposal Windows

Through the analyses listed above, PJM has compiled a list of criteria violations. The violations and the impacted facilities are identified by a table of flowgates. Descriptions of the column headings are provided below. Different analyses often use different column headings.

#### Typical thermal analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| FG # | Flowgate Number | A sequential numbering of the identified potential violations |
| Fr Bus | From Bus Number | PSSE model bus number corresponding to one end of line identified as a potential violation |
| Fr Name | From Bus Name | PSSE model bus name corresponding to one end of line identified as a potential violation |
| To Bus | To Bus Number | PSSE model bus number corresponding to other end of line identified as a potential violation |
| To Name | To Bus Name | PSSE model bus name corresponding to other end of line identified as a potential violation |
| Monitored Facility | Monitored Facility | The circuit on which a potential violation is occurring |
| Base Rate (MVA) | Base Rate (MVA) | Normal Facility Rating (Rate A) |
| % Overload | Percentage Overload | Percentage above corresponding Facility Rating |
| CKT | Circuit ID | Circuit number of identified potential violation |
| KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer |
| Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line |
| Rating | Facility Rating | Applicable thermal rating (MVA) of facility |
| DC Ld(%) | Direct Current Loading percentage | Percentage above Facility Rating determined from DC testing |
| AC Ld(%) | Alternating Current Loading percentage | Percentage above Facility Rating determined from AC testing |
| Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower) |
| Cont Name | Contingency Name | Contingency name as identified in associated contingency file or embedded in the spreadsheet |
| Contingency | Contingency | Contingency description |
| Violation Date | Violation Date | Date on which violation is expected to occur |
| Analysis Case | Analysis Case | Case title to use in replicating analysis |

#### Typical voltage analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| FG # | Flowgate Number | A sequential numbering of the identified potential violations |
| Bus # | Bus Number | PSSE model bus number corresponding to bus identified as a potential violation |
| KVs | Kilovolt level | Kilovolt level of bus identified as potential violation |
| Area | Area Number | Area number of bus identified as potential violation |
| ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied |
| BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied |
| Low Limit | Low Voltage Limit(P.U.) | Threshold of Per Unit Low voltage, if ContVolt is under this limit, a potential violation is identified |
| Upper Limit | High Voltage Limit(P.U.) | Threshold of Per Unit High voltage, if ContVolt is over this limit, a potential violation is identified |
| Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower) |
| Vdrop (%) | Voltage drop | The percentage that the voltage has dropped as a result of the contingency |
| Contingency | Contingency | Contingency name as identified in associated contingency file |
| Contingency 1 | First Contingency | N-1 (first) contingency identified |
| Contingency 2 | Second Contingency | N-1-1 (second) contingency identified in N-1-1 analysis |

#### Typical short circuit analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| Flowgate # | Flowgate Number | A sequential numbering of the identified potential violations |
| TO | Transmission Owner | Transmission Owner company name |
| BUS_NO | Bus Number | ASPEN model bus number corresponding to bus identified as the location of an over duty breaker |
| BUS | Bus Name | ASPEN model bus name corresponding to bus identified as the location of an over duty breaker |
| BREAKER | Breaker ID | Breaker ID of the identified over duty breaker |
| RATINGTYPE | Rating Type | Short circuit current calculation methodology. Either 'S' for Symmetrical Current or 'T' for Total Current |
| Notes | Notes | Breaker Interrupting Rating Class (kA or MVA) |
| DUTY_P | Duty Percent | The percentage of worst case interrupting duty (amps) to the breaker's interrupting capability (amps) |
| DUTY_A | Duty Amps | The worst case interrupting duty (amps) |
| BKR_CAPA | Breaker Capability Amps | The breaker's interrupting capability rating (amps) |

### Proposal Window Exclusion Definitions

The following definitions explain the basis for excluding flowgates from the competitive planning process and designating projects to the incumbent Transmission Owner.

Flowgates excluded from competition will include the underlined language in the comment field.

- Immediate Need Exclusion: For immediate reliability needs that must be addressed within three years or less and for which PJM determines a proposal window may not be feasible, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer to Operating Agreement, Schedule 6 § 1.5.8(m)(1)

- Below 200kV Exclusion: Due to the lower voltage level of the identified violations, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer to Operating Agreement, Schedule 6 § 1.5.8(n)

- Substation Equipment Exclusion: For thermal reliability violations on existing transmission substation equipment, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer Operating Agreement, Schedule 6 § 1.5.8(p)

- Supplemental Projects scope: These cover violations to be addressed through supplemental solutions, including addressing load loss criteria and issues related to the distribution of future planning load that is included part of the forecast (load mapping issues to local transmission networks)

### Analysis Procedure

Participants are expected to develop solutions to the identified criteria violations and perform analysis to validate that the solutions remove these violations in compliance with the PJM planning manuals and criteria listed in PJM Manual 14B. The competitive planning process is documented in PJM Manual 14F.

Proposed solutions must also meet Transmission Owner Planning Criteria.

Although PJM does its best to provide complete and accurate results, changes to the list of violations under consideration are possible. Flowgates may be added or removed from consideration in the proposal window as part of future updates. PJM is planning to post one additional Scenario before end of June 2025 and with that, PJM plans to address any corrections and minor adjustments to the 2030 and 2032 baseline scenarios to be posted as part of the window opening.  PJM works with PJM Transmission Owners, Generation Owners, neighboring ISOs and Transmission Owners and other affected parties to verify the quality of the analysis. PJM endeavors to minimize such changes and will clearly communicate any changes to the participants.

PJM regularly updates the system model to reflect changes to the transmission system. Analyses are performed to verify that violations continue to be valid, no new violations have appeared, and proposed solutions still address the targeted violation(s).

PJM will determine the more efficient or cost-effective enhancements or expansions for any violation.

### Scope of Work

PJM is seeking proposals to resolve identified reliability criteria violations as demonstrated in the 2030 RTEP model suite. The 2032 RTEP models suite will be primarily utilized to right-size needs already showing up in 2030 and for consideration of longer-term needs (requiring 7 or more years to develop, i.e., 500kV and above developments). The posted 2032 results are for reference only unless it is indicated that PJM is soliciting proposals for the associated flowgate(s).

#### OBJECTIVES:

- Develop complete solutions to address the identified criteria violations;

- Develop solutions to address all new criteria violations generated as a consequence of proposed solution. Solutions to these secondary violations are required for the proposal to be considered.

- Adhere to all applicable planning criteria, including PJM, NERC, SERC, RFC and Local Transmission Owner Criteria.

- Solutions proposed to address the 2030 RTEP model suite needs should be considered in view of the evolving needs demonstrated in the 2032 RTEP model suite and beyond given the trend currently demonstrated through the PJM 2025 Load Forecast (right sizing, scalable or incremental upgrade options).

#### REQUIREMENTS:

- Holistic solutions are to be designed such that they are robust and expandable as the load grows within the areas and as the resource mix continues to evolve. A robust solution ensures, at a minimum, near-term reliability needs are addressed while also allowing for efficient and prudent consideration of future and evolving needs. The proposing entities are encouraged to outline their rationale, benefits and general merits of their proposed developments as part of their submissions.

#### ASSUMPTIONS:

- PJM doesn’t currently see major regional transfer issues in the 2030 analysis. In the 2032 analysis, there are several clusters showing EHV backbone overloads primarily along the extremities of the upgraded bulk, backbone transmission network that was reinforced as part of the PJM 2022 RTEP W3 and 2024 RTEP W1 competitive transmission windows. The following provides a brief rationale on whether a specific cluster is considered or not as part of the 2025 RTEP W1 window:

  - ComEd/AEP 765KV transfer path: Wilton Center – Dumont – Sorenson – Marysville

    - Not considered in the window

    - The majority of this path is terminal equipment limited. For the Sorenson - Marysville line overload, the contingency, which causes the thermal violations is a line with stuck breaker contingency, which can be potentially addressed by local substation upgrade measures in the longer term (7 year horizon).

  - AG1-125 – Marysville 765KV line

    - Not considered in the window

    - The line is terminal equipment limited.

  - AEP Columbus area, there are two major backbone (765/345 kV) EHV sources that currently serve the load pocket. Multiple thermal overloads are showing in the area. In 
N-1-1 test, various contingency pairs cause the wide-spread local system voltage issues which are expected to worsen with forecasted load increase through 2032 and beyond. All the related thermal and voltage issues in 2030 are posted and open to competition. Solutions need to consider the longer term needs to ensure efficient and cost effective mitigation.

  - MAAC 500 kV system:

    - In 2032, multiple 500 kV facilities are overloaded due to terminal equipment constraints. However, the violations can be mitigated without long lead-time solutions.

    - Due to offshore wind, the Rock Springs–Bramah 500 kV line exceeds its conductor rating. Proper action will depend on the results of the sensitivity scenario (excluding OSW in 2032) that PJM will be posting by end of June of 2025.

  - ATSI 138 & 115 kV area (2030 RTEP): East Springfield – Melissa – London path

    - PJM is experiencing load growth in Central Ohio, part of ATSI territory causing multiple thermal and voltage violations under various contingencies. These violations spread through several reliability analyses affecting neighboring TOs such as AEP and Dayton. PJM anticipates a holistic proposal to address the need, preferably an EHV solution.

    - PJM is seeking proposals to address these violations holistically and for the longer-term.

  - ATSI 345 kV overloads (2032 RTEP): North to South & West to East

    - PJM has been experiencing increased loadings on the 345 kV backbone in the northern Ohio ATSI territory. As part of the 2024 RTEP W1, PJM selected a 138 kV rebuild solution for several facilities. PJM performed sensitivity analysis by upgrading the 138 kV lines to 345 kV and conducted additional studies incorporating both the 345 kV upgrade and the 2024 RTEP W1 138 kV selected solution and determined that the overloads remain, even if the line is upgraded to 345 kV.

    - The 2032 Summer RTEP shows additional flow from north to south (Lallendorf, Lemoyne and into Foster (AEP)) and west to east (Bayshore, Davis Besse and Beaver). These flows are more regional transfer-based and do not conflict with the rebuild of the existing 138 kV scope assigned by PJM in 2024 RTEP W1.

    - PJM is not currently seeking proposals to resolve the EHV violations but will continue to monitor the area closely moving forward.

  - Dominion / PJM South:

    - PJM will be addressing the 2032 needs to reinforce the southern 500 kV backbone. This 500kV corridor includes multiple North-South 500kV elements.

    - Violations associated with and/or impacted by CVOW (Coastal Virginia Offshore Wind) will be deferred until the network upgrades associated with the project are finalized.

    - 230kV Lines Chesterfield – Basin & Chesterfield – Hopewell will be addressed as part of the 2030 set of violations.

  - PPL Zone:

    - Several 230kV facilities overloaded in PPL zone in 2030, and these issues worsened in the 2032 analysis.

    - Additional overloads are identified in 2032 as the load continue to grow.

    - PJM expects that solutions proposed for the PPL area will address both the 2032 violations and account for potential future load growth (and resource mix evolution) in the region.

#### Load Deliverability analysis:

Summer Load Deliverability:

PJM conducted Load deliverability analysis on the 2025 RTEP W1 2030 scenarios. The majority of the LDAs showed a healthy CETL/CETO margin above 100%. However, with the limited amount of Generation reserves in the 2030 base cases, there is not enough capacity to serve the resource adequacy needs of these larger LDAs under stressed conditions:

- PJM West: There are not enough resources/generators to create the CETO case (no sufficient reserves in the model) – The LDA will meet the CETL/CETO ratio of 100% or higher with sufficient resources outside of PJM West.

- AEP and Dominion: Due to a generation deficiency in developing the CETO cases, the forced outage rates of generators outside the LDA(s) are assumed to be zero. The LDA will meet the CETL/CETO ratio of 100% or higher with sufficient resources outside of AEP and Dominion.

- MAAC:  Reliability violation identified (CTEL/CETO <100%), if the forced outage rate rule is respected during generation optimization. The LDA will meet the CTEL/CETO ratio with sufficient resources external to the regional MAAC LDA.

Winter Load Deliverability:

The winter load deliverability analysis is in progress and PJM will provide the updated result by the end of June. However, PJM doesn’t expect any reliability issues.

#### WHAT PJM PROVIDES:

The information listed below is provided to allow replication of PJM’s analyses. Some of this data is designated Critical Energy Infrastructure Information (CEII) and must be handled consistent with PJM’s CEII request process at Competitive Planning Process page on the PJM website:

- Power Flow Base Cases: Identifies one or more system configurations to which planning criteria are applied.

- Contingency List: Lists all contingency types (single, bus, tower, line w/ stuck breaker).

- Subsystem Files: Identifies all subsystem zones to be considered in analysis.

- Monitor Files: Identify specific ranges of facilities by area and kV level to be considered in analysis.

- Facility Ratings: (if different from those included in the base cases)

- Violations List: Lists all criteria violations with power flow results and additional technical notes (flowgates). The results indicate the case(s) to which the criteria violations apply.

- Short Circuit Base Case. This case reflects the 2030 RTEP base case.

- Breaker Change Files. Lists all over-duty breakers in a specific TO area.

- TO Criteria Setting Files. Lists settings used for short circuit analysis for each specific TO.

- TARA Generation Deliverability options files.

- Generator Data files used in Generation Deliverability tests

### Response Back To PJM (Deliverables)

This section describes the required elements of a complete proposal. The absence of any element renders the proposal incomplete and the proposal will not be considered for selection.

Often there are several viable solutions to a given violation. Include alternate approaches in separate proposals. PJM will not accept proposals with multiple options.

Four categories of information are described below: three are required for a complete package and one is conditional.

- Technical analysis files and documentation

- Completed proposal submittal template

- Project diagrams

- Company evaluation and operations and maintenance information (if required)

#### Technical Analysis Files and Documentation

Include the following technical information to provide a complete project proposal package:

- A detailed analysis spreadsheet showing the planning analysis results for the project.

- A set of updates to the power flow cases which model the proposed solution. Provide files in a format compatible with PSS/E version 35.3. Provide only solvable and convergent solutions. Include an idv, or equivalent type, file in order to apply changes to other models. Assign a unique identifier when new busses are required. Provide contingencies in a single file for each contingency type. Organize the contingencies into one of three categories:

  - Modified Contingencies

  - New Contingencies

  - Deleted Contingencies

- List of all proposed equipment along with relevant parameters and assumptions.

  - All necessary parameters, e.g., equipment ratings, impedances, line lengths, etc.

  - For reactive devices, settings and outputs

  - For synchronous machines, MW and MVAR output assumptions

- An analysis report of proposed solution which identifies the issues being addressed.

- Additional documentation required to verify the proposal.

### PJM Proposal Submittal

The PJM Competitive Planner Tool is used for proposal(s) submittal and captures project details, such as the criteria violations or system constraints that are being targeted by the proposed solution, the overall and specific project descriptions and the details of cost commitment, if included. The Competitive Planner Tool and user guide are available on the Competitive Planning Process page.

All proposals will be made public and posted on pjm.com after the proposal window is closed. Mark all CEII and business proprietary and confidential information for redaction from this public posting. Redact only information which meets the criteria of CEII or business proprietary and confidential information.

Redaction guidelines can be found in PJM Manual 14F, Section 6.2. Please note that this section provides guidance only. PJM reserves the right to challenge proposed redaction of information in order to ensure the appropriate level of transparency.

#### Project Diagrams

Provide project diagrams in the PJM Competitive Planner Tool to detail how the proposed solution will modify existing infrastructure, how new infrastructure will be configured and where new infrastructure will be sited. Project diagrams should include, but are not limited to, the following detail:

- Single line diagrams

- Substation general arrangement and station layout. If expanding the substation, identify the following:

  - Area to be modified

  - Land ownership or acquisition plan

- Line routing diagram:

  - Identify proposed route of new or upgraded transmission lines

  - Clearly identify where  acquisition of additional right-of-way is required

- Detailed project schedule. Include, at minimum, the following major work activities:

  - Engineering and Design

  - Siting and Permitting

  - ROW and Land acquisition

  - Material procurement

  - Construction

  - Testing/Commissioning

Project Capital Expenditure, Cost Containment Information and Cost Escalation

In accordance with PJM Manual 14F, Section 8.4, PJM will initiate the comparative cost framework to evaluate the costs of project proposals that are submitted through PJM’s competitive proposal window process, with the final comparative cost framework being performed once project proposals are found to pass an engineering screen. The comparative cost framework is a multi-step process that calculates project costs and permits the comparison of costs among projects addressing the same violation(s) or constraint(s) (competing projects) submitted through the proposal window.

A cost commitment provision submitted as part of a project proposal may include, but is not limited to, the capital structure (debt to equity ratio) and caps on: initial capital costs (total costs associated with bringing the project into service); the annual revenue requirement; the rate of return on equity (ROE); the debt cost; the total capital cost; allowance for funds used during construction (AFUDC); construction work in progress (CWIP); abandonment costs and schedule guarantees. A cost commitment proposal may also exclude defined cost elements from the cost commitment provision.

Within the Competitive Planner application, there is a Project Financial Information section that includes a financial form through which projected capital expenditures for the project should be provided. This form must be completed and submitted with each proposal submittal.

In addition, following the close of this Window, PJM may request additional details via email regarding the capital structure of submitted projects, and the cost containment provisions proposed in order to perform the comparative cost assessment of the competing proposals.

For the purpose of the escalation calculations in this Proposal Window, PJM recommends the use of a 2.1% escalation factor to ensure consistency in escalation calculations for all submitted proposals.

#### Company Evaluation and Operations and Maintenance Information

For proposers seeking Designated Entity status, provide additional information which will aid PJM in understanding how the proposed solution will be developed, constructed, operated and maintained. Include this information in the PJM Competitive Planner Tool.

Relevant PJM Operating Agreement language in Schedule 6, Section 1.5.8(f):

(f) Entity-Specific Criteria Considered in Determining the Designated Entity for a Project.  In determining whether the entity proposing a Short-term Project, Long-lead Project or Economic-based Enhancement or Expansion recommended for inclusion in the plan shall be the Designated Entity, the Office of the Interconnection shall consider:  (i) whether in its proposal, the entity indicated its intent to be the Designated Entity; (ii) whether the entity is pre-qualified to be a Designated Entity pursuant to Operating Agreement, Schedule 6, section 1.5.8(a); (iii) information provided either in the proposing entity’s submission  pursuant to the Operating Agreement, Schedule 6, section 1.5.8(a) or 1.5.8(c)(2) relative to the specific proposed project that demonstrates:  (1) the technical and engineering experience of the entity or its affiliate, partner, or parent company, including its previous record regarding construction, maintenance, and operation of transmission facilities relative to the project proposed; (2) ability of the entity or its affiliate, partner, or parent company to construct, maintain, and operate transmission facilities, as proposed, (3) capability of the entity to adhere to standardized construction, maintenance, and operating practices, including the capability for emergency response and restoration of damaged equipment; (4) experience of the entity in acquiring rights of way; (5) evidence of the ability of the entity, its affiliate, partner, or parent company to secure a financial commitment from an approved financial institution(s) agreeing to finance the construction, operation, and maintenance of the project, if it is accepted into the recommended plan; and (iv) any other factors that may be relevant to the proposed project, including but not limited to whether the proposal includes the entity’s previously designated project(s) included in the plan.

#### Transmittal of Proposals

Proposal submissions along with all files required for submission will be done with the PJM Competitive Planner Tool for each submitted proposal.

### Proposal Fees

All proposals, upgrades and greenfield solutions, with the exception of solutions submitted with an estimated cost of $5M or less, submitted for consideration in the 2025 RTEP Proposal Window 1 are subject to an initial $5,000 deposit per the PJM Operating Agreement, Schedule 6, Section 1.5.8(c).

Relevant PJM Operating Agreement language in Schedule 6, Section 1.5.8(c):

(c)(1)	All proposals submitted in the proposal windows must contain:  (i) the name and address of the proposing entity; (ii) a statement whether the entity intends to be the Designated Entity for the proposed project; (iii) the location of proposed project, including source and sink, if applicable; (iv) relevant engineering studies, and other relevant information as described in the PJM Manuals pertaining to the proposed project; (v) a proposed initial construction schedule including projected dates on which needed permits are required to be obtained in order to meet the required in-service date; (vi) cost estimates and analyses that provide sufficient detail for the Office of Interconnection to review and analyze the proposed cost of the project; and (vii) with the exception of project proposals submitted with cost estimates of $5 million or less, a $5,000 non-refundable deposit must be included with each project proposal submitted by a proposing entity that indicates an intention to be the Designated Entity.

(c)(1)(i)  In addition, any proposing entity indicating its intention to be the Designated Entity will be responsible for and must pay all actual costs incurred by the Transmission Provider to evaluate the submitted project proposal.  To the extent the Transmission Provider incurs costs to evaluate multiple submitted project proposals where such costs are not severable by individual project proposal, the Transmission Provider shall invoice equal shares of the non-severable costs among the project proposals that cause such non-severable costs to be incurred.  Notwithstanding this method of invoicing non-severable costs, non-severable costs will be jointly and severally owed by the proposing entities that cause such costs to be incurred.

(c)(1)(ii)  All non-refundable deposits will be credited towards the actual costs incurred by the Transmission Provider as a result of the evaluation of a submitted project proposal.

(c)(1)(iii)  Following the close of a proposal window but before the Transmission Provider incurs any third-party consultant work costs to evaluate a submitted project proposal, the Transmission Provider will issue to the proposing entity an initial invoice seeking payment of estimated costs to evaluate each submitted project proposal.  The estimated costs will be determined by considering the:  potential cost of consultant work, historical estimates for project proposals of similar scope, complexity and nature of the need, and/or technology and nature of the project proposal. The Transmission Provider may issue additional invoices to the proposing entity prior to the completion of the evaluation activities associated with a project proposal if the Transmission Provider receives updated actual cost information and/or upon consideration of the factors specified in this section.

(c)(1)(iv) At the completion of the evaluation activities associated with a project proposal, the Transmission Provider will reconcile the actual costs with monies paid and, to the extent necessary, issue either a final invoice or refund.

(c)(1)(v)  The proposing party must pay any invoiced costs within fifteen (15) calendar days of the Transmission Provider sending the invoice to the proposing entity or its agent.  For good cause shown, this fifteen (15) calendar day time period may be extended by the Transmission Provider.  If the proposing entity fails to pay any invoice within the time period specified and/or extended by the Transmission Provider in accordance with this section, the proposing entity’s pre-qualification status may be suspended and the proposing entity will be ineligible to be a Designated Entity for any projects that do not yet have an executed Designated Entity Agreement.  Such a suspension and/or ineligibility will remain in place until the proposing entity pays in full all outstanding monies owed to the Transmission Provider as a result of the evaluation of the proposing entity’s project proposal(s).

The non-refundable deposit is due at the time of submission. Pay the non-refundable deposit by wire transfer to PJM Interconnection at:

| Wire transfer funds to: | PJM Interconnection, LLC |
| --- | --- |
| Bank Name: | PNC Bank, N.A. New Jersey |
| ABA Number: | 031207607 (Fed Wire and ACH) |
| Account Number: | 80-1358-9826 |
| Provide Reference (see Note below) | Order 1000 |

Note: To ensure the non-refundable deposit is properly accounted for, include a reference to “Order 1000 – Competitive submittal PJM Proposal ID #” in the subject, notes or addenda field of the wire transfer form.  Please note that the PJM Proposal ID # will be displayed on the confirmation email you receive after submitting the proposal and is also identified on the Competitive Planner Tool once a competitive proposal is initially saved.

The proposer also needs to provide the following information to PJM:

Company Info, Primary contact name, Billing email & Tax ID#.

The PJM Proposal ID# can also be located on the Existing Proposal screen in the PJM Competitive Planner Tool as shown in the screenshot below.

### Timeline

6/18/2025: Opening of 2025 RTEP Proposal Window 1

8/18/2025: Close of 2025 RTEP Proposal Window 1 at 5:00 p.m. Eastern Daylight Time

Notes:

- Confidentiality of individual proposals will be maintained for the duration of the window.

- Proposals received after close of the proposal window will not be accepted.

### Questions

Submit all questions about the proposal window to the PJM Planning Community. Submit questions involving confidential information or CEII under the “Confidential” topic on the Planning Community.

Answers will be provided to all participants in the proposal window.

Please reference 2025 RTEP Proposal Window 1 in all correspondence.

### Specialized Requirements

PJM seeks proposals to evaluate the identified needs in this window.  PJM has not determined specialized requirements that PJM is seeking in project proposals in this window for consideration in its evaluation.

Notice

In accordance with the PJM Open Access Transmission Tariff, Attachment M, the Market Monitoring Unit (MMU) has access to all data submitted to PJM through PJM’s competitive proposal window process.  See PJM Manual 14F, Section 8.4.4.

### Document Revision History

6/18/2025 - V1 -	Original Problem Statement posted to the PJM Competitive Planning Process webpage: