## N-1 Thermal
PJM N-1 Thermal Result (Light Load 2030 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025W1-N1-LLT1 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 126.7769 | 148.03 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT2 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 722.86 | 128.9323 | 130.9149 | Single | 'DVP_P1-2: LN 217_SRT-L' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT3 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 722.86 | 128.3513 | 129.617 | Single | 'DVP_P1-2: LN 563_SRT-A' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT4 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 126.0728 | 128.46 | Line_FB | 'DVP_P4-2: 205T217_SRT-A' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT5 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 123.7191 | 124.87 | Line_FB | 'DVP_P4-2: 562T563_SRT-L' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT6 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 115.2838 | 124.37 | Line_FB | 'ATSI_P2-3_OES-138-065_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT7 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 115.2838 | 124.37 | Line_FB | 'ATSI_P2-3_OES-138-065B_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT8 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 121.1964 | 123.06 | Line_FB | 'DVP_P4-2: 21712_SRT-L' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT9 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 121.1053 | 122.96 | Line_FB | 'DVP_P4-2: H8T217_SRT-L' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT10 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 115.2838 | 122.01 | Single | 'ATSI_P1-2_OES-138-002D_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT11 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 722.86 | 118.9304 | 120.4574 | Single | 'DVP_P1-2: LN 228_SRT-A' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT12 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 111.7355 | 120.01 | Line_FB | 'ATSI_P2-3_OES-138-065G_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT13 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 118.1014 | 119.37 | Line_FB | 'DVP_P4-2: 56372_SRT-A' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT14 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 111.7355 | 117.77 | Single | 'ATSI_P1-2_OES-138-002C_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT15 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 110.4167 | 115.59 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT16 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 110.4167 | 115.58 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT17 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 110.1562 | 115.4 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT18 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138/138 | 202/202 | 227 | 99.6035 | 115.05 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT19 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 107.3362 | 114.85 | Tower | 'ATSI_P7-1_OES-138-066_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT20 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 105.3719 | 112.93 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT21 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 105.7025 | 112.76 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT22 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 105.7025 | 112.76 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT23 | 208113 | SUSQ | 207972 | TOMH | 2 | 230/230 | 229/229 | 843 | 112.5267 | 112.45 | Tower | 'PL_48_P71_103285_SRT-A' | 717/843/768/894 | Yes
2025W1-N1-LLT24 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 104.0175 | 111.47 | Line_FB | 'ATSI_P2-3_OES-138-050_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT25 | 208113 | SUSQ | 207972 | TOMH | 1 | 230/230 | 229/229 | 843 | 111.7082 | 111.18 | Tower | 'PL_48_P71_103285_SRT-A' | 717/843/768/894 | Yes
2025W1-N1-LLT26 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 103.5371 | 110.99 | Line_FB | 'ATSI_P2-3_OES-138-051_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT27 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 103.5371 | 110.99 | Bus | 'ATSI_P2-2_OES-138-003_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT28 | 238908 | 02LONDON | 240709 | 02N TITUS | 1 | 138/138 | 202/202 | 242 | 94.7934 | 110.5 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT29 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 722.86 | 107.628 | 109.2447 | Single | 'DVP_P1-2: LN 567_SRT-A' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT30 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 107.2172 | 108.98 | Tower | 'DVP_P7-1: LN 2127-216_SRT-L' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT31 | 243469 | 05BEATTY | 241952 | 02DEERCREEK | 1 | 138/138 | 205/202 | 242 | N/A | 108.67 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT32 | 241987 | AE2-217_POI | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 242 | 92.8926 | 108.56 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-LLT33 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 101.4062 | 106.17 | Line_FB | 'ATSI_P2-3_OES-138-050_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT34 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 722.86 | 104.3632 | 106.0851 | Single | 'DVP_P1-2: LN 557_SRT-A' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT35 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 101.0417 | 105.87 | Line_FB | 'ATSI_P2-3_OES-138-051_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT36 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 101.0417 | 105.87 | Bus | 'ATSI_P2-2_OES-138-003_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT37 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 97.3967 | 104.66 | Line_FB | 'ATSI_P2-3_OES-138-048_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT38 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 97.3967 | 104.66 | Bus | 'ATSI_P2-2_OES-138-002_SRT-A' | 200/242/226/286 | Yes
2025W1-N1-LLT39 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 99.2188 | 102.74 | Line_FB | 'ATSI_P2-3_OES-138-025_SRT-A' | 160/192/180/228 | Yes
2025W1-N1-LLT40 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 769 | 101.0013 | 102.53 | Tower | 'DVP_P7-1: LN 211-228_SRT-L' | 705/705/811 : 782/782/899 : 769/769/884 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | Yes
2025W1-N1-LLT41 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 99.1667 | 102.43 | Line_FB | 'ATSI_P2-3_OES-138-026_SRT-A' | 160/192/180/228 | Yes
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230/230 | 345/345 | 830.02 | 101.9373 | 100.7872 | Single | 'DVP_P1-2: LN 588_SRT-A' | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD: WN/WE/WLD: LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025W1-N1-LLT43 | 208113 | SUSQ | 207972 | TOMH | 2 | 230/230 | 229/229 | 843 | 100.9134 | 100.05 | Tower | 'PL_48_P71_103319_SRT-A' | 717/843/768/894 | Yes
Note on J7: New Rating is used. Original rating is 769.0
Note on J8: New Rating is used. Original rating is 769.0
Note on J16: New Rating is used. Original rating is 769.0
Note on J34: New Rating is used. Original rating is 769.0
Note on J39: New Rating is used. Original rating is 769.0
Note on J47: New Rating is used. Original rating is 883.0

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Light Load 2030 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025W1-N1-LLVM1 | 208072 | SIEG | 230 | 229 | 0.89238 | 1.0183 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM2 | 207969 | TRES | 230 | 229 | 0.80115 | 1.0153 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM3 | 207967 | LOFT | 230 | 229 | 0.79598 | 1.0113 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM4 | 207966 | BWAY | 230 | 229 | 0.79945 | 1.0157 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM5 | 207963 | SLYK | 230 | 229 | 0.79965 | 1.0159 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM6 | 207960 | EPAL TR2 | 230 | 229 | 0.85999 | 1.0178 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM7 | 207959 | EPAL TR1 | 230 | 229 | 0.86023 | 1.0178 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVM8 | 241988 | AE2-217_MAIN | 138 | 202 | 0.77188 | 0.96188 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM9 | 241987 | AE2-217_POI | 138 | 202 | 0.77184 | 0.96183 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM10 | 241956 | AC1-078 MAIN | 138 | 202 | 0.89545 | 0.98082 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM11 | 241952 | 02DEERCREEK | 138 | 202 | 0.89548 | 0.98111 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM12 | 240710 | 02MELISSA | 138 | 202 | 0.74496 | 0.956 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM13 | 240709 | 02N TITUS | 138 | 202 | 0.74583 | 0.95615 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM14 | 240706 | 02NATIONAL | 138 | 202 | 0.8487 | 0.97169 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVM15 | 238908 | 02LONDON | 138 | 202 | 0.81714 | 0.96755 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Light Load 2030 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
2025W1-N1-LLVD1 | 208072 | SIEG | 230 | 229 | 0.90395 | 1.0183 | 11.433 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD2 | 207969 | TRES | 230 | 229 | 0.81753 | 1.0153 | 19.776 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD3 | 207967 | LOFT | 230 | 229 | 0.81242 | 1.0113 | 19.884 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD4 | 207966 | BWAY | 230 | 229 | 0.81595 | 1.0157 | 19.976 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD5 | 207963 | SLYK | 230 | 229 | 0.81615 | 1.0159 | 19.972 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD6 | 207960 | EPAL TR2 | 230 | 229 | 0.87312 | 1.0178 | 14.471 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD7 | 207959 | EPAL TR1 | 230 | 229 | 0.87335 | 1.0178 | 14.448 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD8 | 241987 | AE2-217_POI | 138 | 202 | 0.78042 | 0.96183 | 18.141 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVD9 | 240710 | 02MELISSA | 138 | 202 | 0.75339 | 0.956 | 20.261 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVD10 | 240709 | 02N TITUS | 138 | 202 | 0.75427 | 0.95615 | 20.188 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVD11 | 240706 | 02NATIONAL | 138 | 202 | 0.85551 | 0.97169 | 11.618 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVD12 | 238908 | 02LONDON | 138 | 202 | 0.82594 | 0.96755 | 14.161 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-LLVD13 | 211161 | SIEG | 138 | 229 | 0.92554 | 1.0146 | 8.908 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD14 | 211007 | NOEN TP2 | 138 | 229 | 0.92925 | 1.0134 | 8.414 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD15 | 211006 | NOEN TP1 | 138 | 229 | 0.92958 | 1.0136 | 8.403 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD16 | 211005 | NOEN | 138 | 229 | 0.92924 | 1.0134 | 8.414 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD17 | 210999 | NHAM 2 | 138 | 229 | 0.92924 | 1.0134 | 8.413 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD18 | 210998 | NHAM 1 | 138 | 229 | 0.92955 | 1.0136 | 8.403 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD19 | 210997 | NHAM TP2 | 138 | 229 | 0.92935 | 1.0135 | 8.412 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD20 | 210996 | NHAM TP1 | 138 | 229 | 0.92962 | 1.0136 | 8.402 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD21 | 210616 | EGYP 2 | 138 | 229 | 0.93179 | 1.0143 | 8.246 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD22 | 210615 | EGYP 1 | 138 | 229 | 0.93184 | 1.0142 | 8.231 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD23 | 210504 | WIBR 2 | 138 | 229 | 0.93109 | 1.0132 | 8.207 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD24 | 210503 | WIBR 1 | 138 | 229 | 0.93134 | 1.0133 | 8.194 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD25 | 210502 | WIBR TP2 | 138 | 229 | 0.93109 | 1.0132 | 8.207 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD26 | 210501 | WIBR TP1 | 138 | 229 | 0.93134 | 1.0133 | 8.194 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD27 | 210437 | BLMO | 138 | 229 | 0.93291 | 1.0142 | 8.133 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD28 | 211951 | WEIS TP1 | 69 | 229 | 0.84966 | 0.99036 | 14.07 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD29 | 211950 | WEIS TP2 | 69 | 229 | 0.84791 | 0.9889 | 14.099 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD30 | 211949 | WEIS | 69 | 229 | 0.83985 | 0.98225 | 14.24 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD31 | 211698 | LNFD | 69 | 229 | 0.89674 | 0.98013 | 8.339 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD32 | 211697 | LEHI TP | 69 | 229 | 0.84111 | 0.98327 | 14.216 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD33 | 211696 | LEHI | 69 | 229 | 0.84058 | 0.98282 | 14.224 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD34 | 211611 | HIRU | 69 | 229 | 0.8491 | 0.99 | 14.09 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD35 | 211446 | CHRI TP | 69 | 229 | 0.84957 | 0.9904 | 14.083 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD36 | 211427 | CARB | 69 | 229 | 0.8498 | 0.99057 | 14.077 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD37 | 211379 | BELT | 69 | 229 | 0.85007 | 0.99076 | 14.069 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD38 | 211377 | BELT 2 | 69 | 229 | 0.84792 | 0.98891 | 14.099 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD39 | 211376 | BELT 1 | 69 | 229 | 0.85007 | 0.99076 | 14.069 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD40 | 211366 | ASHF TP2 | 69 | 229 | 0.88569 | 0.98736 | 10.167 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD41 | 211365 | ASHF TP1 | 69 | 229 | 0.8908 | 0.98266 | 9.186 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD42 | 211347 | WHCE | 69 | 229 | 0.88294 | 0.98649 | 10.355 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD43 | 211346 | WHCE 2 | 69 | 229 | 0.88294 | 0.9865 | 10.356 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD44 | 211345 | WHCE 1 | 69 | 229 | 0.88417 | 0.9876 | 10.343 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD45 | 211337 | WGAT 2 | 69 | 229 | 0.8716 | 0.97682 | 10.522 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD46 | 211336 | WGAT 1 | 69 | 229 | 0.86991 | 0.9756 | 10.569 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD47 | 211273 | TREI DC | 69 | 229 | 0.88539 | 0.98716 | 10.177 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD48 | 211272 | TREI TP2 | 69 | 229 | 0.88518 | 0.98819 | 10.301 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD49 | 211270 | TREI | 69 | 229 | 0.88506 | 0.98687 | 10.181 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD50 | 211268 | TREI TP1 | 69 | 229 | 0.88539 | 0.98717 | 10.178 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD51 | 211193 | SSLA 2 | 69 | 229 | 0.88542 | 0.98784 | 10.242 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD52 | 211190 | SSLA 1 | 69 | 229 | 0.88694 | 0.98561 | 9.867 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD53 | 211160 | SIEG | 69 | 229 | 0.88504 | 0.98835 | 10.331 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD54 | 211064 | PSPA COL | 69 | 229 | 0.89848 | 0.97982 | 8.134 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD55 | 211063 | PSPA | 69 | 229 | 0.89757 | 0.97998 | 8.241 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD56 | 211062 | PSPA TP2 | 69 | 229 | 0.88583 | 0.98751 | 10.168 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD57 | 211061 | PSPA TP1 | 69 | 229 | 0.89747 | 0.98 | 8.253 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD58 | 211057 | PONO 1 | 69 | 229 | 0.86963 | 0.97538 | 10.575 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD59 | 211056 | PNWG TP2 | 69 | 229 | 0.87224 | 0.97738 | 10.514 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD60 | 211055 | PNWG TP1 | 69 | 229 | 0.87066 | 0.97625 | 10.559 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD61 | 211054 | PONO 2 | 69 | 229 | 0.87132 | 0.9766 | 10.528 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD62 | 211052 | APRF TP | 69 | 229 | 0.86967 | 0.97541 | 10.574 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD63 | 211051 | APRF | 69 | 229 | 0.86965 | 0.9754 | 10.575 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD64 | 211031 | PAZI | 69 | 229 | 0.8491 | 0.98986 | 14.076 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD65 | 211030 | PAZI 2 | 69 | 229 | 0.84911 | 0.98986 | 14.075 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD66 | 211029 | PAZI 1 | 69 | 229 | 0.8494 | 0.99011 | 14.071 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD67 | 211022 | PALM 2 | 69 | 229 | 0.84918 | 0.98992 | 14.074 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD68 | 211021 | PALM 1 | 69 | 229 | 0.84946 | 0.99017 | 14.071 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD69 | 210972 | NBET 2 | 69 | 229 | 0.8741 | 0.979 | 10.49 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD70 | 210971 | NBET 1 | 69 | 229 | 0.87282 | 0.97808 | 10.526 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD71 | 210914 | MICK TP2 | 69 | 229 | 0.8817 | 0.98543 | 10.373 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD72 | 210913 | MICK 2 | 69 | 229 | 0.8815 | 0.98526 | 10.376 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD73 | 210912 | MICK 1 | 69 | 229 | 0.88252 | 0.98617 | 10.365 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD74 | 210911 | MICK TP1 | 69 | 229 | 0.88275 | 0.98637 | 10.362 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD75 | 210829 | LIGA 1 | 69 | 229 | 0.84933 | 0.99005 | 14.072 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD76 | 210828 | LIGA 2 | 69 | 229 | 0.84892 | 0.9897 | 14.078 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD77 | 210827 | LIGA TAP | 69 | 229 | 0.84928 | 0.99 | 14.072 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD78 | 210762 | KECE 1-2 | 69 | 229 | 0.89282 | 0.97926 | 8.644 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD79 | 210761 | KECE 1-1 | 69 | 229 | 0.89298 | 0.97916 | 8.618 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD80 | 210760 | KECE 2-2 | 69 | 229 | 0.89286 | 0.97929 | 8.643 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD81 | 210759 | KECE 2-1 | 69 | 229 | 0.89302 | 0.97919 | 8.617 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD82 | 210758 | KECE2TP2 | 69 | 229 | 0.89298 | 0.9794 | 8.642 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD83 | 210757 | KECE2TP1 | 69 | 229 | 0.89314 | 0.9793 | 8.616 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD84 | 210756 | KECE1TP2 | 69 | 229 | 0.89407 | 0.98039 | 8.632 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD85 | 210755 | KECE1TP1 | 69 | 229 | 0.89422 | 0.98029 | 8.607 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD86 | 210601 | EPAL | 69 | 229 | 0.84933 | 0.99004 | 14.071 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD87 | 210570 | DRAG 2 | 69 | 229 | 0.88335 | 0.98686 | 10.351 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD88 | 210569 | DRAG 1 | 69 | 229 | 0.88428 | 0.9877 | 10.342 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD89 | 210568 | DRAG | 69 | 229 | 0.88428 | 0.9877 | 10.342 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD90 | 210405 | EPHA TI2 | 69 | 229 | 0.88563 | 0.98774 | 10.211 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-LLVD91 | 210404 | EPHA TI1 | 69 | 229 | 0.88842 | 0.98435 | 9.593 | Tower | PL_60_P71_000890_SRT-A | Yes

## N-1 Load Drop
PJM N-1 Load Drop Result (Light Load 2030 Case)
FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
N/A | DVP_P1-2: LN 2140_SRT-A | Single | 345 | 0 | 371 | 371 | No | To be adressed through supplemental process.
N/A | DVP_P4-2: 214052_SRT-A | Line_FB | 345 | 0 | 371 | 371 | No | To be adressed through supplemental process.
N/A | DVP_P4-2: 2094T2140_SRT-A | Line_FB | 345 | 0 | 371 | 371 | No | To be adressed through supplemental process.
N/A | DVP_P4-2: 214042_SRT-A | Line_FB | 345 | 0 | 371 | 371 | No | To be adressed through supplemental process.
N/A | DVP_P7-1: LN 2140-2176_SRT-A | Tower | 345 | 0 | 371 | 371 | No | To be adressed through supplemental process.
N/A | DVP_P7-1: LN 2140-535_SRT-A | Tower | 345, 201 | 0 | 371 | 371 | No | To be adressed through supplemental process.