## Light Load GenDeliv
2030 RTEP PJM Generator Deliverability Result (Light Load)
FG Index | FG # | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
10 | 2025W1-GD-LL10 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 269.5 | 284.7 | 117.67 | 124.34 | ATSI_P1-2_OES-138-002D_SRT-A | Single | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
102 | 2025W1-GD-LL102 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 269.5 | 290 | 117.67 | 126.66 | ATSI_P2-3_OES-138-065_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
103 | 2025W1-GD-LL103 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 269.5 | 290 | 117.67 | 126.66 | ATSI_P2-3_OES-138-065B_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
104 | 2025W1-GD-LL104 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 276 | 295.9 | 114.04 | 122.26 | ATSI_P2-3_OES-138-065G_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes
105 | 2025W1-GD-LL105 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 884 | 1064.3 | 1073.2 | 120.39 | 121.41 | DVP_P4-2: 562T563_SRT-L | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
106 | 2025W1-GD-LL106 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 884 | 1017.9 | 1027.7 | 115.15 | 116.25 | DVP_P4-2: 56372_SRT-A | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
107 | 2025W1-GD-LL107 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 212.7 | 220.4 | 110.77 | 114.81 | ATSI_P2-3_OES-138-0208BT_SRT-A | Breaker | 160 / 192 / 180 / 228 | Yes
108 | 2025W1-GD-LL108 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 884 | 991.9 | 1010.3 | 112.21 | 114.29 | DVP_P4-2: 205T217_SRT-A | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
109 | 2025W1-GD-LL109 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 242.8 | 260.1 | 106.04 | 113.59 | ATSI_P2-3_OES-138-050_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
11 | 2025W1-GD-LL11 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 722.9 | 887.5 | 898.5 | 122.78 | 124.3 | DVP_P1-2: LN 228_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
110 | 2025W1-GD-LL110 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 241.7 | 258.9 | 105.56 | 113.04 | ATSI_P2-3_OES-138-051_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
111 | 2025W1-GD-LL111 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 884 | 970.8 | 985.1 | 109.81 | 111.43 | DVP_P4-2: 21712_SRT-L | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
112 | 2025W1-GD-LL112 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 884 | 970.1 | 984.4 | 109.74 | 111.35 | DVP_P4-2: H8T217_SRT-L | Breaker | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
113 | 2025W1-GD-LL113 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 197.9 | 207.2 | 103.08 | 107.94 | ATSI_P2-3_OES-138-050_SRT-A | Breaker | 160 / 192 / 180 / 228 | Yes
114 | 2025W1-GD-LL114 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 197.3 | 206.5 | 102.75 | 107.55 | ATSI_P2-3_OES-138-051_SRT-A | Breaker | 160 / 192 / 180 / 228 | Yes
119 | 2025W1-GD-LL119 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 240.9 | 258.4 | 99.55 | 106.79 | ATSI_P2-3_OES-138-048_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes
12 | 2025W1-GD-LL12 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 276 | 290.5 | 114.04 | 120.05 | ATSI_P1-2_OES-138-002C_SRT-A | Single | 200 / 242 / 226 / 286 | Yes
124 | 2025W1-GD-LL124 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 193.4 | 200 | 100.72 | 104.18 | ATSI_P2-3_OES-138-025_SRT-A | Breaker | 160 / 192 / 180 / 228 | Yes
125 | 2025W1-GD-LL125 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 193.3 | 199.5 | 100.68 | 103.88 | ATSI_P2-3_OES-138-026_SRT-A | Breaker | 160 / 192 / 180 / 228 | Yes
127 | 2025-W1-GD-LL127 | 243017 | 05HAVILAND1 | 242989 | 05E LIMA | 1 | 138 | 205 | 205 | 206.9 | 209.3 | 100.95 | 102.1 | AEP_P4_#7445_05MARYSV 765_B_SRT-A | Breaker | 205/284/258/320 | No | Substation Equipment Exclusion
13 | 2025W1-GD-LL13 | 314747 | 6BREMO | 313867 | 6BREMODIST | 1 | 230 | 345 | 830 | 950.9 | 945.5 | 114.57 | 113.91 | DVP_P1-2: LN 576_SRT-A | Single | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
130 | 2025W1-GD-LL130 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138 | 202 | 282 | 276.3 | 286.7 | 97.98 | 101.66 | ATSI_P2-3_OES-138-060H_SRT-A | Breaker | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
136 | 2025W1-GD-LL136 | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 163.5 | 160.9 | 102.21 | 100.57 | PN_P2-3_PN-115-62D_SRT-A | Breaker | 133/160/150/190 (SLN/SLE/WN/WE) | Yes |  | Overlap with current market efficiency window. Overlap FE EOL candidate
14 | 2025W1-GD-LL14 | 313867 | 6BREMODIST | 313707 | 6FORK UNION | 1 | 230 | 345 | 830 | 947.6 | 942.2 | 114.17 | 113.52 | DVP_P1-2: LN 576_SRT-A | Single | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
15 | 2025W1-GD-LL15 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 722.9 | 803.7 | 815.4 | 111.19 | 112.81 | DVP_P1-2: LN 567_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
16 | 2025W1-GD-LL16 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 722.9 | 778.7 | 791.1 | 107.73 | 109.44 | DVP_P1-2: LN 557_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
175 | 2025W1-GD-LL175 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 212.6 | 220.4 | 110.75 | 114.79 | ATSI_P2-2_OES-138-055T_SRT-A | Bus | 160 / 192 / 180 / 228 | Yes
176 | 2025W1-GD-LL176 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 241.7 | 258.9 | 105.56 | 113.04 | ATSI_P2-2_OES-138-003_SRT-A | Bus | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
177 | 2025W1-GD-LL177 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 197.3 | 206.5 | 102.75 | 107.55 | ATSI_P2-2_OES-138-003_SRT-A | Bus | 160 / 192 / 180 / 228 | Yes
178 | 2025W1-GD-LL178 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 240.9 | 258.4 | 99.55 | 106.79 | ATSI_P2-2_OES-138-002_SRT-A | Bus | 200 / 242 / 226 / 286 | Yes
180 | 2025W1-GD-LL180 | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 163.6 | 160.9 | 102.25 | 100.57 | PN_P2-2_PN-115-002_SRT-A | Bus | 133/160/150/190 (SLN/SLE/WN/WE) | Yes |  | Overlap with current market efficiency window. Overlap FE EOL candidate
189 | 2025-W1-GD-LL189 | 272730 | WATERMAN ; R | 272445 | SANDWICH ; R | 1 | 138 | 222 | 331 | 471.6 | 471.1 | 142.49 | 142.33 | COMED_P7-1_138-L11106_B-R_+_345-L30003_B-R_SRT-A | Tower | 238/309/312/331/295/343/355/376 (SN/SLTE/SSTE/SLD/WN/WLTE/WSTE/WLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
190 | 2025W1-GD-LL190 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 250.7 | 267.6 | 109.48 | 116.85 | ATSI_P7-1_OES-138-066_SRT-A | Tower | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
191 | 2025W1-GD-LL191 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 212.1 | 222.3 | 110.48 | 115.77 | ATSI_P7-1_OES-138-066A_SRT-A | Tower | 160 / 192 / 180 / 228 | Yes
192 | 2025W1-GD-LL192 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 956 | 956.9 | 113.41 | 113.51 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 | Yes
194 | 2025W1-GD-LL194 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 949 | 946 | 112.57 | 112.22 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 | Yes
195 | 2025W1-GD-LL195 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 858.6 | 852.3 | 101.85 | 101.11 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 | Yes
22 | 2025W1-GD-LL22 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 1071.6 | 1125 | 1134.2 | 104.98 | 105.84 | DVP_P1-2: LN 563_SRT-A | Single | 1046/1046/1203 : 1160/1160/1333 : 1140/1140/1311 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
24 | 2025W1-GD-LL24 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 1071.6 | 1105.8 | 1111.7 | 103.19 | 103.74 | DVP_P1-2: LN 567_SRT-A | Single | 1046/1046/1203 : 1160/1160/1333 : 1140/1140/1311 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
25 | 2025W1-GD-LL25 | 313373 | 6GRAPEVINE | 314765 | 6MTEAGLE | 1 | 230 | 345 | 808.4 | 821.8 | 822.5 | 101.66 | 101.75 | DVP_P1-2: LN 576_SRT-A | Single | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
26 | 2025-W1-GD-LL26 | 314744 | 3BREMO | 313708 | 3FORK UNION | 2 | 115 | 345 | 179.5 | 184.2 | 182.3 | 102.62 | 101.54 | DVP_P1-2: LN 2193_SRT-A | Single | 143/143/164 : 200/200/230 : 191/191/220 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
27 | 2025W1-GD-LL27 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 1071.6 | 1079.5 | 1087.2 | 100.74 | 101.45 | DVP_P1-2: LN 259_SRT-L | Single | 1046/1046/1203 : 1160/1160/1333 : 1140/1140/1311 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
28 | 2025W1-GD-LL28 | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 164.6 | 161.9 | 102.89 | 101.2 | PN_P1-2_PN-115-068_SRT-A | Single | 133/160/150/190 (SLN/SLE/WN/WE) | Yes |  | Overlap with current market efficiency window. Overlap FE EOL candidate
31 | 2025W1-GD-LL31 | 314303 | 6HOPEWLL | 314286 | 6CHESTF A | 1 | 230 | 345 | 1071.6 | 1069.8 | 1078.5 | 99.83 | 100.65 | DVP_P1-2: LN 217_SRT-L | Single | 1046/1046/1203 : 1160/1160/1333 : 1140/1140/1311 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
32 | 2025W1-GD-LL32 | 200762 | 26GARRETT | 235470 | 01GARRET | 1 | 115 | 226/201 | 160 | 163.6 | 160.9 | 102.25 | 100.57 | PN_P1-3_PN-115-025_SRT-A | Single | 133/160/150/190 (SLN/SLE/WN/WE) | Yes |  | Overlap with current market efficiency window. Overlap FE EOL candidate
33 | 2025W1-GD-LL33 | 314765 | 6MTEAGLE | 314749 | 6CHARLVL | 1 | 230 | 345 | 808.4 | 805.2 | 812.4 | 99.6 | 100.49 | DVP_P1-2: LN 576_SRT-A | Single | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
35 | 2025W1-GD-LL35 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138 | 202 | 192 | 186.4 | 192.4 | 97.11 | 100.22 | ATSI_P1-2_OES-138-018_SRT-A | Single | 160 / 192 / 180 / 228 | Yes
8 | 2025W1-GD-LL8 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 722.9 | 1050.5 | 1059.9 | 145.32 | 146.63 | DVP_P1-2: LN 563_SRT-A | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
9 | 2025W1-GD-LL9 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230 | 345 | 722.9 | 972.9 | 987.2 | 134.59 | 136.57 | DVP_P1-2: LN 217_SRT-L | Single | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
96 | 2025W1-GD-LL96 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138 | 202 | 242 | 308 | 359.6 | 127.26 | 148.59 | ATSI_P2-4_OES-138-047_SRT-A | Breaker | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
1 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 1545.5 | 1536.1 | 186.2 | 185.06 | DVP_P1-2: LN 588_SRT-A | Single | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
94 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1538.6 | 1529 | 151.59 | 150.64 | DVP_P4-2: H2T588_SRT-A | Breaker | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
95 | N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1538.5 | 1529 | 151.58 | 150.64 | DVP_P4-2: H5T588_SRT-A | Breaker | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
30 | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 1 | 500/230 | 345 | 1254.9 | 1260.1 | 1267.9 | 100.42 | 101.04 | DVP_P1-2: LN 588_SRT-A | Single | 1133/1190/1323 : 1344/1344/1344 : 1336/1338/1344 | No |  | Defer until CVOW network upgrades are finalized.
34 | N/A | 314909 | 8FENTRES | 314466 | 6FENTRES | 2 | 500/230 | 345 | 1246.4 | 1244.7 | 1252.5 | 99.86 | 100.48 | DVP_P1-2: LN 588_SRT-A | Single | 1122/1176/1302 : 1344/1344/1344 : 1324/1330/1344 | No |  | Defer until CVOW network upgrades are finalized.
17 | N/A | 316171 | 6POCATY | 314481 | 6LANDSTN | 1 | 230 | 345 | 830 | 894.8 | 889.3 | 107.81 | 107.15 | DVP_P1-2: LN 588_SRT-A | Single | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
23 | N/A | 314214 | 6CHCKAHM | 314258 | 6ELKO | 1 | 230 | 345 | 830 | 866.7 | 866.1 | 104.42 | 104.35 | DVP_P1-2: LN 557_SRT-A | Single | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.

## Light Load IPD
2030 RTEP PJM Individual Plant Deliverability Result (Light Load)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reason For Exclusion | Comments
2025W1-IPD-LL1 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 242 | 375.7 | 134.47 | 155.26 | AD1-081 | ATSI_P2-4_OES-138-047_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 969.3 | 131.86 | 134.09 | AF1-123 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 969.3 | 131.86 | 134.09 | AF1-124 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 969.3 | 131.86 | 134.09 | AF1-125 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 966.2 | 131.98 | 133.66 | AF1-123 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 966.2 | 131.98 | 133.66 | AF1-124 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 966.2 | 131.98 | 133.66 | AF1-125 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025W1-IPD-LL2 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 962.7 | 131.04 | 133.18 | AE1-173 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL3 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 959.9 | 131.27 | 132.79 | AE1-173 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL4 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 955.9 | 130.17 | 132.25 | AB2-190 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL5 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 955.9 | 130.17 | 132.24 | AD1-151 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL6 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 955.4 | 130.1 | 132.17 | AD1-025 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL7 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 955.1 | 130.06 | 132.12 | AB2-134 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL8 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 955.1 | 130.04 | 132.12 | LTFIMP_O-066 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL9 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 953.4 | 129.86 | 131.89 | AE2-033 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 1094.6 | 133.55 | 131.88 | AF1-123 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 1094.6 | 133.55 | 131.88 | AF1-124 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 1094.6 | 133.55 | 131.88 | AF1-125 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025W1-IPD-LL10 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 953.3 | 129.82 | 131.87 | AD1-074 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL11 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 953 | 129.79 | 131.84 | AE1-149 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL12 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 952.4 | 129.71 | 131.75 | AC1-216 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL13 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 951.9 | 129.66 | 131.68 | AE2-027 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL14 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 951.9 | 129.64 | 131.68 | W1-029 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL15 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 951.7 | 129.63 | 131.65 | AF2-304 | DVP_P1-2: LN 217_SRT-L | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL16 | 314276 | 6BASIN | 314287 | 6CHESTF B | 1 | 230 | 345 | 722.9 | 947.2 | 129.63 | 131.03 | LTFIMP_O-066 | DVP_P1-2: LN 563_SRT-A | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL17 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 296 | 120.29 | 129.27 | AD2-163 | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL18 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 296 | 120.29 | 129.27 | AD2-163 | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL19 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 293.3 | 119.17 | 128.09 | AD1-140 | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL20 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 293.3 | 119.17 | 128.09 | AD1-140 | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL21 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290.9 | 120.29 | 127.05 | AD2-163 | ATSI_P1-2_OES-138-002D_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL22 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290.1 | 117.81 | 126.67 | AF1-053 | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL23 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290.1 | 117.81 | 126.67 | AF1-053 | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL24 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290 | 117.62 | 126.65 | 08ZIMRHP | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL25 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 290 | 117.62 | 126.65 | 08ZIMRHP | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL26 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 289.8 | 117.7 | 126.57 | AE2-305 | ATSI_P2-3_OES-138-065_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL27 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 289.8 | 117.7 | 126.57 | AE2-305 | ATSI_P2-3_OES-138-065B_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL28 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138 | 202 | 229 | 288.2 | 119.17 | 125.84 | AD1-140 | ATSI_P1-2_OES-138-002D_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-IPD-LL29 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 302 | 116.58 | 124.78 | AD2-163 | ATSI_P2-3_OES-138-065G_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL30 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 299.2 | 115.49 | 123.63 | AD1-140 | ATSI_P2-3_OES-138-065G_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL31 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 296.9 | 116.58 | 122.68 | AD2-163 | ATSI_P1-2_OES-138-002C_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL32 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 295.8 | 114.17 | 122.25 | AF1-053 | ATSI_P2-3_OES-138-065G_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL33 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 295.8 | 113.99 | 122.24 | 08ZIMRHP | ATSI_P2-3_OES-138-065G_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL34 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 295.6 | 114.06 | 122.15 | AE2-305 | ATSI_P2-3_OES-138-065G_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL35 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 294 | 115.49 | 121.49 | AD1-140 | ATSI_P1-2_OES-138-002C_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL36 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 290.5 | 113.99 | 120.06 | 08ZIMRHP | ATSI_P1-2_OES-138-002C_SRT-A | 200 / 242 / 226 / 286 | Yes
2025W1-IPD-LL37 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138 | 202 | 242 | 290.5 | 114.17 | 120.04 | AF1-053 | ATSI_P1-2_OES-138-002C_SRT-A | 200 / 242 / 226 / 286 | Yes
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1090.3 | 108.78 | 107.42 | AF1-123 | DVP_P4-2: H2T588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1090.3 | 108.78 | 107.42 | AF1-124 | DVP_P4-2: H2T588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1090.3 | 108.78 | 107.42 | AF1-125 | DVP_P4-2: H2T588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1090.2 | 108.78 | 107.41 | AF1-123 | DVP_P4-2: H5T588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1090.2 | 108.78 | 107.41 | AF1-124 | DVP_P4-2: H5T588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 1015 | 1090.2 | 108.78 | 107.41 | AF1-125 | DVP_P4-2: H5T588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025W1-IPD-LL38 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 297.6 | 101.99 | 105.54 | AD1-140 | ATSI_P2-3_OES-138-060H_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 867 | 105.62 | 104.46 | AE1-072 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 862.7 | 105.11 | 103.94 | AA1-139 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 858.5 | 104.6 | 103.43 | AE2-253 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 856.8 | 104.36 | 103.23 | W1-029 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 853.9 | 104.01 | 102.87 | Z1-036 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 851.6 | 103.76 | 102.6 | AD1-033 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 850.8 | 103.63 | 102.5 | AD1-074 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 845.3 | 102.97 | 101.84 | AE2-034 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025-W1-IPD-LL39 | 313708 | 3FORK UNION | 314744 | 3BREMO | 2 | 115 | 345 | 179.5 | 182.8 | 102.73 | 101.81 | AE1-108 | DVP_P1-2: LN 2193_SRT-A | 143/143/164 : 200/200/230 : 191/191/220 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025W1-IPD-LL40 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 287 | 98.14 | 101.77 | 08ZIMRHP | ATSI_P2-3_OES-138-060H_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 844.7 | 102.93 | 101.77 | 3O INLET | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 842.4 | 102.65 | 101.5 | LTFIMP_O-066 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 314466 | 6FENTRES | 314508 | 6THRASHER | 1 | 230 | 345 | 830 | 841.8 | 102.56 | 101.42 | AD1-076 | DVP_P1-2: LN 588_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025W1-IPD-LL41 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138 | 202 | 282 | 285.6 | 97.65 | 101.26 | 08ZIMRLP | ATSI_P2-3_OES-138-060H_SRT-A | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
N/A | 313867 | 6BREMODIST | 314747 | 6BREMO | 1 | 230 | 345 | 830 | 838.7 | 101.45 | 101.04 | AF1-123 | DVP_P1-2: LN 576_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 313867 | 6BREMODIST | 314747 | 6BREMO | 1 | 230 | 345 | 830 | 838.7 | 101.45 | 101.04 | AF1-124 | DVP_P1-2: LN 576_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 313867 | 6BREMODIST | 314747 | 6BREMO | 1 | 230 | 345 | 830 | 838.7 | 101.45 | 101.04 | AF1-125 | DVP_P1-2: LN 576_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 313707 | 6FORK UNION | 313867 | 6BREMODIST | 1 | 230 | 345 | 830 | 835.4 | 101.06 | 100.65 | AF1-123 | DVP_P1-2: LN 576_SRT-A | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 313707 | 6FORK UNION | 313867 | 6BREMODIST | 1 | 230 | 345 | 830 | 835.4 | 101.06 | 100.65 | AF1-124 | DVP_P1-2: LN 576_SRT-A | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
N/A | 313707 | 6FORK UNION | 313867 | 6BREMODIST | 1 | 230 | 345 | 830 | 835.4 | 101.06 | 100.65 | AF1-125 | DVP_P1-2: LN 576_SRT-A | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No |  | Defer until CVOW network upgrades are finalized.
2025W1-IPD-LL42 | 313867 | 6BREMODIST | 314747 | 6BREMO | 1 | 230 | 345 | 830 | 834 | 100.94 | 100.47 | AE1-173 | DVP_P1-2: LN 576_SRT-A | 721/721/829 : 913/913/1050 : 883/883/1015 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-IPD-LL43 | 313707 | 6FORK UNION | 313867 | 6BREMODIST | 1 | 230 | 345 | 830 | 830.7 | 100.55 | 100.08 | AE1-173 | DVP_P1-2: LN 576_SRT-A | 703/703/808 : 890/890/1024 : 860/860/989 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes