## N-0 Thermal
PJM N-0 Thermal Result (Summer 2030 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025W1-N0-ST1 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 163 | 103.0061 | 101.55 | Single | 'BASE CASE' | 163/200/201/220 | Yes
2025W1-N0-ST2 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138/138 | 202/202 | 233 | 100.3863 | 100.86 | Single | 'BASE CASE' | 233/282/263/333 | Yes |  | Overlap FE EOL candidate

## N-0 Volt Mag
PJM N-0 Voltage Magnitude Result (Summer 2030 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025W1-N0-SVM1 | 240710 | 02MELISSA | 138 | 202 | 0.94604 | 0.94604 | 0.95 | Single | BASE CASE | Yes
2025W1-N0-SVM2 | 240709 | 02N TITUS | 138 | 202 | 0.94613 | 0.94613 | 0.95 | Single | BASE CASE | Yes

## N-1 Thermal
PJM N-1 Thermal Result (Summer 2030 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | Conductor Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025W1-N1-ST1 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 135.5785 | 157.22 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST2 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 118.125 | 138.68 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST3 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 127.0213 | 138.11 | Line_FB | 'ATSI_P2-3_OES-138-060H_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST4 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 118.4896 | 136.41 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST5 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 118.5417 | 136.35 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST6 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 105.9917 | 127.7 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST7 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 662.7 | 127.1465 | 127.5532 | Single | 'DVP_P1-2: LN 563_SRT-A' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST8 | 243469 | 05BEATTY | 241952 | 02DEERCREEK | 1 | 138/138 | 205/202 | 242 | 105.5372 | 124.64 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025-W1-N1-ST9 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 123.8095 | 126.82 | P2_1 | '246613 05GENOA 69.0 246643 05WESTRV2B 69.0 1_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025-W1-N1-ST10 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 123.8095 | 126.8 | Single | 'AEP_P1-3_#11531_05GENOA 138_2_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025W1-N1-ST11 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 662.7 | 124.9736 | 126.2872 | Single | 'DVP_P1-2: LN 217_SRT-S' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST12 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 124.3262 | 125.84 | Line_FB | 'DVP_P4-2: 205T217_SRT-A' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST13 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 125.3759 | 125.61 | Line_FB | 'DVP_P4-2: 562T563_SRT-S' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST14 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 106.3223 | 125.37 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST15 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 106.3223 | 125.27 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST16 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 113.0131 | 124.72 | Line_FB | 'ATSI_P2-3_OES-138-065B_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST17 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 113.0131 | 124.72 | Line_FB | 'ATSI_P2-3_OES-138-065_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025-W1-N1-ST18 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 123.8095 | 126.8 | Line_FB | 'AEP_P4_#11531_05GENOA 69.0_64_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025-W1-N1-ST19 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 106.0317 | 107.39 | P2_1 | '243513 05GENOA 138 246613 05GENOA 69.0 2_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025-W1-N1-ST20 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 105.7143 | 107.1 | P2_1 | '246627 05WESTRVL5 69.0 246643 05WESTRV2B 69.0 1_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025-W1-N1-ST21 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 101.2698 | 101.58 | Line_FB | 'AEP_P4_#9656_05GENOA 138_103N_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025-W1-N1-ST22 | 243513 | 05GENOA | 246615 | 05GENOAEQ1 | 1 | 138/1 | 205/205 | 63 | 101.2698 | 101.58 | Bus | 'AEP_P2-2_#9656_05GENOA 138_N_SRT-A' | 136/138/153/158 | No | Substation Equipment Exclusion
2025W1-N1-ST23 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345/345 | 205/205 | 1385 | 101.1625 | 102.77 | Tower | '34506 34542_SRT-A' | 1385/1385/1750/1750 | Yes
2025W1-N1-ST24 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 104.7521 | 122.27 | Line_FB | 'ATSI_P2-3_OES-138-060H_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST25 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 113.0131 | 122.08 | Single | 'ATSI_P1-2_OES-138-002D_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST26 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 109.5041 | 120.22 | Line_FB | 'ATSI_P2-3_OES-138-065G_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST27 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 119.7 | 119.56 | Tower | '34506 34542_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST28 | 208113 | SUSQ | 207972 | TOMH | 2 | 230/230 | 229/229 | 843 | 117.9715 | 119.1 | Tower | 'PL_48_P71_103285_SRT-A' | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N1-ST29 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 117.4752 | 118.71 | Line_FB | 'DVP_P4-2: 21712_SRT-S' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST30 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 117.461 | 118.69 | Line_FB | 'DVP_P4-2: H8T217_SRT-S' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST31 | 208113 | SUSQ | 207972 | TOMH | 1 | 230/230 | 229/229 | 843 | 117.1293 | 117.74 | Tower | 'PL_48_P71_103285_SRT-A' | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N1-ST32 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 109.5041 | 117.71 | Single | 'ATSI_P1-2_OES-138-002C_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST33 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 116.0426 | 116.49 | Line_FB | 'DVP_P4-2: 56372_SRT-A' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST34 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 662.7 | 114.8333 | 115.9255 | Single | 'DVP_P1-2: LN 228_SRT-A' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST35 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 104.9345 | 115.02 | Tower | 'ATSI_P7-1_OES-138-066_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST36 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 114.3 | 114.64 | Single | 'ATSI_P1-2_OES-138-935TB_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST37 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 114.3 | 114.64 | Line_FB | 'ATSI_P2-3_OES-138-024AT_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST38 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 114.25 | 114.61 | Line_FB | 'ATSI_P2-3_OES-138-023T_SRT-SL' | 163/200/201/220 | Yes
2025W1-N1-ST39 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 103.8652 | 113.86 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST40 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 108.8542 | 113.37 | Line_FB | 'ATSI_P2-3_OES-138-025_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST41 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 108.8021 | 112.92 | Line_FB | 'ATSI_P2-3_OES-138-026_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST42 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 102.5328 | 112.85 | Line_FB | 'ATSI_P2-3_OES-138-050_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST43 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 106.6667 | 112.82 | Line_FB | 'ATSI_P2-3_OES-138-050_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST44 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 103.9716 | 112.74 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST45 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138/138 | 202/202 | 227 | 100.1762 | 112.69 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST46 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 103.8298 | 112.52 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST47 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 112 | 112.37 | Tower | 'ATSI_P7-1_OES-138-065T_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST48 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 105.9896 | 112.27 | Line_FB | 'ATSI_P2-3_OES-138-051_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST49 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 105.9896 | 112.27 | Bus | 'ATSI_P2-2_OES-138-003_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST50 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 101.5721 | 111.94 | Line_FB | 'ATSI_P2-3_OES-138-051_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST51 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | 101.5721 | 111.94 | Bus | 'ATSI_P2-2_OES-138-003_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST52 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 103.5124 | 111.78 | Line_FB | 'ATSI_P2-3_OES-138-0607A_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST53 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 103.5124 | 111.76 | Line_FB | 'ATSI_P2-3_OES-138-0607C_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST54 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 103.4711 | 111.75 | Line_FB | 'ATSI_P2-3_OES-138-0607E_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST55 | 241952 | 02DEERCREEK | 238908 | 02LONDON | 1 | 138/138 | 202/202 | 242 | 103.595 | 111.73 | Bus | 'ATSI_P2-2_OES-138-054_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST56 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 114.8936 | 123.37 | Single | 'AEP_P1-2_#5793_663_SRT-A' | 47/47/47/47 | Yes
2025W1-N1-ST57 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 106.1458 | 110.1 | P2_1 | 'ATSI_P2-1_OES-138-LINE1-SR-044_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST58 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 108.25 | 108.71 | Line_FB | 'AEP_P4_#7445_05MARYSV 765_B_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST59 | 238908 | 02LONDON | 240709 | 02N TITUS | 1 | 138/138 | 202/202 | 242 | 95.2893 | 108.25 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST60 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 105.2128 | 108.19 | Line_FB | 'DAY_URBANA_FB_DB_D_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST61 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 103.8021 | 107.73 | Single | 'ATSI_P1-2_OES-138-018_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST62 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 114.8936 | 123.37 | Line_FB | 'AEP_P4_#5793_05BEATTY 138_1E_SRT-A' | 47/47/47/47 | Yes
2025W1-N1-ST63 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 103.2812 | 107.38 | P2_1 | 'ATSI_P2-1_OES-138-LINE1-SR-043_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST64 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 90.4412 | 107.3 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST65 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 104.078 | 107.2 | Line_FB | 'DAY_URBANA_FB_DB_C_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST66 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 114.8936 | 123.37 | Bus | 'AEP_P2-2_#5793_05MCCOMB 138_2_SRT-A' | 47/47/47/47 | Yes
2025W1-N1-ST67 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 103.9362 | 106.98 | Single | 'DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST68 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 103.9362 | 106.98 | Bus | 'URBANA_138KV_W_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST69 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 102.15 | 106.73 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST70 | 241987 | AE2-217_POI | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 242 | 93.3884 | 106.33 | Line_FB | 'ATSI_P2-4_OES-138-047_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST71 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 102.2 | 106.1 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 163/200/201/220 | Yes
2025-W1-N1-ST72 | 249567 | 08M.FORT | 250057 | 08M.FORT | 10 | 345/138 | 212/212 | 498 | 101.9679 | 105.98 | Line_FB | 'DEOK_P4_1418_MIAMI FORT_SRT-A' | SN/SE/SLD/WN/WE/WLD: 478/498/498/600/600/600 MVA | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025W1-N1-ST73 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 102 | 105.87 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST74 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | N/A | 105.46 | Tower | 'ATSI_P7-1_OES-138-066A_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST75 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 90.6618 | 105.4 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST76 | 207915 | GLBR | 208120 | SU10 | 1 | 230/230 | 229/229 | 801 | 106.1798 | 105.19 | Line_FB | 'PL_48_P42_101954_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST77 | 207915 | GLBR | 208120 | SU10 | 1 | 230/230 | 229/229 | 801 | 106.1798 | 105.18 | Single | 'PL_48_P12_101741_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST78 | 207915 | GLBR | 208120 | SU10 | 1 | 230/230 | 229/229 | 801 | 106.1798 | 105.18 | P2_1 | 'PL_48_P21_102618_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST79 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 90.4412 | 105.12 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST80 | 207915 | GLBR | 208120 | SU10 | 2 | 230/230 | 229/229 | 801 | 106.0924 | 105.11 | Line_FB | 'PL_08_P42_102683_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST81 | 207915 | GLBR | 208120 | SU10 | 2 | 230/230 | 229/229 | 801 | 106.0924 | 105.11 | Line_FB | 'PL_08_P42_101955_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST82 | 207915 | GLBR | 208120 | SU10 | 2 | 230/230 | 229/229 | 801 | 106.0924 | 105.1 | Single | 'PL_08_P12_101740_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST83 | 207915 | GLBR | 208120 | SU10 | 2 | 230/230 | 229/229 | 801 | 106.0924 | 105.1 | Line_FB | 'PL_08_P42_102684_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST84 | 207915 | GLBR | 208120 | SU10 | 2 | 230/230 | 229/229 | 801 | 106.0924 | 105.1 | P2_1 | 'PL_08_P21_102680_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST85 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 98.6458 | 104.99 | Single | 'AEP_P1-2_#5809_1984_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST86 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 100.6618 | 104.92 | Line_FB | 'ATSI_P2-3_OES-138-023T_SRT-SL' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST87 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 100.7353 | 104.88 | Single | 'ATSI_P1-2_OES-138-935TB_SRT-A' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST88 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 100.7353 | 104.88 | Line_FB | 'ATSI_P2-3_OES-138-024AT_SRT-A' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST89 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 115.1064 | 122.84 | P2_1 | '243540 05MCCOMB 138 246662 05MCCMBEQ2 1.00 2_SRT-A' | 47/47/47/47 | Yes
2025W1-N1-ST90 | 243540 | 05MCCOMB | 246661 | 05MCCMBEQ1 | 1 | 138/1 | 205/205 | 47 | 114.8936 | 122.84 | P2_1 | '246663 05MCCOMB L 13.8 246662 05MCCMBEQ2 1.00 2_SRT-A' | 47/47/47/47 | Yes
2025W1-N1-ST91 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 94.3388 | 104.32 | Line_FB | 'ATSI_P2-3_OES-138-048_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST92 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 2 | 138/138 | 202/202 | 242 | 94.3388 | 104.32 | Bus | 'ATSI_P2-2_OES-138-002_SRT-A' | 200 / 242 / 226 / 286 | Yes
2025W1-N1-ST93 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | N/A | 103.54 | Bus | 'ATSI_P2-2_OES-138-055T_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST94 | 238703 | 02ESPRNG | 240710 | 02MELISSA | 1 | 138/138 | 202/202 | 229 | N/A | 103.46 | Line_FB | 'ATSI_P2-3_OES-138-0208BT_SRT-A' | 200 / 242 / 226 / 286 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST95 | 239278 | 02BRDVIE | 238703 | 02ESPRNG | 1 | 138/138 | 202/202 | 192 | 99.0625 | 103.42 | Tower | 'ATSI_P7-1_OES-138-066_SRT-A' | 160 / 192 / 180 / 228 | Yes
2025W1-N1-ST96 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138/138 | 205/205 | 173 | 98.5549 | 111.5 | Line_FB | 'AEP_P4_#7445_05MARYSV 765_B_SRT-A' | 131/173/136/178 | Yes
2025W1-N1-ST97 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 662.7 | 101.6297 | 102.6064 | Single | 'DVP_P1-2: LN 567_SRT-A' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST98 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138/138 | 205/205 | 173 | 95.3757 | 104.52 | Tower | 'AEP_P7-1_#17439___SRT-A' | 131/173/136/178 | Yes
2025W1-N1-ST99 | 207915 | GLBR | 208120 | SU10 | 1 | 230/230 | 229/229 | 801 | 103.0087 | 102.04 | Line_FB | 'PL_48_P42_103291_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST100 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138/138 | 205/205 | 173 | 95.6647 | 104.33 | Line_FB | 'AEP_P4_#9653_05GAY 138_102_SRT-A' | 131/173/136/178 | Yes
2025W1-N1-ST101 | 243548 | 05MOUND ST | 243876 | 05ST.CXX | 1 | 138/138 | 205/205 | 173 | 93.3526 | 102.43 | Line_FB | 'AEP_P4_#10715_05COLE 345_C_SRT-A' | 131/173/136/178 | Yes
2025W1-N1-ST102 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 163 | 103.0061 | 101.55 | Single | 'BASE CASE' | 163/200/201/220 | Yes
2025W1-N1-ST103 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 102.15 | 101.42 | Single | 'DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST104 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 102.1 | 101.27 | Line_FB | 'AEP_P4_#8122_05BEATTY 345_302W_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST105 | 208120 | SU10 | 208113 | SUSQ | 2 | 230/230 | 229/229 | 1079 | 100.8063 | 101.19 | Line_FB | 'PL_48_P42_000438_SRT-A' | 647/801/746/903 | Yes
2025W1-N1-ST106 | 208120 | SU10 | 208113 | SUSQ | 1 | 230/230 | 229/229 | 1079 | 100.8063 | 101.19 | Tower | 'PL_48_P71_102649_SRT-A' | 647/801/746/903 | Yes
2025W1-N1-ST107 | 253026 | 09GREENE | 241968 | AD1-140 TAP | 1 | 138/138 | 209/202 | 282 | 93.8298 | 101.12 | Line_FB | 'ATSI_P2-3_OES-138-060H_SRT-A' | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST108 | 241968 | AD1-140 TAP | 238623 | 02CLARK | 1 | 138/138 | 202/202 | 282 | 99.1489 | 101.09 | Line_FB | 'AEP_P4_#7445_05MARYSV 765_B_SRT-A' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST109 | 253085 | 09URBANA | 239278 | 02BRDVIE | 1 | 138/138 | 209/202 | 272 | 97.2426 | 100.94 | Tower | 'ATSI_P7-1_OES-138-065T_SRT-A' | Dayton: 221/272/301/330 ATSI: 278/339/315/401 | Yes
2025W1-N1-ST110 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 99.617 | 100.91 | Tower | 'DVP_P7-1: LN 2127-216_SRT-S' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
2025W1-N1-ST111 | 238623 | 02CLARK | 241968 | AD1-140 TAP | 1 | 138/138 | 202/202 | 233 | 100.3863 | 100.86 | Single | 'BASE CASE' | 233 / 282 / 263 / 333 | Yes |  | Overlap FE EOL candidate
2025W1-N1-ST112 | 208113 | SUSQ | 207972 | TOMH | 2 | 230/230 | 229/229 | 843 | 100.344 | 100.79 | Tower | 'PL_48_P71_103319_SRT-A' | Summer Rate 1: 647MVA Summer Rate 2: 801MVA Winter Rate 1: 746MVA Winter Rate 2: 903MVA | Yes
2025W1-N1-ST113 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 101.35 | 100.53 | Single | 'AEP_P1-2_#18134_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST114 | 253005 | 09BATH | 253085 | 09URBANA | 1 | 138/138 | 209/209 | 200 | 101.35 | 100.53 | P2_1 | '243453 05BEATTY 345 289114 05BIG PLAIN 345 1_SRT-A' | 163/200/201/220 | Yes
2025W1-N1-ST115 | 314287 | 6CHESTF B | 314276 | 6BASIN | 1 | 230/230 | 345/345 | 705 | 98.766 | 100.06 | Tower | 'DVP_P7-1: LN 211-228_SRT-S' | 705/705/811:782/782/899:769/769/884 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | Yes
Note on J12: New Rating is used. Original rating is 705.0
Note on J16: New Rating is used. Original rating is 705.0
Note on J39: New Rating is used. Original rating is 705.0
Note on J102: New Rating is used. Original rating is 705.0

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Summer 2030 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025W1-N1-SVM1 | 208072 | SIEG | 230 | 229 | 0.90945 | 1.0071 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM2 | 207969 | TRES | 230 | 229 | 0.8277 | 1.0017 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM3 | 207967 | LOFT | 230 | 229 | 0.82266 | 0.9976 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM4 | 207966 | BWAY | 230 | 229 | 0.8262 | 1.0018 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM5 | 207963 | SLYK | 230 | 229 | 0.8264 | 1.002 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM6 | 207960 | EPAL TR2 | 230 | 229 | 0.88207 | 1.0082 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM7 | 207959 | EPAL TR1 | 230 | 229 | 0.88228 | 1.0082 | 0.92 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVM8 | 241988 | AE2-217_MAIN | 138 | 202 | 0.91061 | 0.95082 | 0.92 | Single | AEP_P1-2_#5809_1984_SRT-A | Yes
2025W1-N1-SVM9 | 241987 | AE2-217_POI | 138 | 202 | 0.91057 | 0.95078 | 0.92 | Single | AEP_P1-2_#5809_1984_SRT-A | Yes
2025W1-N1-SVM10 | 241987 | AE2-217_POI | 138 | 202 | 0.75209 | 0.95078 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM11 | 241987 | AE2-217_POI | 138 | 202 | 0.91057 | 0.95078 | 0.92 | Line_FB | AEP_P4_#5809_05BEATTY 138_5W_SRT-A | Yes
2025W1-N1-SVM12 | 241987 | AE2-217_POI | 138 | 202 | 0.86928 | 0.95078 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM13 | 241987 | AE2-217_POI | 138 | 202 | 0.91049 | 0.95078 | 0.92 | Line_FB | AEP_P4_#9530_05BEATTY 138_5C_SRT-A | Yes
2025W1-N1-SVM14 | 241987 | AE2-217_POI | 138 | 202 | 0.9185 | 0.95078 | 0.92 | Bus | ATSI_P2-2_OES-138-002_SRT-A | Yes
2025W1-N1-SVM15 | 241987 | AE2-217_POI | 138 | 202 | 0.91829 | 0.95078 | 0.92 | Bus | ATSI_P2-2_OES-138-054_SRT-A | Yes
2025W1-N1-SVM16 | 241952 | 02DEERCREEK | 138 | 202 | 0.88304 | 0.97209 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM17 | 240710 | 02MELISSA | 138 | 202 | 0.91812 | 0.94604 | 0.92 | Single | ATSI_P1-2_OES-138-935TB_SRT-A | Yes
2025W1-N1-SVM18 | 240710 | 02MELISSA | 138 | 202 | 0.9075 | 0.94604 | 0.92 | Single | AEP_P1-2_#5809_1984_SRT-A | Yes
2025W1-N1-SVM19 | 240710 | 02MELISSA | 138 | 202 | 0.91338 | 0.94604 | 0.92 | Single | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Yes
2025W1-N1-SVM20 | 240710 | 02MELISSA | 138 | 202 | 0.72573 | 0.94604 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM21 | 240710 | 02MELISSA | 138 | 202 | 0.9075 | 0.94604 | 0.92 | Line_FB | AEP_P4_#5809_05BEATTY 138_5W_SRT-A | Yes
2025W1-N1-SVM22 | 240710 | 02MELISSA | 138 | 202 | 0.85722 | 0.94604 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM23 | 240710 | 02MELISSA | 138 | 202 | 0.90742 | 0.94604 | 0.92 | Line_FB | AEP_P4_#9530_05BEATTY 138_5C_SRT-A | Yes
2025W1-N1-SVM24 | 240710 | 02MELISSA | 138 | 202 | 0.90938 | 0.94604 | 0.92 | Bus | ATSI_P2-2_OES-138-002_SRT-A | Yes
2025W1-N1-SVM25 | 240710 | 02MELISSA | 138 | 202 | 0.91943 | 0.94604 | 0.92 | Bus | ATSI_P2-2_OES-138-003_SRT-A | Yes
2025W1-N1-SVM26 | 240710 | 02MELISSA | 138 | 202 | 0.91488 | 0.94604 | 0.92 | Bus | ATSI_P2-2_OES-138-054_SRT-A | Yes
2025W1-N1-SVM27 | 240710 | 02MELISSA | 138 | 202 | 0.91338 | 0.94604 | 0.92 | Bus | URBANA_138KV_W_SRT-A | Yes
2025W1-N1-SVM28 | 240710 | 02MELISSA | 138 | 202 | 0.91504 | 0.94604 | 0.92 | Tower | ATSI_P7-1_OES-138-065T_SRT-A | Yes
2025W1-N1-SVM29 | 240709 | 02N TITUS | 138 | 202 | 0.91827 | 0.94613 | 0.92 | Single | ATSI_P1-2_OES-138-935TB_SRT-A | Yes
2025W1-N1-SVM30 | 240709 | 02N TITUS | 138 | 202 | 0.90754 | 0.94613 | 0.92 | Single | AEP_P1-2_#5809_1984_SRT-A | Yes
2025W1-N1-SVM31 | 240709 | 02N TITUS | 138 | 202 | 0.91359 | 0.94613 | 0.92 | Single | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Yes
2025W1-N1-SVM32 | 240709 | 02N TITUS | 138 | 202 | 0.72657 | 0.94613 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM33 | 240709 | 02N TITUS | 138 | 202 | 0.90754 | 0.94613 | 0.92 | Line_FB | AEP_P4_#5809_05BEATTY 138_5W_SRT-A | Yes
2025W1-N1-SVM34 | 240709 | 02N TITUS | 138 | 202 | 0.85756 | 0.94613 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM35 | 240709 | 02N TITUS | 138 | 202 | 0.90746 | 0.94613 | 0.92 | Line_FB | AEP_P4_#9530_05BEATTY 138_5C_SRT-A | Yes
2025W1-N1-SVM36 | 240709 | 02N TITUS | 138 | 202 | 0.90963 | 0.94613 | 0.92 | Bus | ATSI_P2-2_OES-138-002_SRT-A | Yes
2025W1-N1-SVM37 | 240709 | 02N TITUS | 138 | 202 | 0.91964 | 0.94613 | 0.92 | Bus | ATSI_P2-2_OES-138-003_SRT-A | Yes
2025W1-N1-SVM38 | 240709 | 02N TITUS | 138 | 202 | 0.91493 | 0.94613 | 0.92 | Bus | ATSI_P2-2_OES-138-054_SRT-A | Yes
2025W1-N1-SVM39 | 240709 | 02N TITUS | 138 | 202 | 0.91359 | 0.94613 | 0.92 | Bus | URBANA_138KV_W_SRT-A | Yes
2025W1-N1-SVM40 | 240709 | 02N TITUS | 138 | 202 | 0.9152 | 0.94613 | 0.92 | Tower | ATSI_P7-1_OES-138-065T_SRT-A | Yes
2025W1-N1-SVM41 | 240706 | 02NATIONAL | 138 | 202 | 0.82973 | 0.96001 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM42 | 240706 | 02NATIONAL | 138 | 202 | 0.90358 | 0.96001 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM43 | 240637 | 02URECMITCHL | 138 | 202 | 0.91919 | 0.97929 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM44 | 239278 | 02BRDVIE | 138 | 202 | 0.90536 | 0.97859 | 0.92 | Line_FB | ATSI_P2-3_OES-138-0208BT_SRT-A | Yes
2025W1-N1-SVM45 | 239278 | 02BRDVIE | 138 | 202 | 0.87994 | 0.97859 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM46 | 239278 | 02BRDVIE | 138 | 202 | 0.9048 | 0.97859 | 0.92 | Bus | ATSI_P2-2_OES-138-055T_SRT-A | Yes
2025W1-N1-SVM47 | 239278 | 02BRDVIE | 138 | 202 | 0.89591 | 0.97859 | 0.92 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes
2025W1-N1-SVM48 | 238908 | 02LONDON | 138 | 202 | 0.91172 | 0.95506 | 0.92 | Single | AEP_P1-2_#5809_1984_SRT-A | Yes
2025W1-N1-SVM49 | 238908 | 02LONDON | 138 | 202 | 0.91995 | 0.95506 | 0.92 | Line_FB | ATSI_P2-3_OES-138-0607A_SRT-A | Yes
2025W1-N1-SVM50 | 238908 | 02LONDON | 138 | 202 | 0.79653 | 0.95506 | 0.92 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVM51 | 238908 | 02LONDON | 138 | 202 | 0.91172 | 0.95506 | 0.92 | Line_FB | AEP_P4_#5809_05BEATTY 138_5W_SRT-A | Yes
2025W1-N1-SVM52 | 238908 | 02LONDON | 138 | 202 | 0.8885 | 0.95506 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM53 | 238908 | 02LONDON | 138 | 202 | 0.91164 | 0.95506 | 0.92 | Line_FB | AEP_P4_#9530_05BEATTY 138_5C_SRT-A | Yes
2025W1-N1-SVM54 | 238703 | 02ESPRNG | 138 | 202 | 0.91932 | 0.95568 | 0.92 | Single | AEP_P1-2_#5809_1984_SRT-A | Yes
2025W1-N1-SVM55 | 238703 | 02ESPRNG | 138 | 202 | 0.85891 | 0.95568 | 0.92 | Line_FB | ATSI_P2-3_OES-138-0208BT_SRT-A | Yes
2025W1-N1-SVM56 | 238703 | 02ESPRNG | 138 | 202 | 0.91932 | 0.95568 | 0.92 | Line_FB | AEP_P4_#5809_05BEATTY 138_5W_SRT-A | Yes
2025W1-N1-SVM57 | 238703 | 02ESPRNG | 138 | 202 | 0.8652 | 0.95568 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM58 | 238703 | 02ESPRNG | 138 | 202 | 0.91923 | 0.95568 | 0.92 | Line_FB | AEP_P4_#9530_05BEATTY 138_5C_SRT-A | Yes
2025W1-N1-SVM59 | 238703 | 02ESPRNG | 138 | 202 | 0.85826 | 0.95568 | 0.92 | Bus | ATSI_P2-2_OES-138-055T_SRT-A | Yes
2025W1-N1-SVM60 | 238703 | 02ESPRNG | 138 | 202 | 0.84551 | 0.95568 | 0.92 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes
2025W1-N1-SVM61 | 238623 | 02CLARK | 138 | 202 | 0.89946 | 0.97825 | 0.92 | Line_FB | ATSI_P2-3_OES-138-0208BT_SRT-A | Yes
2025W1-N1-SVM62 | 238623 | 02CLARK | 138 | 202 | 0.886 | 0.97825 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM63 | 238623 | 02CLARK | 138 | 202 | 0.89888 | 0.97825 | 0.92 | Bus | ATSI_P2-2_OES-138-055T_SRT-A | Yes
2025W1-N1-SVM64 | 238623 | 02CLARK | 138 | 202 | 0.88934 | 0.97825 | 0.92 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes
2025W1-N1-SVM65 | 238529 | 02AIRPK+ | 138 | 202 | 0.88971 | 0.97293 | 0.92 | Line_FB | ATSI_P2-3_OES-138-0208BT_SRT-A | Yes
2025W1-N1-SVM66 | 238529 | 02AIRPK+ | 138 | 202 | 0.88103 | 0.97293 | 0.92 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVM67 | 238529 | 02AIRPK+ | 138 | 202 | 0.88911 | 0.97293 | 0.92 | Bus | ATSI_P2-2_OES-138-055T_SRT-A | Yes
2025W1-N1-SVM68 | 238529 | 02AIRPK+ | 138 | 202 | 0.87886 | 0.97293 | 0.92 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Summer 2030 Case)
FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment
2025-W1-N1-SVD1 | 314621 | 3WEYRHAEUSER | 115 | 345 | 0.91301 | 1.0186 | 10.559 | Line_FB | DVP_P4-2: 2034T2126_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N1-SVD2 | 314614 | 3TRWBRDG2 | 115 | 345 | 0.91575 | 1.0202 | 10.442 | Line_FB | DVP_P4-2: 2034T2126_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N1-SVD3 | 314613 | 3TRWBRDG | 115 | 345 | 0.91364 | 1.0199 | 10.631 | Line_FB | DVP_P4-2: 2034T2126_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025W1-N1-SVD4 | 208072 | SIEG | 230 | 229 | 0.91896 | 1.0071 | 8.814 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD5 | 207969 | TRES | 230 | 229 | 0.84183 | 1.0017 | 15.986 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD6 | 207967 | LOFT | 230 | 229 | 0.8369 | 0.9976 | 16.07 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD7 | 207966 | BWAY | 230 | 229 | 0.84045 | 1.0018 | 16.14 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD8 | 207963 | SLYK | 230 | 229 | 0.84065 | 1.002 | 16.136 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD9 | 207960 | EPAL TR2 | 230 | 229 | 0.89285 | 1.0082 | 11.532 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD10 | 207959 | EPAL TR1 | 230 | 229 | 0.89304 | 1.0082 | 11.513 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD11 | 241987 | AE2-217_POI | 138 | 202 | 0.75854 | 0.95078 | 19.224 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVD12 | 240710 | 02MELISSA | 138 | 202 | 0.73182 | 0.94604 | 21.422 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVD13 | 240709 | 02N TITUS | 138 | 202 | 0.73268 | 0.94613 | 21.345 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVD14 | 240706 | 02NATIONAL | 138 | 202 | 0.83516 | 0.96001 | 12.485 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVD15 | 239278 | 02BRDVIE | 138 | 202 | 0.86998 | 0.97859 | 10.861 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVD16 | 238908 | 02LONDON | 138 | 202 | 0.8037 | 0.95506 | 15.136 | Line_FB | ATSI_P2-4_OES-138-047_SRT-A | Yes
2025W1-N1-SVD17 | 238703 | 02ESPRNG | 138 | 202 | 0.84684 | 0.95568 | 10.884 | Line_FB | ATSI_P2-3_OES-138-0208BT_SRT-A | Yes
2025W1-N1-SVD18 | 238703 | 02ESPRNG | 138 | 202 | 0.8475 | 0.95568 | 10.818 | Bus | ATSI_P2-2_OES-138-055T_SRT-A | Yes
2025W1-N1-SVD19 | 238703 | 02ESPRNG | 138 | 202 | 0.83267 | 0.95568 | 12.301 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes
2025W1-N1-SVD20 | 238623 | 02CLARK | 138 | 202 | 0.87718 | 0.97825 | 10.107 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVD21 | 238529 | 02AIRPK+ | 138 | 202 | 0.87227 | 0.97293 | 10.066 | Line_FB | ATSI_P2-3_OES-138-060H_SRT-A | Yes
2025W1-N1-SVD22 | 238529 | 02AIRPK+ | 138 | 202 | 0.86777 | 0.97293 | 10.516 | Tower | ATSI_P7-1_OES-138-066A_SRT-A | Yes
2025W1-N1-SVD23 | 211995 | YATE 1 | 69 | 229 | 0.88702 | 0.98289 | 9.587 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD24 | 211994 | YATE 2 | 69 | 229 | 0.88437 | 0.98208 | 9.771 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD25 | 211988 | WYVA TP1 | 69 | 229 | 0.89085 | 0.98797 | 9.712 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD26 | 211987 | WYVA TP2 | 69 | 229 | 0.87887 | 0.97724 | 9.837 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD27 | 211986 | WYVA 2 | 69 | 229 | 0.87874 | 0.97713 | 9.839 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD28 | 211985 | WYVA 1 | 69 | 229 | 0.89073 | 0.98786 | 9.713 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD29 | 211951 | WEIS TP1 | 69 | 229 | 0.88445 | 0.99677 | 11.232 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD30 | 211950 | WEIS TP2 | 69 | 229 | 0.87721 | 0.99041 | 11.32 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD31 | 211949 | WEIS | 69 | 229 | 0.86253 | 0.97842 | 11.589 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD32 | 211837 | SCRA 1 | 69 | 229 | 0.86599 | 0.95436 | 8.837 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD33 | 211789 | PIRI 1 | 69 | 229 | 0.8911 | 0.98819 | 9.709 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD34 | 211788 | PIRI 2 | 69 | 229 | 0.88568 | 0.98334 | 9.766 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD35 | 211781 | MUND 2 | 69 | 229 | 0.87878 | 0.97716 | 9.838 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD36 | 211780 | MUND 1 | 69 | 229 | 0.85995 | 0.95806 | 9.811 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD37 | 211760 | OWIL 1 | 69 | 229 | 0.88763 | 0.9843 | 9.667 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD38 | 211759 | OWIL 2 | 69 | 229 | 0.89033 | 0.98739 | 9.706 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD39 | 211758 | OWIL TP1 | 69 | 229 | 0.88915 | 0.98563 | 9.648 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD40 | 211757 | OWIL TP2 | 69 | 229 | 0.89235 | 0.98924 | 9.689 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD41 | 211752 | AVOC TI1 | 69 | 229 | 0.87533 | 0.96746 | 9.213 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD42 | 211728 | MTGE 1 | 69 | 229 | 0.87694 | 0.96958 | 9.264 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD43 | 211727 | MTGE 2 | 69 | 229 | 0.86971 | 0.96829 | 9.858 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD44 | 211719 | MINO 2 | 69 | 229 | 0.86517 | 0.96353 | 9.836 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD45 | 211718 | MINO 1 | 69 | 229 | 0.87018 | 0.96069 | 9.051 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD46 | 211697 | LEHI TP | 69 | 229 | 0.86273 | 0.97834 | 11.561 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD47 | 211696 | LEHI | 69 | 229 | 0.8612 | 0.97699 | 11.579 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD48 | 211654 | JENK | 69 | 229 | 0.89344 | 0.99023 | 9.679 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD49 | 211611 | HIRU | 69 | 229 | 0.88679 | 0.99912 | 11.233 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD50 | 211542 | GEOR TP1 | 69 | 229 | 0.87186 | 0.96851 | 9.665 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD51 | 211541 | GEOR TP2 | 69 | 229 | 0.89188 | 0.9888 | 9.692 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD52 | 211538 | GEOR 1 | 69 | 229 | 0.86272 | 0.96054 | 9.782 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD53 | 211537 | GEOR 2 | 69 | 229 | 0.87625 | 0.97489 | 9.864 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD54 | 211483 | EMOU TP2 | 69 | 229 | 0.89184 | 0.98876 | 9.692 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD55 | 211482 | EMOU 2 | 69 | 229 | 0.89171 | 0.98864 | 9.693 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD56 | 211481 | EMOU 1 | 69 | 229 | 0.88487 | 0.98095 | 9.608 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD57 | 211480 | EMOU TP1 | 69 | 229 | 0.88494 | 0.981 | 9.606 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD58 | 211456 | DUPO 2 | 69 | 229 | 0.87471 | 0.97309 | 9.838 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD59 | 211455 | DUPO 1 | 69 | 229 | 0.88105 | 0.975 | 9.395 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD60 | 211452 | DUPO DC | 69 | 229 | 0.8747 | 0.97308 | 9.838 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD61 | 211446 | CHRI TP | 69 | 229 | 0.88743 | 0.99968 | 11.225 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD62 | 211432 | CEAV 1 | 69 | 229 | 0.86599 | 0.95437 | 8.838 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD63 | 211431 | CEAV 2 | 69 | 229 | 0.86128 | 0.95926 | 9.798 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD64 | 211427 | CARB | 69 | 229 | 0.88841 | 1.0005 | 11.211 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD65 | 211392 | BECR TP2 | 69 | 229 | 0.89186 | 0.98878 | 9.692 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD66 | 211382 | BECR TP1 | 69 | 229 | 0.88058 | 0.97606 | 9.548 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD67 | 211381 | BECR NUG | 69 | 229 | 0.88063 | 0.97585 | 9.522 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD68 | 211380 | BCRK | 69 | 229 | 0.87969 | 0.97501 | 9.532 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD69 | 211379 | BELT | 69 | 229 | 0.88966 | 1.0016 | 11.192 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD70 | 211377 | BELT 2 | 69 | 229 | 0.87722 | 0.99042 | 11.32 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD71 | 211376 | BELT 1 | 69 | 229 | 0.88964 | 1.0016 | 11.192 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD72 | 211373 | AVOC TI2 | 69 | 229 | 0.86863 | 0.96716 | 9.853 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD73 | 211366 | ASHF TP2 | 69 | 229 | 0.89792 | 0.97825 | 8.033 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD74 | 211347 | WHCE | 69 | 229 | 0.90146 | 0.98306 | 8.16 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD75 | 211346 | WHCE 2 | 69 | 229 | 0.90146 | 0.98306 | 8.16 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD76 | 211345 | WHCE 1 | 69 | 229 | 0.90234 | 0.98388 | 8.154 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD77 | 211337 | WGAT 2 | 69 | 229 | 0.86696 | 0.95322 | 8.626 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD78 | 211336 | WGAT 1 | 69 | 229 | 0.86857 | 0.95542 | 8.685 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD79 | 211273 | TREI DC | 69 | 229 | 0.90185 | 0.98186 | 8.001 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD80 | 211272 | TREI TP2 | 69 | 229 | 0.90314 | 0.98426 | 8.112 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD81 | 211270 | TREI | 69 | 229 | 0.90046 | 0.98059 | 8.013 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD82 | 211268 | TREI TP1 | 69 | 229 | 0.90185 | 0.98186 | 8.001 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD83 | 211193 | SSLA 2 | 69 | 229 | 0.90073 | 0.98153 | 8.08 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD84 | 211160 | SIEG | 69 | 229 | 0.90442 | 0.9857 | 8.128 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD85 | 211062 | PSPA TP2 | 69 | 229 | 0.89805 | 0.9784 | 8.035 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD86 | 211057 | PONO 1 | 69 | 229 | 0.86807 | 0.95507 | 8.7 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD87 | 211056 | PNWG TP2 | 69 | 229 | 0.86892 | 0.95495 | 8.603 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD88 | 211055 | PNWG TP1 | 69 | 229 | 0.87021 | 0.95684 | 8.663 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD89 | 211054 | PONO 2 | 69 | 229 | 0.86672 | 0.95303 | 8.631 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD90 | 211052 | APRF TP | 69 | 229 | 0.86814 | 0.95513 | 8.699 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD91 | 211051 | APRF | 69 | 229 | 0.86814 | 0.95513 | 8.699 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD92 | 211031 | PAZI | 69 | 229 | 0.88216 | 0.99504 | 11.288 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD93 | 211030 | PAZI 2 | 69 | 229 | 0.88216 | 0.99504 | 11.288 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD94 | 211029 | PAZI 1 | 69 | 229 | 0.88062 | 0.99325 | 11.263 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD95 | 211022 | PALM 2 | 69 | 229 | 0.88404 | 0.99712 | 11.308 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD96 | 211021 | PALM 1 | 69 | 229 | 0.88084 | 0.99346 | 11.262 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD97 | 210972 | NBET 2 | 69 | 229 | 0.8738 | 0.95924 | 8.544 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD98 | 210971 | NBET 1 | 69 | 229 | 0.87479 | 0.96074 | 8.595 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD99 | 210921 | BECR DC | 69 | 229 | 0.88058 | 0.97605 | 9.547 | Line_FB | PL_40_P43_101647_SRT-A | Yes
2025W1-N1-SVD100 | 210914 | MICK TP2 | 69 | 229 | 0.89733 | 0.97943 | 8.21 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD101 | 210913 | MICK 2 | 69 | 229 | 0.89669 | 0.97886 | 8.217 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD102 | 210912 | MICK 1 | 69 | 229 | 0.89747 | 0.97958 | 8.211 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD103 | 210911 | MICK TP1 | 69 | 229 | 0.89813 | 0.98016 | 8.203 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD104 | 210829 | LIGA 1 | 69 | 229 | 0.87979 | 0.9925 | 11.271 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD105 | 210828 | LIGA 2 | 69 | 229 | 0.88007 | 0.99275 | 11.268 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD106 | 210827 | LIGA TAP | 69 | 229 | 0.88027 | 0.99292 | 11.265 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD107 | 210601 | EPAL | 69 | 229 | 0.88038 | 0.99301 | 11.263 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD108 | 210570 | DRAG 2 | 69 | 229 | 0.90204 | 0.98358 | 8.154 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD109 | 210569 | DRAG 1 | 69 | 229 | 0.9027 | 0.98419 | 8.149 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD110 | 210568 | DRAG | 69 | 229 | 0.9027 | 0.98419 | 8.149 | Tower | PL_60_P71_000890_SRT-A | Yes
2025W1-N1-SVD111 | 210405 | EPHA TI2 | 69 | 229 | 0.89981 | 0.98041 | 8.06 | Tower | PL_60_P71_000890_SRT-A | Yes

## N-1 Load Drop
PJM N-1 Load Drop Result (Winter 2030 Case)
FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
N/A | DVP_P1-2: LN 2140_SRT-A | Single | 345 | 0 | 419.3 | 419.3 | No | To be adressed through supplemental process.
N/A | DVP_P4-2: 214052_SRT-A | Line_FB | 345 | 0 | 419.3 | 419.3 | No | To be adressed through supplemental process.
N/A | DVP_P4-2: 2094T2140_SRT-A | Line_FB | 345 | 0 | 419.3 | 419.3 | No | To be adressed through supplemental process.
N/A | DVP_P4-2: 214042_SRT-A | Line_FB | 345 | 0 | 419.3 | 419.3 | No | To be adressed through supplemental process.
N/A | DVP_P7-1: LN 2140-2176_SRT-A | Tower | 345 | 0 | 419.3 | 419.3 | No | To be adressed through supplemental process.
N/A | DVP_P7-1: LN 2140-535_SRT-A | Tower | 345, 201 | 0 | 419.3 | 419.3 | No | To be adressed through supplemental process.