## Thermal
PJM N-1-1 Thermal Result (Summer 2030 Case)
FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Base (MVA) | Rate Cont (MVA) | Contingency 1 | Contingency 2 | Initial AC %Loading | SCD AC %Loading | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025-W1-N11-ST1 | 204540 | 27JACKSON | 204548 | 27N.HANOVR | 1 | 115 | 227 | 133 | 160 | ME_P1-2_ME-115-017_SRT-A | ME_P1-2_ME-115-027B_SRT-A | 115.05 | 115.05 | 133/160/150/190 SLN/SLE/WN/WE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST2 | 204540 | 27JACKSON | 204548 | 27N.HANOVR | 1 | 115 | 227 | 133 | 160 | ME_P1-2_ME-115-027B_SRT-A | ME_P1-2_ME-115-017_SRT-A | 115.04 | 115.04 | 133/160/150/190 SLN/SLE/WN/WE | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST3 | 221047 | GREEN553 | 221855 | CONSTITUTION | 1 | 115 | 232 | 140 | 158 | BG_P1_PORTCOV_GRN ST 554_SRT-A | BG_P1_110552_SRT-A | 116.96 | 110.14 | 140/158/187/203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST4 | 221048 | GREEN554 | 221855 | CONSTITUTION | 1 | 115 | 232 | 140 | 158 | BG_P1_PORTCOV_GRN ST 553_SRT-A | BG_P1_110552_SRT-A | 118.49 | 109.38 | 140/158/187/203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST5 | 221048 | GREEN554 | 221855 | CONSTITUTION | 1 | 115 | 232 | 140 | 158 | BG_P1_110552_SRT-A | BG_P1_PORTCOV_GRN ST 553_SRT-A | 118.49 | 109.16 | 140/158/187/203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST6 | 221047 | GREEN553 | 221855 | CONSTITUTION | 1 | 115 | 232 | 140 | 158 | BG_P1_110552_SRT-A | BG_P1_PORTCOV_GRN ST 554_SRT-A | 116.97 | 107.74 | 140/158/187/203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST7 | 235502 | 01REDBUD | 235519 | 01W WINC | 1 | 138 | 201 | 221 | 268 | AP_P1-2_PE-138-035_SRT-A | Base Case | 106.73 | 106.74 | 221/268/250/317 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST8 | 235457 | 01DTG | 235474 | 01GREENW | 1 | 138 | 201 | 278 | 339 | AP_P1-2_PE-138-056_SRT-A | Base Case | 106.64 | 106.64 | 278/339/315/401 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
N/A | 235461 | 01SAGE | 235532 | 01ALIGN_DATA | 1 | 230 | 201 | 617 | 754 | AP_P1-2_PE-230-007B_SRT-A | Base Case | 110.3 | 105.1 | 617/754/699/894 | No | To be adressed through supplemental process. | Overlap FE EOL candidate
N/A | 235514 | 01QUANTUM400 | 235532 | 01ALIGN_DATA | 2 | 230 | 201 | 617 | 754 | AP_P1-2_PE-230-008A_SRT-A | Base Case | 109.03 | 103.98 | 617/754/699/894 | No | To be adressed through supplemental process. | Overlap FE EOL candidate
2025-W1-N11-ST9 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 292 | 314 | AP_P1-2_PE-138-035_SRT-A | Base Case | 103.57 | 103.58 | 308/376/349/445 | No | Substation Equipment Exclusion
2025-W1-N11-ST10 | 314576 | 3FIVE PT | 314622 | 3WHARTON | 1 | 115 | 345 | 79 | 79 | DVP_P1-2: LN 2126_SRT-A | DVP_P1-2: LN 168_SRT-A | 102.2 | 102.19 | 79/79/91:100/100/115:96/96/111 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST11 | 314576 | 3FIVE PT | 314622 | 3WHARTON | 1 | 115 | 345 | 79 | 79 | DVP_P1-2: LN 168_SRT-A | DVP_P1-2: LN 2126_SRT-A | 101.94 | 101.94 | 79/79/91:100/100/115:96/96/111 (SN/SE/SLD:WN/WE/WLD:LLN/LLE/LLLD) | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST12 | 271436 | PINE ; B | 271736 | ITASCA ;12 | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_138-L10109_R-N_SRT-A | Base Case | 107.93 | 101.68 | 351/449/351/449 (SN/SE/WN/WE) | No | To be adressed through supplemental process.
2025-W1-N11-ST13 | 221048 | GREEN554 | 221855 | CONSTITUTION | 1 | 115 | 232 | 140 | 158 | BG_P1_NEAST_230-3_SRT-A | BG_P1_PORTCOV_GRN ST 553_SRT-A | 105.19 | 101.41 | 140/158/187/203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST14 | 221048 | GREEN554 | 221855 | CONSTITUTION | 1 | 115 | 232 | 140 | 158 | BG_P1_NEAST_230-2_SRT-A | BG_P1_PORTCOV_GRN ST 553_SRT-A | 105.12 | 101.34 | 140/158/187/203 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-ST15 | 235483 | 01MDWBRK | 235519 | 01W WINC | 1 | 138 | 201 | 292 | 314 | AP_P1-4_PE-138-056_SRT-A | AP_P1-2_PE-138-035_SRT-A | 101.32 | 101.32 | 308/376/349/445 | No | Substation Equipment Exclusion
2025-W1-N11-ST16 | 271436 | PINE ; B | 271736 | ITASCA ;12 | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_138-L10118_B-N_SRT-A | COMED_P1-2_138-L10109_R-N_SRT-A | 106.96 | 100.6 | 351/449/351/449 (SN/SE/WN/WE) | No | To be adressed through supplemental process.
2025-W1-N11-ST17 | 271436 | PINE ; B | 271736 | ITASCA ;12 | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_138-L10109_R-N_SRT-A | COMED_P1-2_138-L10118_B-N_SRT-A | 106.96 | 100.6 | 351/449/351/449 (SN/SE/WN/WE) | No | To be adressed through supplemental process.
2025-W1-N11-ST18 | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 351 | 449 | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | COMED_P1-2_138-L10117_R-N_SRT-A | 105.18 | 100.41 | 351/449/351/449 (SN/SE/WN/WE) | No | To be adressed through supplemental process.
2025-W1-N11-ST19 | 271437 | PINE ; R | 271737 | ITASCA ;6R | 1 | 138 | 222 | 351 | 449 | COMED_P1-2_138-L10117_R-N_SRT-A | COMED_P1-3_TR81_ELKGR_R-N_SRT-A | 105.18 | 100.38 | 351/449/351/449 (SN/SE/WN/WE) | No | To be adressed through supplemental process.
2025-W1-N11-ST20 | 271436 | PINE ; B | 271736 | ITASCA ;12 | 1 | 138 | 222 | 351 | 449 | COMED_P1-3_TR82_ELKGR_B-N_SRT-A | COMED_P1-2_138-L10118_B-N_SRT-A | 105.99 | 100.24 | 351/449/351/449 (SN/SE/WN/WE) | No | To be adressed through supplemental process.
2025W1-N11-ST21 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 127.78 | 127 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST22 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 127.77 | 120.03 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST23 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 125.08 | 117.91 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST24 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 125.08 | 117.91 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST25 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 159.52 | 158.84 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST26 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 159.52 | 154.4 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST27 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 154.2 | 154.25 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST28 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 154.19 | 152 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST29 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 156.66 | 150.73 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST30 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 156.66 | 150.73 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST31 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 146.47 | 145.75 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST32 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 139.36 | 139.41 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST33 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 139.28 | 139.26 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST34 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 146.4 | 139.22 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST35 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 133.9 | 135.01 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST36 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 133.94 | 134.43 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST37 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 128.27 | 132.43 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST38 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 128.14 | 127.72 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST39 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 125.15 | 127.61 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST40 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 116.16 | 115.46 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST41 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 125.18 | 124.64 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST42 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 123.43 | 123.43 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST43 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 123.17 | 122.91 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST44 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 123.17 | 122.44 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST45 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 116.16 | 108.47 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST46 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 123.39 | 119.46 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST47 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 102.88 | 103.96 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST48 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 102.92 | 103.27 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST49 | 207972 | TOMH | 207977 | HARW | 2 | 230 | 229 | 718 | 843 | PL_48_P12_103306_SRT-A | PL:40:P12:103379 | 143.06 | 117.85 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST50 | 207972 | TOMH | 207977 | HARW | 2 | 230 | 229 | 718 | 843 | PL:40:P12:103379 | PL_48_P12_103306_SRT-A | 143.07 | 117.82 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST51 | 207972 | TOMH | 207977 | HARW | 1 | 230 | 229 | 718 | 843 | PL_48_P12_103315_SRT-A | PL:40:P12:103379 | 142.94 | 117.74 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST52 | 207972 | TOMH | 207977 | HARW | 1 | 230 | 229 | 718 | 843 | PL:40:P12:103379 | PL_48_P12_103315_SRT-A | 142.95 | 117.72 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST53 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 119.01 | 116.89 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST54 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | 120.29 | 115.71 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST55 | 241952 | 02DEERCREEK | 243469 | 05BEATTY | 1 | 138 | 202/205 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 97.68 | 101.97 | ATSI: 200/242/226/286 AEP: N/A (conductor owned by FirstEnergy) | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST56 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 114.78 | 115.21 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST57 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 112.29 | 114.22 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST58 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 119.08 | 114.11 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST59 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 114.71 | 113.89 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST60 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 112.46 | 112.86 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST61 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | 113.52 | 112.62 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST62 | 238529 | 02AIRPK+ | 238703 | 02ESPRNG | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 111.54 | 111.88 | 200/242/226/286 | Yes
2025W1-N11-ST63 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 112.34 | 111.42 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST64 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 112.34 | 111.42 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST65 | 238529 | 02AIRPK+ | 238703 | 02ESPRNG | 1 | 138 | 202 | 200 | 242 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 111.44 | 111.39 | 200/242/226/286 | Yes
2025W1-N11-ST66 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 114.1 | 110.85 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST67 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 110.82 | 110.62 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST68 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 114.75 | 110.45 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST69 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 114.7 | 110.06 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST70 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 106.69 | 109.95 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST71 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 114.14 | 109.8 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST72 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 111.63 | 109.51 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST73 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 108.96 | 109.35 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST74 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 110.81 | 108.44 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST75 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 112.52 | 108.27 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST76 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 107.67 | 108.25 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST77 | 243469 | 05BEATTY | 243540 | 05MCCOMB | 1 | 138 | 205 | 216 | 251 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#18036_SRT-A | 106.99 | 105.74 | 216/259/272/304 | Yes
2025W1-N11-ST78 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 108.13 | 107.83 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST79 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 310 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#10137_570_SRT-A | 102.66 | 102.37 | 223/310/281/349 | Yes
2025W1-N11-ST80 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 108.19 | 107.42 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST81 | 207972 | TOMH | 208113 | SUSQ | 2 | 230 | 229 | 718 | 843 | PL_48_P12_103307_SRT-A | PL:40:P12:103379 | 120.25 | 107.37 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST82 | 207972 | TOMH | 208113 | SUSQ | 2 | 230 | 229 | 718 | 843 | PL:40:P12:103379 | PL_48_P12_103307_SRT-A | 120.25 | 107.28 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST83 | 238908 | 02LONDON | 240709 | 02N TITUS | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 107.91 | 107.03 | 200/242/226/286 | Yes
2025W1-N11-ST84 | 238908 | 02LONDON | 240709 | 02N TITUS | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 107.91 | 107.02 | 200/242/226/286 | Yes
2025W1-N11-ST85 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | 106.88 | 106.94 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST86 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 106.61 | 106.78 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST87 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 233 | 282 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 106 | 106.25 | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST88 | 238908 | 02LONDON | 240709 | 02N TITUS | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 106.36 | 106.17 | 200/242/226/286 | Yes
2025W1-N11-ST89 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 233 | 282 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 105.98 | 106.16 | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST90 | 207972 | TOMH | 208113 | SUSQ | 1 | 230 | 229 | 718 | 843 | PL_48_P12_103307_SRT-A | PL:40:P12:103379 | 118.89 | 106.15 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST91 | 207972 | TOMH | 208113 | SUSQ | 1 | 230 | 229 | 718 | 843 | PL:40:P12:103379 | PL_48_P12_103307_SRT-A | 118.89 | 106.07 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST92 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 105.44 | 106.01 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST93 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 104.52 | 105.98 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST94 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 310 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#18125_SRT-A | 102.66 | 102.23 | 223/310/281/349 | Yes
2025W1-N11-ST95 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 109.54 | 105.59 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST96 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 105.86 | 105.58 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST97 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-034_SRT-A | 108.02 | 105.47 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST98 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | Base Case | 112.41 | 105.39 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST99 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 108.09 | 105.23 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST100 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 106 | 105.13 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST101 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 106 | 105.13 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST102 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 310 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#10137_570_SRT-A | 100.87 | 101.1 | 223/310/281/349 | Yes
2025W1-N11-ST103 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 233 | 282 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 104.18 | 104.81 | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST104 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | AEP_P1-2_#10137_570_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 105.65 | 104.8 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST105 | 238574 | 02BELPT+ | 239134 | 02TANGY | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 104.52 | 104.8 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST106 | 241968 | AD1-140 TAP | 253026 | 09GREENE | 1 | 138 | 202/209 | 233 | 282 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 104.17 | 104.5 | Dayton: 221/272/301/330 ATSI: 233/282/263/333 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST107 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 104.37 | 104.18 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST108 | 238908 | 02LONDON | 240709 | 02N TITUS | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 106.35 | 104.08 | 200/242/226/286 | Yes
2025W1-N11-ST109 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 310 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#18125_SRT-A | 100.87 | 100.94 | 223/310/281/349 | Yes
2025W1-N11-ST110 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 102.75 | 103.95 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST111 | 207972 | TOMH | 208113 | SUSQ | 2 | 230 | 229 | 718 | 843 | PL_48_P12_103307_SRT-A | PL_40_P12_000182_SRT-A | 115.58 | 103.82 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST112 | 207972 | TOMH | 208113 | SUSQ | 2 | 230 | 229 | 718 | 843 | PL_40_P12_000182_SRT-A | PL_48_P12_103307_SRT-A | 115.58 | 103.75 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST113 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 107.64 | 103.72 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST114 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 310 | AEP_P1-2_#10137_570_SRT-A | Base Case | 102.17 | 100.61 | 223/310/281/349 | Yes
2025W1-N11-ST115 | 207972 | TOMH | 208113 | SUSQ | 1 | 230 | 229 | 718 | 843 | PL_48_P12_103307_SRT-A | PL_48_P12_102309_SRT-A | 114.88 | 103.2 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST116 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 108.94 | 103.15 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST117 | 207972 | TOMH | 208113 | SUSQ | 1 | 230 | 229 | 718 | 843 | PL_48_P12_102309_SRT-A | PL_48_P12_103307_SRT-A | 114.88 | 103.12 | Summer Rate 1: 717MVA Summer Rate 2: 843MVA Winter Rate 1: 768MVA Winter Rate 2: 894MVA | Yes
2025W1-N11-ST118 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 112.25 | 103.1 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST119 | 240637 | 02URECMITCHL | 240706 | 02NATIONAL | 1 | 138 | 202 | 233 | 282 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 102.83 | 102.96 | 233/282/263/333 | Yes
2025W1-N11-ST120 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | 104.36 | 102.93 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST121 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 105.82 | 102.75 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST122 | 243485 | 05CLINTO | 243576 | 05ST.CLX | 1 | 138 | 205 | 142 | 174 | AEP_P1-2_#18125_SRT-A | AEP_P1-2_#10137_570_SRT-A | 107.69 | 108.01 | 142/180/139/184 | Yes
2025W1-N11-ST123 | 243485 | 05CLINTO | 243576 | 05ST.CLX | 1 | 138 | 205 | 142 | 174 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#18125_SRT-A | 107.69 | 107.93 | 142/180/139/184 | Yes
2025W1-N11-ST124 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 102.77 | 102.6 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST125 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345 | 205 | 1370 | 1385 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#762_8072_SRT-A | 103.87 | 101.67 | 1385/1385/1750/1750 | Yes
2025W1-N11-ST126 | 243458 | 05HYATT | 290516 | 05CELTIC | 1 | 345 | 205 | 1370 | 1385 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#18134_SRT-A | 103.87 | 101.25 | 1385/1385/1750/1750 | Yes
2025W1-N11-ST127 | 290573 | 05INNOVATION | 288789 | 05INNOVAT2EQ | 2 | 345/1.0 | 205 | 745 | 796 | AEP_P1-3_#17991_05INNOVATION 345_1_SRT-A | AEP_P1-2_#18090_SRT-A | 102.74 | 102.7 | 811/866/918/969 | Yes
2025W1-N11-ST128 | 290254 | 05INNOVATION | 288789 | 05INNOVAT2EQ | 2 | 138/1.0 | 205 | 745 | 796 | AEP_P1-3_#17991_05INNOVATION 345_1_SRT-A | AEP_P1-2_#18090_SRT-A | 102.74 | 102.7 | 811/866/918/969 | Yes
2025W1-N11-ST129 | 290573 | 05INNOVATION | 290577 | 05INNOVAT1EQ | 1 | 345/1.0 | 205 | 745 | 796 | AEP_P1-3_#17992_05INNOVATION 345_2_SRT-A | AEP_P1-2_#18090_SRT-A | 102.74 | 102.7 | 745/796/844/891 | Yes
2025W1-N11-ST130 | 290254 | 05INNOVATION | 290577 | 05INNOVAT1EQ | 1 | 138/1.0 | 205 | 745 | 796 | AEP_P1-3_#17992_05INNOVATION 345_2_SRT-A | AEP_P1-2_#18090_SRT-A | 102.74 | 102.7 | 745/796/844/891 | Yes
2025W1-N11-ST131 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 104.36 | 102.14 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST132 | 290573 | 05INNOVATION | 290577 | 05INNOVAT1EQ | 1 | 345/1.0 | 205 | 745 | 796 | AEP_P1-2_#18090_SRT-A | AEP_P1-3_#17992_05INNOVATION 345_2_SRT-A | 102.74 | 102.51 | 745/796/844/891 | Yes
2025W1-N11-ST133 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 106.35 | 101.96 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST134 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 106.35 | 101.81 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST135 | 290573 | 05INNOVATION | 288789 | 05INNOVAT2EQ | 2 | 345/1.0 | 205 | 745 | 796 | AEP_P1-2_#18090_SRT-A | AEP_P1-3_#17991_05INNOVATION 345_1_SRT-A | 102.74 | 102.51 | 811/866/918/969 | Yes
2025W1-N11-ST136 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 105.51 | 101.66 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST137 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 108.18 | 101.61 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST138 | 290254 | 05INNOVATION | 290577 | 05INNOVAT1EQ | 1 | 138/1.0 | 205 | 745 | 796 | AEP_P1-2_#18090_SRT-A | AEP_P1-3_#17992_05INNOVATION 345_2_SRT-A | 102.74 | 102.51 | 745/796/844/891 | Yes
2025W1-N11-ST139 | 290254 | 05INNOVATION | 288789 | 05INNOVAT2EQ | 2 | 138/1.0 | 205 | 745 | 796 | AEP_P1-2_#18090_SRT-A | AEP_P1-3_#17991_05INNOVATION 345_1_SRT-A | 102.74 | 102.51 | 811/866/918/969 | Yes
2025W1-N11-ST140 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#10137_570_SRT-A | 105.7 | 101.31 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST141 | 240710 | 02MELISSA | 241987 | AE2-217_POI | 1 | 138 | 202 | 200 | 242 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 101.57 | 101.3 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST142 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 100.97 | 101.24 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST143 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#707_8315_SRT-A | 103.08 | 101.21 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST144 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 223 | 310 | AEP_P1-2_#5832_6228_SRT-A | Base Case | 107.76 | 107.76 | 223/310/281/349 | Yes
2025W1-N11-ST145 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 101 | 101.01 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST146 | 243537 | 05MALIS | 243553 | 05POLARS | 1 | 138 | 205 | 223 | 310 | AEP_P1-3_#11531_05GENOA 138_2_SRT-A | Base Case | 104.92 | 104.92 | 223/310/281/349 | Yes
2025W1-N11-ST147 | 238908 | 02LONDON | 241987 | AE2-217_POI | 1 | 138 | 202 | 186 | 227 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 101.05 | 100.93 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST148 | 240637 | 02URECMITCHL | 240706 | 02NATIONAL | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 102.83 | 100.59 | 233/282/263/333 | Yes
2025W1-N11-ST149 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 100.27 | 100.56 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST150 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 109.54 | 100.39 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST151 | 238529 | 02AIRPK+ | 238623 | 02CLARK | 1 | 138 | 202 | 233 | 282 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 100.01 | 100.33 | 233/282/263/333 | Yes
2025W1-N11-ST152 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 100.29 | 100.32 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST153 | 239278 | 02BRDVIE | 241980 | AD2-163_POI | 1 | 138 | 202 | 160 | 192 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 100.03 | 100.3 | 160/192/180/228 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST154 | 240637 | 02URECMITCHL | 240706 | 02NATIONAL | 1 | 138 | 202 | 233 | 282 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 100.07 | 100.25 | 233/282/263/333 | Yes
2025W1-N11-ST155 | 238908 | 02LONDON | 241952 | 02DEERCREEK | 1 | 138 | 202 | 200 | 242 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035B_SRT-A | 103.43 | 100.11 | 200/242/226/286 | Yes |  | Overlap FE EOL candidate
2025W1-N11-ST156 | 216950 | ROSELAND | 217997 | LIVINGSTON | 1 | 230 | 231 | 731 | 885 | PS_P1-2_W-2249_LT_SRT-A | PS_P1-2_J-2288_SRT-A | 115.41 | 104.36 | 731/885/821/978 | Yes |  | This result was identified setting the Waldwick O Par angle range to +/- 40. This is only applicable for N-1-1 studies. Proposals submitted should set the O Par to this range to confirm mitigation.
2025W1-N11-ST157 | 216950 | ROSELAND | 217997 | LIVINGSTON | 1 | 230 | 231 | 731 | 885 | PS_P1-2_W-2249_SRT-A | PS_P1-2_J-2288_SRT-A | 115.31 | 104.34 | 731/885/821/978 | Yes |  | This result was identified setting the Waldwick O Par angle range to +/- 40. This is only applicable for N-1-1 studies. Proposals submitted should set the O Par to this range to confirm mitigation.
2025W1-N11-ST158 | 216950 | ROSELAND | 217997 | LIVINGSTON | 1 | 230 | 231 | 731 | 885 | PS_P1-2_W-2249_LT_SRT-A | PS_P1-2_J-2288_LT_SRT-A | 114.24 | 103.19 | 731/885/821/978 | Yes |  | This result was identified setting the Waldwick O Par angle range to +/- 40. This is only applicable for N-1-1 studies. Proposals submitted should set the O Par to this range to confirm mitigation.
2025W1-N11-ST159 | 216950 | ROSELAND | 217997 | LIVINGSTON | 1 | 230 | 231 | 731 | 885 | PS_P1-2_W-2249_SRT-A | PS_P1-2_J-2288_LT_SRT-A | 114.13 | 103.16 | 731/885/821/978 | Yes |  | This result was identified setting the Waldwick O Par angle range to +/- 40. This is only applicable for N-1-1 studies. Proposals submitted should set the O Par to this range to confirm mitigation.
2025W1-N11-ST160 | 216950 | ROSELAND | 216973 | LAUREL_J | 1 | 230 | 231 | 731 | 885 | PS_P1-2_W-2249_LT_SRT-A | PS_P1-2_B-2333_SRT-A | 111.33 | 100.35 | 731/885/821/978 | Yes |  | This result was identified setting the Waldwick O Par angle range to +/- 40. This is only applicable for N-1-1 studies. Proposals submitted should set the O Par to this range to confirm mitigation.
2025W1-N11-ST161 | 216950 | ROSELAND | 216973 | LAUREL_J | 1 | 230 | 231 | 731 | 885 | PS_P1-2_W-2249_SRT-A | PS_P1-2_B-2333_SRT-A | 111.23 | 100.33 | 731/885/821/978 | Yes |  | This result was identified setting the Waldwick O Par angle range to +/- 40. This is only applicable for N-1-1 studies. Proposals submitted should set the O Par to this range to confirm mitigation.

## Volt Mag
PJM N-1-1 Voltage Magnitude Result (Summer 2030 Case)
FG# | Bus # | Name | KV | Area | Min Volt Limit | Max Volt Limit | Contingency 1 | Contingency 2 | ContVolt | BaseVolt | PJM Accepting Proposals | Reasons for Exclusions | Comments
2025-W1-N11-SVM204527 | 204527 | 27FAIRVIEW | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-017_SRT-A | ME_P1-2_ME-115-027B_SRT-A | 0.90777 | 0.98048 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204527 | 204527 | 27FAIRVIEW | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-027B_SRT-A | ME_P1-2_ME-115-017_SRT-A | 0.90783 | 0.97516 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204532 | 204532 | 27GITTS RN | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-017_SRT-A | ME_P1-2_ME-115-027B_SRT-A | 0.91271 | 0.98504 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204532 | 204532 | 27GITTS RN | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-027B_SRT-A | ME_P1-2_ME-115-017_SRT-A | 0.91277 | 0.97974 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204548 | 204548 | 27N.HANOVR | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-017_SRT-A | ME_P1-2_ME-115-027B_SRT-A | 0.91505 | 0.98372 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204548 | 204548 | 27N.HANOVR | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-027B_SRT-A | ME_P1-2_ME-115-017_SRT-A | 0.91511 | 0.9819 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204715 | 204715 | 27EISENHOWER | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-017_SRT-A | ME_P1-2_ME-115-027B_SRT-A | 0.91375 | 0.98392 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025-W1-N11-SVM204715 | 204715 | 27EISENHOWER | 115 | 227 | 0.92 | 1.05 | ME_P1-2_ME-115-027B_SRT-A | ME_P1-2_ME-115-017_SRT-A | 0.91381 | 0.9807 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion
2025W1-N11-SVM206244 | 206244 | 28MONTVILE | 230 | 228 | 0.92 | 1.05 | JC_P1-2_JCN-230-017_SRT-A | PS_P1-2_E-2205_SRT-A | 0.79042 | 1.0283 | Yes
2025W1-N11-SVM206244 | 206244 | 28MONTVILE | 230 | 228 | 0.92 | 1.05 | PS_P1-2_E-2205_SRT-A | JC_P1-2_JCN-230-017_SRT-A | 0.79241 | 1.0142 | Yes
2025W1-N11-SVM207959 | 207959 | EPAL TR1 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.88272 | 0.99854 | Yes
2025W1-N11-SVM207959 | 207959 | EPAL TR1 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.88272 | 0.99854 | Yes
2025W1-N11-SVM207960 | 207960 | EPAL TR2 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.88252 | 0.99851 | Yes
2025W1-N11-SVM207960 | 207960 | EPAL TR2 | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.88252 | 0.99851 | Yes
2025W1-N11-SVM207963 | 207963 | SLYK | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.82702 | 0.98466 | Yes
2025W1-N11-SVM207963 | 207963 | SLYK | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.82702 | 0.98466 | Yes
2025W1-N11-SVM207966 | 207966 | BWAY | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.82682 | 0.98449 | Yes
2025W1-N11-SVM207966 | 207966 | BWAY | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.82682 | 0.98449 | Yes
2025W1-N11-SVM207967 | 207967 | LOFT | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.82328 | 0.98105 | Yes
2025W1-N11-SVM207967 | 207967 | LOFT | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.82328 | 0.98105 | Yes
2025W1-N11-SVM207969 | 207969 | TRES | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.82831 | 0.98521 | Yes
2025W1-N11-SVM207969 | 207969 | TRES | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.82831 | 0.98521 | Yes
2025W1-N11-SVM208072 | 208072 | SIEG | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.90981 | 0.99977 | Yes
2025W1-N11-SVM208072 | 208072 | SIEG | 230 | 229 | 0.92 | 1.05 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.90981 | 0.99977 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91705 | 0.9567 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91842 | 0.9567 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.79555 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.80388 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.82058 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.87642 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.89339 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.90385 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90485 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91721 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91809 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91859 | 0.93276 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91985 | 0.95834 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91703 | 0.95562 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91872 | 0.95562 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89928 | 0.95694 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8996 | 0.95694 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90261 | 0.95815 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90277 | 0.95815 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89355 | 0.95685 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91603 | 0.95685 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82048 | 0.95557 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89333 | 0.95557 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89442 | 0.95557 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91 | 0.96581 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.86487 | 0.95729 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89729 | 0.95729 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90392 | 0.95729 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.75363 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.80387 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89428 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.89715 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.89722 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91677 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-69-011_SRT-A | 0.91715 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91848 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91911 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.91989 | 0.93406 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9185 | 0.95752 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91861 | 0.95752 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91934 | 0.95752 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91626 | 0.95636 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91832 | 0.95636 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91717 | 0.95687 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91853 | 0.95687 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90138 | 0.95139 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90366 | 0.95139 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80831 | 0.95952 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87654 | 0.95952 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90159 | 0.95435 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90595 | 0.95435 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.75374 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.79541 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.80842 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.86475 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89323 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.90256 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.90364 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-138-004_SRT-A | 0.91831 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-011_SRT-A | 0.91852 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91933 | 0.93405 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89727 | 0.95753 | Yes
2025W1-N11-SVM238529 | 238529 | 02AIRPK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90496 | 0.95753 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80378 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8103 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.83338 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.88408 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90628 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91146 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91239 | 0.94 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90482 | 0.96282 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90531 | 0.96282 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90794 | 0.96395 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90855 | 0.96395 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90643 | 0.96467 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83329 | 0.96153 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89953 | 0.96153 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89973 | 0.96153 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91408 | 0.97114 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.86981 | 0.9626 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90196 | 0.9626 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91152 | 0.9626 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.7558 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8103 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89959 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90184 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.90189 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.90475 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.90513 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.90583 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.90788 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-034_SRT-A | 0.91402 | 0.93885 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90516 | 0.95635 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90842 | 0.95635 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81265 | 0.96512 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8842 | 0.96512 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90587 | 0.9597 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91366 | 0.9597 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.75591 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.80363 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.81276 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.86969 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89944 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.90527 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.9084 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.90851 | 0.93918 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90196 | 0.96277 | Yes
2025W1-N11-SVM238623 | 238623 | 02CLARK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91249 | 0.96277 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91446 | 0.95003 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91453 | 0.95003 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89828 | 0.94572 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90626 | 0.94572 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91905 | 0.94572 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90662 | 0.948 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91525 | 0.948 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90716 | 0.94824 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90454 | 0.94576 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9127 | 0.94576 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91324 | 0.94576 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90388 | 0.9462 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91354 | 0.9462 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91467 | 0.9462 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89421 | 0.93881 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90102 | 0.93881 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9016 | 0.93881 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9048 | 0.93881 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90868 | 0.93881 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91971 | 0.93881 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91338 | 0.94654 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91351 | 0.94654 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90415 | 0.94376 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90806 | 0.94376 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9103 | 0.94376 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18135_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9073 | 0.94751 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90578 | 0.94518 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90997 | 0.94518 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91196 | 0.94518 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91405 | 0.94685 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91466 | 0.94685 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9009 | 0.94845 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90718 | 0.94845 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.76991 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.78003 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.78263 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.85075 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.85395 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.90347 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16635_SRT-A | 0.90386 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.90396 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#18134_SRT-A | 0.90413 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16618_27957_SRT-A | 0.90451 | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.90956 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90471 | 0.94663 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91244 | 0.94663 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9061 | 0.94721 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91365 | 0.94721 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90615 | 0.94749 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91448 | 0.94749 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91457 | 0.94749 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90458 | 0.94573 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91236 | 0.94573 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.913 | 0.94573 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90376 | 0.94543 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9121 | 0.94543 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91278 | 0.94543 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90681 | 0.94744 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91538 | 0.94744 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89649 | 0.94058 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90427 | 0.94058 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90669 | 0.94058 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90865 | 0.94058 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91715 | 0.94058 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90565 | 0.94647 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91414 | 0.94647 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91486 | 0.94647 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89712 | 0.94076 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90161 | 0.94076 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90401 | 0.94076 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90708 | 0.94076 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90698 | 0.9482 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91474 | 0.9482 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#728_584_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91445 | 0.94742 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91479 | 0.94724 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9151 | 0.94724 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89353 | 0.9385 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90303 | 0.9385 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90567 | 0.9385 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91621 | 0.9385 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91666 | 0.9385 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90641 | 0.94727 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91522 | 0.94727 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8968 | 0.94008 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90535 | 0.94008 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90638 | 0.94008 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9065 | 0.94795 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91427 | 0.94795 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90681 | 0.94771 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91543 | 0.94771 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05ROBERT 138_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90682 | 0.94686 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-237805-237806_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91531 | 0.94728 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-242508-237805_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91509 | 0.94711 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88004 | 0.93795 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88209 | 0.93795 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90351 | 0.93795 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91779 | 0.93795 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88368 | 0.93942 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88545 | 0.93942 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90526 | 0.93942 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91981 | 0.93942 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90298 | 0.95015 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89897 | 0.95081 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85415 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.8917 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89319 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90565 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91549 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91732 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91779 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91802 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91981 | 0.93219 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87595 | 0.93726 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.8917 | 0.93726 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90603 | 0.93726 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91457 | 0.93726 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.77992 | 0.93635 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.87359 | 0.93635 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87664 | 0.93635 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91548 | 0.93635 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89693 | 0.94823 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90644 | 0.94823 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90558 | 0.95061 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90764 | 0.95061 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91317 | 0.95061 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.84925 | 0.94002 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87952 | 0.94002 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88165 | 0.94002 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.74758 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.78262 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.87649 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.88141 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.88158 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.91208 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.91215 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.91226 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.91235 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#16618_27957_SRT-A | 0.91269 | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | - | 0.91793 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-023A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90735 | 0.95233 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9069 | 0.9482 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91516 | 0.94867 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-936_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9072 | 0.94913 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-937_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90721 | 0.94913 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-938_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90734 | 0.94914 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90603 | 0.94778 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91436 | 0.94778 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90568 | 0.94763 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91405 | 0.94763 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89162 | 0.93735 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90034 | 0.93735 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90084 | 0.93735 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91802 | 0.93735 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90332 | 0.94086 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9038 | 0.94086 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90641 | 0.94274 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90711 | 0.94274 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-006_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91053 | 0.94481 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90998 | 0.94929 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91064 | 0.94929 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9029 | 0.94022 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90305 | 0.94022 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90765 | 0.94295 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90815 | 0.94295 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88882 | 0.93562 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88918 | 0.93562 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91732 | 0.93562 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.79416 | 0.94049 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85088 | 0.94049 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 241972 AD1-140 GEN 0.57_SRT-A | 0.91873 | 0.94049 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88124 | 0.93708 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88747 | 0.93708 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.74768 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.76978 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.79435 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.84913 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.87348 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035B_SRT-A | 0.90759 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-013_SRT-A | 0.90764 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-008_SRT-A | 0.90997 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91029 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18232_SRT-A | 0.91195 | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | - | 0.91761 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90208 | 0.94563 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90989 | 0.94563 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90561 | 0.94704 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91375 | 0.94704 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88105 | 0.94063 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88153 | 0.94063 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90125 | 0.94525 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90922 | 0.94525 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90321 | 0.94531 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91216 | 0.94531 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91335 | 0.94531 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90561 | 0.94713 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91443 | 0.94713 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91547 | 0.94713 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34508_CLAY_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90724 | 0.94817 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90373 | 0.94624 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91381 | 0.94624 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9149 | 0.94624 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90542 | 0.94728 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91462 | 0.94728 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90548 | 0.94662 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91377 | 0.94662 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91421 | 0.94662 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9033 | 0.94608 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91159 | 0.94608 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90407 | 0.94646 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91414 | 0.94646 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91445 | 0.94646 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90605 | 0.94747 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91525 | 0.94747 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90577 | 0.94803 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91299 | 0.94803 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9059 | 0.94732 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9139 | 0.94732 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90396 | 0.94529 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91227 | 0.94529 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91275 | 0.94529 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90692 | 0.94824 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_S_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90678 | 0.94817 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90191 | 0.94548 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90973 | 0.94548 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_MIAMI_345_MIAMI_138_BK_E_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91414 | 0.94582 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90331 | 0.94608 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91159 | 0.94608 | Yes
2025W1-N11-SVM238703 | 238703 | 02ESPRNG | 138 | 202 | 0.92 | 1.05 | DAY_P1_URBANA_22.5_MVAR_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91104 | 0.94531 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89205 | 0.9471 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91935 | 0.9471 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | 253222 09TAIT E 69.0_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89996 | 0.94856 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89977 | 0.94834 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90023 | 0.94861 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.898 | 0.94758 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89816 | 0.94915 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8873 | 0.9402 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90359 | 0.9402 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91015 | 0.9402 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91152 | 0.9402 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91614 | 0.9402 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89824 | 0.94618 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91949 | 0.94618 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18135_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90008 | 0.94836 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89962 | 0.9472 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89477 | 0.94925 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91882 | 0.94925 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.75222 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.77907 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.78718 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.84721 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.852 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89048 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.89135 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | 241972 AD1-140 GEN 0.57_SRT-A | 0.8917 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 0.89646 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | 0.89647 | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.90239 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89791 | 0.94788 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89913 | 0.94817 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89927 | 0.94818 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89778 | 0.94692 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89704 | 0.94719 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89026 | 0.94213 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91011 | 0.94213 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91441 | 0.94213 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91813 | 0.94213 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89911 | 0.94798 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89044 | 0.94253 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90362 | 0.94253 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91474 | 0.94253 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91877 | 0.94253 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89993 | 0.949 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8881 | 0.94133 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91431 | 0.94133 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91816 | 0.94133 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91856 | 0.94133 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90003 | 0.94853 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89106 | 0.94321 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91698 | 0.94321 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91952 | 0.94321 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89949 | 0.94882 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89999 | 0.94852 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05ROBERT 138_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89954 | 0.94717 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91635 | 0.94916 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91753 | 0.94916 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91788 | 0.94974 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91919 | 0.94974 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.79403 | 0.94544 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88749 | 0.94544 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.79403 | 0.94293 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87816 | 0.94293 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.85218 | 0.93801 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9082 | 0.93801 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.90981 | 0.93801 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91794 | 0.93801 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91906 | 0.93801 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87235 | 0.94186 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90981 | 0.94186 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91949 | 0.94186 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.7521 | 0.93493 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88417 | 0.93493 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88459 | 0.93493 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91793 | 0.93493 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89961 | 0.94913 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91138 | 0.94913 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89873 | 0.95062 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91994 | 0.95062 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87323 | 0.942 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.87617 | 0.942 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89736 | 0.942 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.78718 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80416 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.88447 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.89682 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.89731 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-138-004_SRT-A | 0.91701 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91784 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-69-004_SRT-A | 0.91927 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91948 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-69-013_SRT-A | 0.91997 | 0.92595 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90015 | 0.94924 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-936_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9002 | 0.9497 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-937_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90021 | 0.9497 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90003 | 0.94899 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89928 | 0.94887 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89897 | 0.94878 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88726 | 0.94276 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91561 | 0.94276 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91903 | 0.94478 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91929 | 0.9459 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91687 | 0.9444 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91849 | 0.9444 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91999 | 0.94607 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90841 | 0.94163 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90992 | 0.94163 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.83518 | 0.94192 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84733 | 0.94192 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87762 | 0.94217 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90605 | 0.94217 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.77896 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.80424 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.83518 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.87609 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.88409 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91905 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91917 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91948 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91951 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035B_SRT-A | 0.91991 | 0.92744 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89543 | 0.94713 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8988 | 0.94831 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87564 | 0.94292 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8969 | 0.94292 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89469 | 0.94686 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91953 | 0.94686 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89745 | 0.94808 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89828 | 0.94773 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34508_CLAY_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89992 | 0.94865 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89679 | 0.94729 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89814 | 0.94798 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89881 | 0.94818 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89648 | 0.94745 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89697 | 0.94734 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8988 | 0.94818 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89897 | 0.94897 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89904 | 0.94849 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89751 | 0.94726 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89985 | 0.949 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_S_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89972 | 0.94895 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89532 | 0.94706 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91994 | 0.94706 | Yes
2025W1-N11-SVM238908 | 238908 | 02LONDON | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89649 | 0.94745 | Yes
2025W1-N11-SVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91617 | 0.97459 | Yes
2025W1-N11-SVM238964 | 238964 | 02MLCRK+ | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91619 | 0.9742 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.79764 | 0.94195 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.82646 | 0.94195 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.84356 | 0.94195 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.88905 | 0.94195 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91346 | 0.94195 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91467 | 0.94195 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90035 | 0.96297 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9105 | 0.96297 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90363 | 0.96402 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91326 | 0.96402 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84348 | 0.9618 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89447 | 0.9618 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90609 | 0.9618 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.86362 | 0.96199 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90508 | 0.96199 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91351 | 0.96199 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.75661 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.82646 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.90501 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90507 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90597 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.90783 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91045 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91321 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91431 | 0.9409 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91977 | 0.96339 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90528 | 0.95964 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91434 | 0.95964 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80907 | 0.96257 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88915 | 0.96257 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90787 | 0.95702 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91331 | 0.95702 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.75671 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.79751 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.80915 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.8635 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89438 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.9003 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.90359 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.90526 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-011_SRT-A | 0.91976 | 0.93491 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90518 | 0.96258 | Yes
2025W1-N11-SVM239278 | 239278 | 02BRDVIE | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91477 | 0.96258 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9011 | 0.95383 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90241 | 0.95383 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91568 | 0.97293 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91568 | 0.972 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90241 | 0.96359 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91044 | 0.96359 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90104 | 0.965 | Yes
2025W1-N11-SVM240637 | 240637 | 02URECMITCHL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91047 | 0.965 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90483 | 0.95251 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | 253222 09TAIT E 69.0_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91136 | 0.95366 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91145 | 0.95354 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91003 | 0.95256 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91072 | 0.95411 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89948 | 0.94506 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90718 | 0.94506 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91461 | 0.94506 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91053 | 0.95113 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18135_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91154 | 0.95333 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90741 | 0.9544 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8095 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.81477 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.86553 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.87087 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.88761 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.90272 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.90422 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | 241972 AD1-140 GEN 0.57_SRT-A | 0.90454 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 0.90851 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | 0.90851 | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.91379 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90984 | 0.95312 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91082 | 0.95332 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91094 | 0.95317 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90964 | 0.95198 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90898 | 0.95202 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90281 | 0.94747 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91457 | 0.94747 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91105 | 0.95316 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90268 | 0.94738 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9072 | 0.94738 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91159 | 0.95415 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90131 | 0.94678 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90398 | 0.94838 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#773_565_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91162 | 0.95589 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91121 | 0.954 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05ROBERT 138_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.911 | 0.9523 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.82686 | 0.95131 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90127 | 0.95131 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.82686 | 0.94925 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89341 | 0.94925 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87102 | 0.94499 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91939 | 0.94499 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88842 | 0.94831 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91143 | 0.95429 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91072 | 0.95552 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88767 | 0.94739 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89257 | 0.94739 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90934 | 0.94739 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.81476 | 0.93435 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.83234 | 0.93435 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.90925 | 0.93435 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.9093 | 0.93435 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91781 | 0.93435 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91937 | 0.93435 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91118 | 0.9541 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91092 | 0.95402 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90157 | 0.94918 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85828 | 0.94788 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86562 | 0.94788 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89317 | 0.94857 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91783 | 0.94857 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.80941 | 0.93603 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.83241 | 0.93603 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.85827 | 0.93603 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.89251 | 0.93603 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90763 | 0.95242 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9107 | 0.9536 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89029 | 0.94891 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90932 | 0.94891 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90699 | 0.95217 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91001 | 0.95313 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90989 | 0.95295 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34508_CLAY_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9114 | 0.95378 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90875 | 0.95261 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90979 | 0.95313 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91071 | 0.95315 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90852 | 0.95271 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90881 | 0.95259 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9104 | 0.95334 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91087 | 0.95417 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91089 | 0.95371 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90963 | 0.9523 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91152 | 0.95418 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_S_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91141 | 0.95413 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90756 | 0.95237 | Yes
2025W1-N11-SVM240706 | 240706 | 02NATIONAL | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90853 | 0.95272 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90581 | 0.94101 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90626 | 0.94101 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88628 | 0.93633 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89815 | 0.93633 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91 | 0.93633 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91905 | 0.93633 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | 253222 09TAIT E 69.0_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89538 | 0.9385 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89469 | 0.93847 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90619 | 0.93847 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89523 | 0.93873 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89262 | 0.93655 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90406 | 0.93655 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90507 | 0.93655 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91973 | 0.93655 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89212 | 0.93727 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90518 | 0.93727 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90677 | 0.93727 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88196 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89139 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89218 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89639 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89852 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91001 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91712 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91883 | 0.92932 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90465 | 0.93708 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.905 | 0.93708 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89236 | 0.93469 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89974 | 0.93469 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9024 | 0.93469 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91752 | 0.93469 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91927 | 0.93469 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18135_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89533 | 0.93809 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89398 | 0.93604 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90156 | 0.93604 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90398 | 0.93604 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91897 | 0.93604 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90516 | 0.93744 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90626 | 0.93744 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88898 | 0.93903 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89867 | 0.93903 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.75943 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.76125 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.77095 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.83802 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.84169 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.89204 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16635_SRT-A | 0.8921 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#18134_SRT-A | 0.89234 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.89259 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16618_27957_SRT-A | 0.89259 | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.89763 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89274 | 0.93727 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90364 | 0.93727 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89415 | 0.93779 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90477 | 0.93779 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8942 | 0.93804 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90557 | 0.93804 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90613 | 0.93804 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89261 | 0.93636 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90356 | 0.93636 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90467 | 0.93636 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91945 | 0.93636 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89178 | 0.93619 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90344 | 0.93619 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90458 | 0.93619 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91937 | 0.93619 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89499 | 0.93808 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90649 | 0.93808 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88444 | 0.93117 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89542 | 0.93117 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89833 | 0.93117 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89848 | 0.93117 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90766 | 0.93117 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91375 | 0.93117 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89379 | 0.93718 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90537 | 0.93718 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90657 | 0.93718 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88499 | 0.93141 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.8914 | 0.93141 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89532 | 0.93141 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89881 | 0.93141 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91427 | 0.93141 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91948 | 0.93141 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89501 | 0.93877 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90583 | 0.93877 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#728_584_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90556 | 0.93798 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90591 | 0.93785 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90671 | 0.93785 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88158 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89444 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89755 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90644 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90716 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91654 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91753 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91882 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91907 | 0.92934 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89457 | 0.93795 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90638 | 0.93795 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88486 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89694 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89845 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9139 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91708 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91896 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91915 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91925 | 0.93104 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89453 | 0.93853 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90536 | 0.93853 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89489 | 0.93829 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90648 | 0.93829 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05ROBERT 138_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8948 | 0.93731 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-237805-237806_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9064 | 0.93788 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-242508-237805_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90619 | 0.9377 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.72431 | 0.93339 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88081 | 0.93339 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90355 | 0.93339 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90398 | 0.93339 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.9169 | 0.93339 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91737 | 0.93339 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.72431 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87034 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90077 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90129 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91157 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91733 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91882 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91883 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91888 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91919 | 0.92975 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84189 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.88417 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88484 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89756 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90566 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91778 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#18232_SRT-A | 0.91898 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.91961 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-69-033A_SRT-A | 0.91969 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_URBANA_22.5_MVAR_SRT-A | 0.91972 | 0.92337 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86393 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.88417 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89798 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90579 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91421 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91888 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91913 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91918 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91967 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-4_OES-69-011_SRT-A | 0.91998 | 0.92836 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.76113 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.86436 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.86684 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90565 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91156 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91623 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91685 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.9169 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91796 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91829 | 0.92628 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88866 | 0.93884 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89451 | 0.93884 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91318 | 0.93884 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89362 | 0.94106 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89928 | 0.94106 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90409 | 0.94106 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.84191 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86699 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87284 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91487 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91578 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91667 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91862 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91913 | 0.93052 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.74516 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.77095 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.86669 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.87253 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.90342 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90351 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.90354 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.90363 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.90375 | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | - | 0.90898 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.895 | 0.93883 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91969 | 0.93883 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90632 | 0.93927 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-936_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89525 | 0.93969 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-937_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89526 | 0.93969 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-938_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89539 | 0.9397 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8941 | 0.93841 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90604 | 0.93841 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89375 | 0.93828 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90574 | 0.93828 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87985 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89291 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89295 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9101 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91591 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91606 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91796 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91883 | 0.92869 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89522 | 0.93196 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89617 | 0.93196 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9148 | 0.93196 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91931 | 0.93196 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89862 | 0.93371 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89877 | 0.93371 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91698 | 0.93371 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-006_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.902 | 0.93565 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90198 | 0.93985 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90209 | 0.93985 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89497 | 0.93136 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89533 | 0.93136 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91408 | 0.93136 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91998 | 0.93136 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89977 | 0.93392 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8998 | 0.93392 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91662 | 0.93392 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88192 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88209 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90941 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91463 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91578 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91606 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91607 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91653 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91733 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-4_OES-138-004_SRT-A | 0.91931 | 0.92704 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.78821 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83815 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 241972 AD1-140 GEN 0.57_SRT-A | 0.90967 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91228 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91592 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91619 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91979 | 0.93084 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86936 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87989 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91346 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91462 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91585 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91777 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91862 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91882 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91979 | 0.92831 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.74526 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.75931 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.7884 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.84179 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.86425 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.90128 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-008_SRT-A | 0.90197 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18134_SRT-A | 0.90239 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18232_SRT-A | 0.90397 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90397 | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | - | 0.90916 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89007 | 0.93629 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90112 | 0.93629 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89366 | 0.93769 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9049 | 0.93769 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86877 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87265 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91346 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91541 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91653 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91829 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91967 | 0.93125 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88924 | 0.93593 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90047 | 0.93593 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89143 | 0.93632 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90377 | 0.93632 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90541 | 0.93632 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9196 | 0.93632 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89354 | 0.93761 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9059 | 0.93761 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90644 | 0.93761 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34508_CLAY_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89522 | 0.93866 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8917 | 0.93681 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90536 | 0.93681 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90592 | 0.93681 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89336 | 0.93779 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90612 | 0.93779 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89356 | 0.93737 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90507 | 0.93737 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90598 | 0.93737 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89129 | 0.93672 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90274 | 0.93672 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89202 | 0.93699 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90545 | 0.93699 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90567 | 0.93699 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89401 | 0.938 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90676 | 0.938 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89383 | 0.93863 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90417 | 0.93863 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89395 | 0.93796 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90506 | 0.93796 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89205 | 0.9361 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90364 | 0.9361 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9046 | 0.9361 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91927 | 0.9361 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89494 | 0.9388 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_S_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89481 | 0.93874 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88992 | 0.93616 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90097 | 0.93616 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_MIAMI_345_MIAMI_138_BK_E_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9058 | 0.93651 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89129 | 0.93672 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90275 | 0.93672 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_URBANA_22.5_MVAR_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90246 | 0.93611 | Yes
2025W1-N11-SVM240709 | 240709 | 02N TITUS | 138 | 202 | 0.92 | 1.05 | DAY_P1_URBANA_22.5_MVAR_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91972 | 0.93611 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90561 | 0.94088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90603 | 0.94088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88622 | 0.93622 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8979 | 0.93622 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90983 | 0.93622 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91887 | 0.93622 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | 253222 09TAIT E 69.0_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89533 | 0.93839 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89463 | 0.93837 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90601 | 0.93837 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89517 | 0.93862 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89256 | 0.93642 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90385 | 0.93642 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90484 | 0.93642 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91954 | 0.93642 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89205 | 0.93713 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90496 | 0.93713 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90652 | 0.93713 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8819 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89124 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89197 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89616 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.89838 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.90986 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91697 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91866 | 0.9292 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90445 | 0.93697 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90478 | 0.93697 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91993 | 0.93697 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89229 | 0.93455 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8995 | 0.93455 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90215 | 0.93455 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91731 | 0.93455 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91908 | 0.93455 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18135_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89528 | 0.93797 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89391 | 0.93591 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90133 | 0.93591 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90373 | 0.93591 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91877 | 0.93591 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90497 | 0.93733 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90604 | 0.93733 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88892 | 0.93892 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89845 | 0.93892 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.75917 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.76141 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.77075 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.83791 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.84156 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.89198 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16635_SRT-A | 0.89203 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#18134_SRT-A | 0.89227 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.89253 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16618_27957_SRT-A | 0.89253 | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.89758 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89268 | 0.93715 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90344 | 0.93715 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8941 | 0.93768 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90458 | 0.93768 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89414 | 0.93793 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90538 | 0.93793 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90592 | 0.93793 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89255 | 0.93624 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90336 | 0.93624 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90445 | 0.93624 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91927 | 0.93624 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89172 | 0.93606 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90323 | 0.93606 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90435 | 0.93606 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91918 | 0.93606 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89493 | 0.93796 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9063 | 0.93796 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88437 | 0.93104 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89521 | 0.93104 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8981 | 0.93104 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89834 | 0.93104 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.9075 | 0.93104 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91357 | 0.93104 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89373 | 0.93706 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90517 | 0.93706 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90635 | 0.93706 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88492 | 0.93128 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89125 | 0.93128 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8951 | 0.93128 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89857 | 0.93128 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91408 | 0.93128 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.9193 | 0.93128 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89496 | 0.93866 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90564 | 0.93866 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#728_584_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90537 | 0.93787 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90572 | 0.93773 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90649 | 0.93773 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8815 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89421 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8973 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90629 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.90699 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91636 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91734 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91864 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91888 | 0.92919 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89451 | 0.93783 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90619 | 0.93783 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88479 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89671 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8982 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91369 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91693 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91879 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91896 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91905 | 0.93089 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89448 | 0.93841 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90517 | 0.93841 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89483 | 0.93817 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9063 | 0.93817 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05ROBERT 138_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89475 | 0.9372 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-237805-237806_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90622 | 0.93776 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-242508-237805_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.906 | 0.93759 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.87066 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87222 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89125 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90784 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91329 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91613 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91845 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91856 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91914 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.9193 | 0.92784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.87441 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8757 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89314 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90998 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91273 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91515 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91922 | 0.92942 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.72347 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88073 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90335 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90375 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91677 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91718 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91856 | 0.93325 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.72346 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87024 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90055 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90105 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91142 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91711 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91862 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91862 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91868 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.919 | 0.9296 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84177 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.88387 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88459 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89731 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90552 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91758 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#18232_SRT-A | 0.91878 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.9194 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-69-033A_SRT-A | 0.9195 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_URBANA_22.5_MVAR_SRT-A | 0.91953 | 0.9232 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86383 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.88387 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89773 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90559 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91273 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91868 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91897 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#762_8072_SRT-A | 0.91898 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.9195 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-4_OES-69-011_SRT-A | 0.91977 | 0.9282 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.7613 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.86411 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.86663 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90551 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91142 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91614 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91675 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.91677 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91783 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91819 | 0.92618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88841 | 0.93872 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89445 | 0.93872 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91298 | 0.93872 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89357 | 0.94096 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89905 | 0.94096 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90391 | 0.94096 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.84153 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86693 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87259 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91469 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91558 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91657 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91845 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91897 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91914 | 0.9304 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.74448 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.77075 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.86648 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.87216 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.87229 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#6764_21618_SRT-A | 0.90321 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90331 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#6763_21617_SRT-A | 0.90334 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.90342 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.90353 | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | - | 0.9088 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89494 | 0.93871 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9195 | 0.93871 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90613 | 0.93915 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-936_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89519 | 0.93958 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-937_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8952 | 0.93958 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-938_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89534 | 0.93959 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89405 | 0.9383 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90582 | 0.9383 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8937 | 0.93816 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90552 | 0.93816 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87976 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89265 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89265 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90985 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91569 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91582 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91783 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91862 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.9193 | 0.92852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89497 | 0.9318 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8959 | 0.9318 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91459 | 0.9318 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91908 | 0.9318 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89835 | 0.93357 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89854 | 0.93357 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91678 | 0.93357 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-006_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90179 | 0.93552 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90173 | 0.93974 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90188 | 0.93974 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89472 | 0.9312 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89505 | 0.9312 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91386 | 0.9312 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91977 | 0.9312 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89954 | 0.93377 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89954 | 0.93377 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91642 | 0.93377 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8816 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88174 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.90916 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91438 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91558 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.91582 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91584 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91633 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91711 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-4_OES-138-004_SRT-A | 0.91908 | 0.92686 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.78769 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.83804 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 241972 AD1-140 GEN 0.57_SRT-A | 0.9095 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91212 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91574 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.9161 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91845 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91964 | 0.93073 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86926 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87958 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.91326 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91438 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91571 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91758 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.91845 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91861 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-002B_SRT-A | 0.91922 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91964 | 0.92815 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.74458 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.75905 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.78788 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.84141 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.86401 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.90104 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-008_SRT-A | 0.90172 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18134_SRT-A | 0.90214 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18232_SRT-A | 0.90372 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.90374 | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | - | 0.90895 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89001 | 0.93617 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90091 | 0.93617 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8936 | 0.93757 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90471 | 0.93757 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86869 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87241 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91326 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91523 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91632 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91819 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.9195 | 0.93112 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88918 | 0.93581 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90026 | 0.93581 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89136 | 0.93618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90355 | 0.93618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90517 | 0.93618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9194 | 0.93618 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89349 | 0.9375 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90569 | 0.9375 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90626 | 0.9375 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34508_CLAY_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89517 | 0.93855 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89165 | 0.93669 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90514 | 0.93669 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90574 | 0.93669 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89331 | 0.93768 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9059 | 0.93768 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8935 | 0.93724 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90486 | 0.93724 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90575 | 0.93724 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89124 | 0.9366 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90255 | 0.9366 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89197 | 0.93688 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90526 | 0.93688 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90545 | 0.93688 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91984 | 0.93688 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89397 | 0.93788 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90655 | 0.93788 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89377 | 0.93852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90397 | 0.93852 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89389 | 0.93784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90486 | 0.93784 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89199 | 0.93597 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90343 | 0.93597 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90437 | 0.93597 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91908 | 0.93597 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89489 | 0.93869 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_S_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89475 | 0.93862 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88986 | 0.93604 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90077 | 0.93604 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_MIAMI_345_MIAMI_138_BK_E_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90557 | 0.93639 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89124 | 0.9366 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90255 | 0.9366 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_URBANA_22.5_MVAR_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90225 | 0.93598 | Yes
2025W1-N11-SVM240710 | 240710 | 02MELISSA | 138 | 202 | 0.92 | 1.05 | DAY_P1_URBANA_22.5_MVAR_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91953 | 0.93598 | Yes
2025W1-N11-SVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.88065 | 0.96615 | Yes
2025W1-N11-SVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.88064 | 0.96487 | Yes
2025W1-N11-SVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88395 | 0.9551 | Yes
2025W1-N11-SVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9006 | 0.96367 | Yes
2025W1-N11-SVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88399 | 0.95656 | Yes
2025W1-N11-SVM241952 | 241952 | 02DEERCREEK | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90062 | 0.95656 | Yes
2025W1-N11-SVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90987 | 0.97772 | Yes
2025W1-N11-SVM241968 | 241968 | AD1-140 TAP | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90967 | 0.97744 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.84839 | 0.96265 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87011 | 0.96265 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89048 | 0.96265 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91954 | 0.96265 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89041 | 0.97975 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.81103 | 0.96123 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87011 | 0.96123 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.85365 | 0.97853 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91961 | 0.97853 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8111 | 0.95705 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84829 | 0.95705 | Yes
2025W1-N11-SVM241980 | 241980 | AD2-163_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.85381 | 0.95705 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91343 | 0.94662 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | 241955 AC1-078 GEN 0.60 _SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91457 | 0.94662 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88987 | 0.94161 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90697 | 0.94161 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91698 | 0.94161 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | 253222 09TAIT E 69.0_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89852 | 0.94352 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89806 | 0.94345 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#10137_570_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91337 | 0.94345 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#13648_26782_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89856 | 0.94371 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8961 | 0.94205 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91187 | 0.94205 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16618_27957_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91347 | 0.94205 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89588 | 0.94315 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#16635_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91334 | 0.94315 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88541 | 0.93472 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.89731 | 0.93472 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90023 | 0.93472 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9042 | 0.93472 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90479 | 0.93472 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91588 | 0.93472 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91214 | 0.94221 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18125_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91311 | 0.94221 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89607 | 0.94047 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90815 | 0.94047 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18134_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91127 | 0.94047 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18135_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89855 | 0.94323 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89759 | 0.94168 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90978 | 0.94168 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#18232_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91266 | 0.94168 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91261 | 0.94263 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#37_12_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91429 | 0.94263 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8926 | 0.94414 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5784_654_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90698 | 0.94414 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.75887 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.76801 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.77816 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.84271 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.84688 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 0.89465 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | 0.89465 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | 0.89516 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | 0.89555 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | AEP_P1-2_#16635_SRT-A | 0.89586 | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | Base Case | - | 0.90087 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89612 | 0.94253 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5842_11418_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91129 | 0.94253 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89746 | 0.94297 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#5859_13838_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91224 | 0.94297 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89756 | 0.94315 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91296 | 0.94315 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6146_566_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91413 | 0.94315 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.896 | 0.94165 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91118 | 0.94165 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6763_21617_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91287 | 0.94165 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89521 | 0.94167 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91126 | 0.94167 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#6764_21618_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91297 | 0.94167 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#706_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89851 | 0.9433 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88808 | 0.9366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90334 | 0.9366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.90416 | 0.9366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90676 | 0.9366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#7441_100545_SRT-A | 0.91393 | 0.9366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89725 | 0.94256 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91295 | 0.94256 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#709_546_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91473 | 0.94256 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88848 | 0.93693 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.89733 | 0.93693 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90344 | 0.93693 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#711_6224_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90733 | 0.93693 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89829 | 0.94388 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7211_300000_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91322 | 0.94388 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#728_584_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91298 | 0.94311 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#734_8011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91332 | 0.94305 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88551 | 0.93521 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90274 | 0.93521 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90634 | 0.93521 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#17216_SRT-A | 0.91236 | 0.93521 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7441_100545_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.91344 | 0.93521 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#7442_200545_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89808 | 0.94324 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88866 | 0.93702 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90538 | 0.93702 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-2_#762_8072_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90747 | 0.93702 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89783 | 0.94366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#7219_05VASSEL 345_3_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91279 | 0.94366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-3_#8072_05MARYSV 765_2_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89826 | 0.94342 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AEP_P1-4_05ROBERT 138_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89802 | 0.94229 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-237805-237806_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91374 | 0.94305 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | AP_P1-2_PE-765-242508-237805_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91353 | 0.94289 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.88803 | 0.93662 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88806 | 0.93662 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89652 | 0.93662 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91934 | 0.93662 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89088 | 0.93786 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89106 | 0.93786 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89808 | 0.93786 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.74974 | 0.93918 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88474 | 0.93918 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91131 | 0.93918 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002C_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91238 | 0.93918 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.74974 | 0.93594 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87468 | 0.93594 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90882 | 0.93594 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90998 | 0.93594 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91737 | 0.93594 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84707 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8941 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.89454 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90647 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91154 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | CPP_P1-4_ET CAP_SRT-A | 0.91795 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-4_OES-138-002_SRT-A | 0.9186 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91903 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-003A_SRT-A | ATSI_P1-2_OES-138-002A_SRT-A | 0.91934 | 0.93001 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.86848 | 0.93465 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.89455 | 0.93465 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90692 | 0.93465 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91337 | 0.93465 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-018_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.91964 | 0.93465 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.75876 | 0.93093 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.87291 | 0.93093 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87449 | 0.93093 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91153 | 0.93093 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.91737 | 0.93093 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | ATSI_P1-2_OES-138-018_SRT-A | 0.91964 | 0.93093 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8978 | 0.94398 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-034_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89786 | 0.94398 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89696 | 0.94591 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90778 | 0.94591 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035B_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91139 | 0.94591 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.8548 | 0.9359 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87062 | 0.9359 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-035BA_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88215 | 0.9359 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.76638 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.77815 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.87436 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | 0.88176 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.88209 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-69-006_SRT-A | 0.91006 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | ATSI_P1-4_OES-69-008_SRT-A | 0.91012 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 0.91037 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | 0.91037 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_URBANA_22.5_MVAR_SRT-A | 0.91042 | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | Base Case | - | 0.91613 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-2_OES-69-033A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89838 | 0.94403 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-936_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89857 | 0.94474 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-345-937_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89857 | 0.94474 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89749 | 0.94362 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-006_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91422 | 0.94362 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89716 | 0.9435 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-3_OES-69-007_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91396 | 0.9435 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8841 | 0.93531 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90228 | 0.93531 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90302 | 0.93531 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-002_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.9186 | 0.93531 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90424 | 0.93809 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-138-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90576 | 0.93809 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90729 | 0.9396 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-004_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90788 | 0.9396 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-006_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9101 | 0.94128 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91017 | 0.94489 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-008_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91078 | 0.94489 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90402 | 0.93758 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-011_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90504 | 0.93758 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90818 | 0.93979 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | ATSI_P1-4_OES-69-013_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90892 | 0.93979 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89274 | 0.93386 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89359 | 0.93386 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | CPP_P1-4_ET CAP_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91795 | 0.93386 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.80537 | 0.93599 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.84283 | 0.93599 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 241972 AD1-140 GEN 0.57_SRT-A | 0.91668 | 0.93599 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | ATSI_P1-2_OES-138-003A_SRT-A | 0.91903 | 0.93599 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87389 | 0.93481 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.8904 | 0.93481 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.76648 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.7679 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.80545 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-035BA_SRT-A | 0.85469 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.87282 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-004_SRT-A | 0.90787 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-013_SRT-A | 0.90891 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.90997 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-4_OES-69-008_SRT-A | 0.91077 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#18134_SRT-A | 0.91126 | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | Base Case | - | 0.91699 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89352 | 0.94162 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13830_KISER_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90893 | 0.94162 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89703 | 0.94295 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13836_MIAMI_ELDEAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91244 | 0.94295 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8727 | 0.93675 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_13849_BATH_URBANA_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88187 | 0.93675 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89272 | 0.9413 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_138XX_SHELBY_QUINCY_LOGAN_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90834 | 0.9413 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89517 | 0.94216 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91193 | 0.94216 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34504_GREENE_MADISON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91411 | 0.94216 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89674 | 0.94265 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91364 | 0.94265 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34507_CLINTON_LYNCHBURG_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9138 | 0.94265 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34508_CLAY_LYNCHBURG_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89841 | 0.94366 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89504 | 0.94199 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91322 | 0.94199 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34522_CLINTON_GREENE_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91338 | 0.94199 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89658 | 0.94286 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34524_SUGARCREEK_FOSTER (DUKE)_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91404 | 0.94286 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89699 | 0.94277 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91276 | 0.94277 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34552_STUART_ATLANTA_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91427 | 0.94277 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89467 | 0.94201 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91039 | 0.94201 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8953 | 0.94212 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91273 | 0.94212 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34591_MIAMI FORT (DUKE)_WEST MILTON_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91365 | 0.94212 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89723 | 0.94307 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_34598_BATH_FOSTER (DUKE)_345KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91467 | 0.94307 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8972 | 0.94379 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_6645_LOGAN_KINGS CREEK_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91178 | 0.94379 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.8973 | 0.94319 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91259 | 0.94319 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89556 | 0.94165 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.9115 | 0.94165 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_ATLANTA_345_ATLANTA_69_BK_N_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91306 | 0.94165 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89822 | 0.9439 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_GREENE_345_GREENE_138_BK_S_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89809 | 0.94383 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89338 | 0.94152 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_LOGAN_138_LOGAN_69_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90882 | 0.94152 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_MIAMI_345_MIAMI_138_BK_E_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91394 | 0.94189 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89467 | 0.94201 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_PEORIA_345_PEORIA_69_BK_N_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91039 | 0.94201 | Yes
2025W1-N11-SVM241987 | 241987 | AE2-217_POI | 138 | 202 | 0.92 | 1.05 | DAY_P1_URBANA_22.5_MVAR_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91046 | 0.94165 | Yes
2025W1-N11-SVM241988 | 241988 | AE2-217_MAIN | 138 | 202 | 0.92 | 1.05 | 241972 AD1-140 GEN 0.57_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88991 | 0.94165 | Yes
2025W1-N11-SVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.88887 | 0.96914 | Yes
2025W1-N11-SVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90506 | 0.96914 | Yes
2025W1-N11-SVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.905 | 0.98315 | Yes
2025W1-N11-SVM253025 | 253025 | 09GIVENS | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88886 | 0.96574 | Yes
2025W1-N11-SVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.909 | 0.97649 | Yes
2025W1-N11-SVM253044 | 253044 | 09MECHAN | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.909 | 0.97352 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.87005 | 0.95803 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.88708 | 0.95803 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91626 | 0.95803 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.88702 | 0.97341 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.87005 | 0.95439 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | 0.91755 | 0.95439 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91635 | 0.9718 | Yes
2025W1-N11-SVM253085 | 253085 | 09URBANA | 138 | 209 | 0.92 | 1.05 | DAY_P1_13811_URBANA_AE2-305_138KV_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91758 | 0.96088 | Yes
2025W1-N11-SVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91447 | 0.97843 | Yes
2025W1-N11-SVM253245 | 253245 | 09EAGLE | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91446 | 0.97558 | Yes
2025W1-N11-SVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89061 | 0.97018 | Yes
2025W1-N11-SVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90672 | 0.97018 | Yes
2025W1-N11-SVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90666 | 0.98405 | Yes
2025W1-N11-SVM942860 | 942860 | AE2-305 TAP | 138 | 209 | 0.92 | 1.05 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.89061 | 0.96679 | Yes

## Volt Drop
PJM N-1-1 Voltage Drop Result (Summer 2030 Case)
FG# | Bus # | Name | KV | Area | % Vdrop | Contingency 1 | Contingency 2 | BaseVolt | ContVolt | % Vdrop | PJM Accepting Proposals | Reasons for Exclusions | Comment
2025W1-N11-SVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0109 | 0.85691 | 15.404 | Yes
2025W1-N11-SVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0109 | 0.85725 | 15.369 | Yes
2025W1-N11-SVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.011 | 0.85797 | 15.297 | Yes
2025W1-N11-SVD960800 | 960800 | AF2-371 TAP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.011 | 0.85601 | 15.502 | Yes
2025W1-N11-SVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98059 | 0.8302 | 15.039 | Yes
2025W1-N11-SVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98059 | 0.83172 | 14.887 | Yes
2025W1-N11-SVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98249 | 0.83263 | 14.986 | Yes
2025W1-N11-SVD942860 | 942860 | AE2-305 TAP | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98216 | 0.82924 | 15.292 | Yes
2025W1-N11-SVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0049 | 0.90795 | 9.697 | Yes
2025W1-N11-SVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0049 | 0.91113 | 9.379 | Yes
2025W1-N11-SVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.90851 | 9.697 | Yes
2025W1-N11-SVD940610 | 940610 | AE2-048 TAP | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0064 | 0.91018 | 9.618 | Yes
2025W1-N11-SVD315725 | 315725 | AD1-074 MAIN | 230 | 345 | 8 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99602 | 0.91101 | 8.501 | Yes
2025W1-N11-SVD314616 | 314616 | 6TRWBRDG | 230 | 345 | 8 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99276 | 0.90083 | 9.194 | Yes
2025W1-N11-SVD314616 | 314616 | 6TRWBRDG | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.99646 | 0.91572 | 8.074 | Yes
2025W1-N11-SVD314594 | 314594 | 6PLYMOUTH TP | 230 | 345 | 8 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99318 | 0.90116 | 9.201 | Yes
2025W1-N11-SVD314594 | 314594 | 6PLYMOUTH TP | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.99769 | 0.91608 | 8.161 | Yes
2025W1-N11-SVD314203 | 314203 | 6MACKEYS | 230 | 345 | 8 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99513 | 0.90274 | 9.239 | Yes
2025W1-N11-SVD314203 | 314203 | 6MACKEYS | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 1.0042 | 0.91777 | 8.641 | Yes
2025W1-N11-SVD313054 | 313054 | 6PLYMOUTH | 230 | 345 | 8 | DVP_P1-2: LN 2131_SRT-A | DVP_P1-2: LN 2034_SRT-A | 0.99318 | 0.90116 | 9.201 | Yes
2025W1-N11-SVD313054 | 313054 | 6PLYMOUTH | 230 | 345 | 8 | DVP_P1-2: LN 2034_SRT-A | DVP_P1-2: LN 2131_SRT-A | 0.9977 | 0.91608 | 8.161 | Yes
2025W1-N11-SVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.001 | 0.88783 | 11.321 | Yes
2025W1-N11-SVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.001 | 0.88945 | 11.159 | Yes
2025W1-N11-SVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.88998 | 11.125 | Yes
2025W1-N11-SVD291017 | 291017 | 09FAYETT | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.88717 | 11.454 | Yes
2025W1-N11-SVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99535 | 0.85714 | 13.821 | Yes
2025W1-N11-SVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99535 | 0.88393 | 11.142 | Yes
2025W1-N11-SVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99707 | 0.85771 | 13.936 | Yes
2025W1-N11-SVD290984 | 290984 | 05BOKESCRK | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99938 | 0.88214 | 11.724 | Yes
2025W1-N11-SVD290978 | 290978 | 05PATTONVLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99442 | 0.91261 | 8.182 | Yes
2025W1-N11-SVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98736 | 0.8093 | 17.806 | Yes
2025W1-N11-SVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98736 | 0.81431 | 17.305 | Yes
2025W1-N11-SVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98896 | 0.81502 | 17.394 | Yes
2025W1-N11-SVD290925 | 290925 | 05PARSONS2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.80829 | 18.178 | Yes
2025W1-N11-SVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99482 | 0.77969 | 21.513 | Yes
2025W1-N11-SVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99482 | 0.79005 | 20.477 | Yes
2025W1-N11-SVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99912 | 0.79075 | 20.837 | Yes
2025W1-N11-SVD290887 | 290887 | 05ROCKHOPPER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.77854 | 22.191 | Yes
2025W1-N11-SVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99565 | 0.7807 | 21.495 | Yes
2025W1-N11-SVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99565 | 0.79106 | 20.458 | Yes
2025W1-N11-SVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99994 | 0.79177 | 20.817 | Yes
2025W1-N11-SVD290886 | 290886 | 05ANGUIN 3-4 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.77955 | 22.173 | Yes
2025W1-N11-SVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0024 | 0.79381 | 20.861 | Yes
2025W1-N11-SVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.80497 | 19.745 | Yes
2025W1-N11-SVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.80569 | 20.104 | Yes
2025W1-N11-SVD290884 | 290884 | 05GREENCHL34 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.79263 | 21.53 | Yes
2025W1-N11-SVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99516 | 0.78533 | 20.983 | Yes
2025W1-N11-SVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99516 | 0.79607 | 19.908 | Yes
2025W1-N11-SVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99941 | 0.79679 | 20.262 | Yes
2025W1-N11-SVD290809 | 290809 | 05HORIZON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.78416 | 21.649 | Yes
2025W1-N11-SVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99811 | 0.78747 | 21.064 | Yes
2025W1-N11-SVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99811 | 0.7984 | 19.971 | Yes
2025W1-N11-SVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.79912 | 20.331 | Yes
2025W1-N11-SVD290779 | 290779 | 05JORDEN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.7863 | 21.74 | Yes
2025W1-N11-SVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0024 | 0.79382 | 20.86 | Yes
2025W1-N11-SVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0024 | 0.80498 | 19.744 | Yes
2025W1-N11-SVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0067 | 0.80569 | 20.104 | Yes
2025W1-N11-SVD290690 | 290690 | 05GREENCHL12 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0079 | 0.79264 | 21.529 | Yes
2025W1-N11-SVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98273 | 0.79595 | 18.678 | Yes
2025W1-N11-SVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98273 | 0.80374 | 17.899 | Yes
2025W1-N11-SVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98557 | 0.80443 | 18.114 | Yes
2025W1-N11-SVD290679 | 290679 | 05BEACON | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98557 | 0.79479 | 19.078 | Yes
2025W1-N11-SVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99501 | 0.78521 | 20.979 | Yes
2025W1-N11-SVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99501 | 0.79593 | 19.908 | Yes
2025W1-N11-SVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99925 | 0.79664 | 20.261 | Yes
2025W1-N11-SVD290628 | 290628 | 05BADGER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.78405 | 21.644 | Yes
2025W1-N11-SVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96946 | 0.80784 | 16.162 | Yes
2025W1-N11-SVD290620 | 290620 | 05MARYSVL_RM | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97148 | 0.80842 | 16.305 | Yes
2025W1-N11-SVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96957 | 0.80843 | 16.114 | Yes
2025W1-N11-SVD290608 | 290608 | 05MARYSVL_RS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97133 | 0.80901 | 16.232 | Yes
2025W1-N11-SVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99155 | 0.79316 | 19.839 | Yes
2025W1-N11-SVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99155 | 0.80456 | 18.699 | Yes
2025W1-N11-SVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99577 | 0.80526 | 19.05 | Yes
2025W1-N11-SVD290573 | 290573 | 05INNOVATION | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99703 | 0.79195 | 20.508 | Yes
2025W1-N11-SVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99976 | 0.87422 | 12.554 | Yes
2025W1-N11-SVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99976 | 0.87556 | 12.42 | Yes
2025W1-N11-SVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99886 | 0.87489 | 12.398 | Yes
2025W1-N11-SVD290534 | 290534 | 05LUTZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.87479 | 12.603 | Yes
2025W1-N11-SVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98338 | 0.79735 | 18.602 | Yes
2025W1-N11-SVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98338 | 0.80642 | 17.695 | Yes
2025W1-N11-SVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98699 | 0.80709 | 17.99 | Yes
2025W1-N11-SVD290516 | 290516 | 05CELTIC | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98634 | 0.79607 | 19.026 | Yes
2025W1-N11-SVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98718 | 0.78742 | 19.976 | Yes
2025W1-N11-SVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98718 | 0.79636 | 19.082 | Yes
2025W1-N11-SVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99063 | 0.79707 | 19.356 | Yes
2025W1-N11-SVD290499 | 290499 | 05SCHERERSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99128 | 0.78625 | 20.504 | Yes
2025W1-N11-SVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99843 | 0.85692 | 14.151 | Yes
2025W1-N11-SVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99843 | 0.857 | 14.143 | Yes
2025W1-N11-SVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99907 | 0.85768 | 14.139 | Yes
2025W1-N11-SVD290459 | 290459 | 05MT PERRYSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.856 | 14.483 | Yes
2025W1-N11-SVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97655 | 0.78356 | 19.299 | Yes
2025W1-N11-SVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97655 | 0.7923 | 18.425 | Yes
2025W1-N11-SVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98005 | 0.79297 | 18.708 | Yes
2025W1-N11-SVD290413 | 290413 | 05KILEVILLE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98004 | 0.78234 | 19.77 | Yes
2025W1-N11-SVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99569 | 0.78113 | 21.457 | Yes
2025W1-N11-SVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99569 | 0.79164 | 20.405 | Yes
2025W1-N11-SVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.79235 | 20.766 | Yes
2025W1-N11-SVD290377 | 290377 | 05BRIE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.77997 | 22.136 | Yes
2025W1-N11-SVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98711 | 0.79447 | 19.264 | Yes
2025W1-N11-SVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98711 | 0.80146 | 18.565 | Yes
2025W1-N11-SVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98972 | 0.80218 | 18.754 | Yes
2025W1-N11-SVD290364 | 290364 | 05TRABUE2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99042 | 0.79336 | 19.706 | Yes
2025W1-N11-SVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9827 | 0.79725 | 18.545 | Yes
2025W1-N11-SVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9827 | 0.80497 | 17.774 | Yes
2025W1-N11-SVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98552 | 0.80566 | 17.986 | Yes
2025W1-N11-SVD290328 | 290328 | 05COSGRAY | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9855 | 0.79609 | 18.94 | Yes
2025W1-N11-SVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99526 | 0.78021 | 21.504 | Yes
2025W1-N11-SVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99526 | 0.79057 | 20.468 | Yes
2025W1-N11-SVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99955 | 0.79128 | 20.827 | Yes
2025W1-N11-SVD290316 | 290316 | 05EMPEROR Z2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.77906 | 22.183 | Yes
2025W1-N11-SVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99524 | 0.78019 | 21.505 | Yes
2025W1-N11-SVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99524 | 0.79055 | 20.469 | Yes
2025W1-N11-SVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99954 | 0.79126 | 20.828 | Yes
2025W1-N11-SVD290315 | 290315 | 05EMPEROR Z1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.77904 | 22.183 | Yes
2025W1-N11-SVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98889 | 0.82966 | 15.923 | Yes
2025W1-N11-SVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98889 | 0.83327 | 15.562 | Yes
2025W1-N11-SVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99119 | 0.83396 | 15.723 | Yes
2025W1-N11-SVD290313 | 290313 | 05CONESV_XFL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99215 | 0.82863 | 16.351 | Yes
2025W1-N11-SVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99895 | 0.78922 | 20.974 | Yes
2025W1-N11-SVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99895 | 0.80024 | 19.871 | Yes
2025W1-N11-SVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.80096 | 20.231 | Yes
2025W1-N11-SVD290254 | 290254 | 05INNOVATION | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.78804 | 21.649 | Yes
2025W1-N11-SVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9912 | 0.80994 | 18.126 | Yes
2025W1-N11-SVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9912 | 0.81263 | 17.857 | Yes
2025W1-N11-SVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99286 | 0.8134 | 17.946 | Yes
2025W1-N11-SVD290241 | 290241 | 05SIFFORD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99501 | 0.80891 | 18.61 | Yes
2025W1-N11-SVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99525 | 0.7802 | 21.505 | Yes
2025W1-N11-SVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99525 | 0.79056 | 20.469 | Yes
2025W1-N11-SVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99955 | 0.79127 | 20.828 | Yes
2025W1-N11-SVD290239 | 290239 | 05HUMBOLDT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.77905 | 22.183 | Yes
2025W1-N11-SVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98738 | 0.80933 | 17.805 | Yes
2025W1-N11-SVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98738 | 0.81434 | 17.304 | Yes
2025W1-N11-SVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98899 | 0.81506 | 17.393 | Yes
2025W1-N11-SVD290230 | 290230 | 05CYPRUS12 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99009 | 0.80832 | 18.177 | Yes
2025W1-N11-SVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9945 | 0.85972 | 13.478 | Yes
2025W1-N11-SVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9945 | 0.86066 | 13.384 | Yes
2025W1-N11-SVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99376 | 0.86041 | 13.336 | Yes
2025W1-N11-SVD290113 | 290113 | 05WESTFALL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99572 | 0.85986 | 13.586 | Yes
2025W1-N11-SVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98461 | 0.79585 | 18.876 | Yes
2025W1-N11-SVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98461 | 0.80824 | 17.637 | Yes
2025W1-N11-SVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98885 | 0.8089 | 17.995 | Yes
2025W1-N11-SVD289528 | 289528 | 05MALIS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98891 | 0.79454 | 19.438 | Yes
2025W1-N11-SVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98941 | 0.83857 | 15.084 | Yes
2025W1-N11-SVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98941 | 0.84286 | 14.656 | Yes
2025W1-N11-SVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99037 | 0.8435 | 14.688 | Yes
2025W1-N11-SVD289114 | 289114 | 05BIG PLAIN | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99086 | 0.83768 | 15.318 | Yes
2025W1-N11-SVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9793 | 0.78761 | 19.168 | Yes
2025W1-N11-SVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9793 | 0.79644 | 18.285 | Yes
2025W1-N11-SVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98284 | 0.79712 | 18.572 | Yes
2025W1-N11-SVD288936 | 288936 | 05CELTIC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98266 | 0.78638 | 19.628 | Yes
2025W1-N11-SVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99296 | 0.90685 | 8.61 | Yes
2025W1-N11-SVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99296 | 0.91016 | 8.279 | Yes
2025W1-N11-SVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.90741 | 8.37 | Yes
2025W1-N11-SVD288835 | 288835 | 05BLAIN_TAP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9933 | 0.90954 | 8.375 | Yes
2025W1-N11-SVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98638 | 0.81439 | 17.199 | Yes
2025W1-N11-SVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98638 | 0.81906 | 16.732 | Yes
2025W1-N11-SVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98785 | 0.81975 | 16.809 | Yes
2025W1-N11-SVD288778 | 288778 | 05CYPRUS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98898 | 0.81341 | 17.557 | Yes
2025W1-N11-SVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9874 | 0.80935 | 17.804 | Yes
2025W1-N11-SVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9874 | 0.81436 | 17.303 | Yes
2025W1-N11-SVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.989 | 0.81508 | 17.393 | Yes
2025W1-N11-SVD288776 | 288776 | 05CYPRUS34 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99011 | 0.80834 | 18.177 | Yes
2025W1-N11-SVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99282 | 0.78809 | 20.473 | Yes
2025W1-N11-SVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99282 | 0.79883 | 19.399 | Yes
2025W1-N11-SVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99694 | 0.79955 | 19.739 | Yes
2025W1-N11-SVD288729 | 288729 | 05SOUDER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99813 | 0.78691 | 21.122 | Yes
2025W1-N11-SVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99092 | 0.79328 | 19.763 | Yes
2025W1-N11-SVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99092 | 0.80505 | 18.587 | Yes
2025W1-N11-SVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99517 | 0.80575 | 18.942 | Yes
2025W1-N11-SVD288727 | 288727 | 05CURLEYS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.79206 | 20.44 | Yes
2025W1-N11-SVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98463 | 0.78694 | 19.769 | Yes
2025W1-N11-SVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98463 | 0.79897 | 18.566 | Yes
2025W1-N11-SVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98893 | 0.79966 | 18.927 | Yes
2025W1-N11-SVD288726 | 288726 | 05GREENCHPL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99036 | 0.78573 | 20.464 | Yes
2025W1-N11-SVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99348 | 0.85949 | 13.4 | Yes
2025W1-N11-SVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99348 | 0.86279 | 13.069 | Yes
2025W1-N11-SVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99408 | 0.86339 | 13.069 | Yes
2025W1-N11-SVD288724 | 288724 | 05CHENOWETH | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99448 | 0.85869 | 13.579 | Yes
2025W1-N11-SVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99521 | 0.78034 | 21.488 | Yes
2025W1-N11-SVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99521 | 0.7908 | 20.442 | Yes
2025W1-N11-SVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99953 | 0.7915 | 20.802 | Yes
2025W1-N11-SVD288721 | 288721 | 05MACY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.77918 | 22.167 | Yes
2025W1-N11-SVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99119 | 0.79072 | 20.047 | Yes
2025W1-N11-SVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99119 | 0.79941 | 19.178 | Yes
2025W1-N11-SVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99448 | 0.80013 | 19.435 | Yes
2025W1-N11-SVD288718 | 288718 | 05GILES | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99521 | 0.78957 | 20.564 | Yes
2025W1-N11-SVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9887 | 0.79343 | 19.526 | Yes
2025W1-N11-SVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9887 | 0.80608 | 18.262 | Yes
2025W1-N11-SVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99309 | 0.80677 | 18.632 | Yes
2025W1-N11-SVD288705 | 288705 | 05VASSEL2XFL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99459 | 0.7922 | 20.24 | Yes
2025W1-N11-SVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98643 | 0.79438 | 19.205 | Yes
2025W1-N11-SVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98643 | 0.80126 | 18.517 | Yes
2025W1-N11-SVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98899 | 0.80198 | 18.701 | Yes
2025W1-N11-SVD288701 | 288701 | 05MILEPOST | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9897 | 0.79328 | 19.642 | Yes
2025W1-N11-SVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0046 | 0.79662 | 20.797 | Yes
2025W1-N11-SVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0046 | 0.80768 | 19.691 | Yes
2025W1-N11-SVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0089 | 0.80839 | 20.049 | Yes
2025W1-N11-SVD288643 | 288643 | 05KIBER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.01 | 0.79545 | 21.455 | Yes
2025W1-N11-SVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9805 | 0.78413 | 19.637 | Yes
2025W1-N11-SVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9805 | 0.79251 | 18.799 | Yes
2025W1-N11-SVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98382 | 0.7932 | 19.062 | Yes
2025W1-N11-SVD288640 | 288640 | 05DUBLINX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98423 | 0.78295 | 20.128 | Yes
2025W1-N11-SVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99363 | 0.77825 | 21.538 | Yes
2025W1-N11-SVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99363 | 0.78859 | 20.505 | Yes
2025W1-N11-SVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99794 | 0.78929 | 20.865 | Yes
2025W1-N11-SVD288619 | 288619 | 05NBY6 Z2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99927 | 0.77711 | 22.217 | Yes
2025W1-N11-SVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99363 | 0.77825 | 21.538 | Yes
2025W1-N11-SVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99363 | 0.78859 | 20.505 | Yes
2025W1-N11-SVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99794 | 0.78929 | 20.865 | Yes
2025W1-N11-SVD288618 | 288618 | 05NBY6 Z1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99927 | 0.77711 | 22.217 | Yes
2025W1-N11-SVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99343 | 0.778 | 21.542 | Yes
2025W1-N11-SVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99343 | 0.78833 | 20.509 | Yes
2025W1-N11-SVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99773 | 0.78903 | 20.87 | Yes
2025W1-N11-SVD288617 | 288617 | 05NBY7 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99907 | 0.77685 | 22.221 | Yes
2025W1-N11-SVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99361 | 0.77823 | 21.539 | Yes
2025W1-N11-SVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99361 | 0.78856 | 20.505 | Yes
2025W1-N11-SVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99792 | 0.78927 | 20.865 | Yes
2025W1-N11-SVD288616 | 288616 | 05NBY6 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99926 | 0.77708 | 22.217 | Yes
2025W1-N11-SVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99465 | 0.77949 | 21.516 | Yes
2025W1-N11-SVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99465 | 0.78984 | 20.481 | Yes
2025W1-N11-SVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99895 | 0.79054 | 20.841 | Yes
2025W1-N11-SVD288615 | 288615 | 05S.ROCKHOPR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.77834 | 22.195 | Yes
2025W1-N11-SVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99483 | 0.77971 | 21.513 | Yes
2025W1-N11-SVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99483 | 0.79006 | 20.477 | Yes
2025W1-N11-SVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99913 | 0.79076 | 20.837 | Yes
2025W1-N11-SVD288614 | 288614 | 05ROCKHOPPZ2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.77856 | 22.191 | Yes
2025W1-N11-SVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99484 | 0.77972 | 21.512 | Yes
2025W1-N11-SVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99484 | 0.79007 | 20.477 | Yes
2025W1-N11-SVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99914 | 0.79078 | 20.836 | Yes
2025W1-N11-SVD288613 | 288613 | 05ROCKHOPPZ1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.77857 | 22.191 | Yes
2025W1-N11-SVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9995 | 0.78994 | 20.956 | Yes
2025W1-N11-SVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9995 | 0.801 | 19.85 | Yes
2025W1-N11-SVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.80171 | 20.209 | Yes
2025W1-N11-SVD288603 | 288603 | 05TASJAN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.78876 | 21.63 | Yes
2025W1-N11-SVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99608 | 0.78704 | 20.905 | Yes
2025W1-N11-SVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99608 | 0.79781 | 19.827 | Yes
2025W1-N11-SVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.79853 | 20.179 | Yes
2025W1-N11-SVD288579 | 288579 | 05FIESTA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.78587 | 21.567 | Yes
2025W1-N11-SVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99086 | 0.79304 | 19.783 | Yes
2025W1-N11-SVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99086 | 0.80474 | 18.612 | Yes
2025W1-N11-SVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99512 | 0.80544 | 18.967 | Yes
2025W1-N11-SVD288569 | 288569 | 05BERMUDA | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.79182 | 20.459 | Yes
2025W1-N11-SVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99542 | 0.85724 | 13.818 | Yes
2025W1-N11-SVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99542 | 0.88402 | 11.139 | Yes
2025W1-N11-SVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99713 | 0.8578 | 13.932 | Yes
2025W1-N11-SVD270280 | 270280 | AF1-227 MAIN | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99943 | 0.88223 | 11.72 | Yes
2025W1-N11-SVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98768 | 0.84086 | 14.682 | Yes
2025W1-N11-SVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98768 | 0.84484 | 14.284 | Yes
2025W1-N11-SVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98991 | 0.84138 | 14.854 | Yes
2025W1-N11-SVD253283 | 253283 | 09E.LOGAN | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99031 | 0.84352 | 14.679 | Yes
2025W1-N11-SVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99284 | 0.83772 | 15.512 | Yes
2025W1-N11-SVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99284 | 0.86462 | 12.822 | Yes
2025W1-N11-SVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99526 | 0.83829 | 15.697 | Yes
2025W1-N11-SVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99765 | 0.86265 | 13.5 | Yes
2025W1-N11-SVD253251 | 253251 | 09PEORIA | 345 | 209 | 8 | DAY_P1_6931_PEORIA_DARBY_69KV_SRT-A | DAY_P1_34556_PEORIA_MARYSVILLE(AEP)_345KV_SRT-A | 1.003 | 0.9163 | 8.675 | Yes
2025W1-N11-SVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9969 | 0.88451 | 11.239 | Yes
2025W1-N11-SVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9969 | 0.88611 | 11.079 | Yes
2025W1-N11-SVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99709 | 0.88664 | 11.045 | Yes
2025W1-N11-SVD253248 | 253248 | 09MADISN | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99757 | 0.88385 | 11.372 | Yes
2025W1-N11-SVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98374 | 0.82273 | 16.101 | Yes
2025W1-N11-SVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98374 | 0.82638 | 15.736 | Yes
2025W1-N11-SVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98672 | 0.82777 | 15.895 | Yes
2025W1-N11-SVD253245 | 253245 | 09EAGLE | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.82163 | 16.398 | Yes
2025W1-N11-SVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98822 | 0.84296 | 14.526 | Yes
2025W1-N11-SVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98822 | 0.8489 | 13.932 | Yes
2025W1-N11-SVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99012 | 0.84344 | 14.668 | Yes
2025W1-N11-SVD253101 | 253101 | 09BLUJK | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99056 | 0.84755 | 14.301 | Yes
2025W1-N11-SVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.993 | 0.86026 | 13.273 | Yes
2025W1-N11-SVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.993 | 0.8633 | 12.969 | Yes
2025W1-N11-SVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99326 | 0.86391 | 12.935 | Yes
2025W1-N11-SVD253100 | 253100 | 09ATLNTA | 345 | 209 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9939 | 0.8595 | 13.44 | Yes
2025W1-N11-SVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97113 | 0.82511 | 14.602 | Yes
2025W1-N11-SVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97113 | 0.82552 | 14.561 | Yes
2025W1-N11-SVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97248 | 0.8262 | 14.629 | Yes
2025W1-N11-SVD253085 | 253085 | 09URBANA | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97256 | 0.82421 | 14.835 | Yes
2025W1-N11-SVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98292 | 0.82413 | 15.879 | Yes
2025W1-N11-SVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98292 | 0.82733 | 15.559 | Yes
2025W1-N11-SVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98566 | 0.8286 | 15.705 | Yes
2025W1-N11-SVD253044 | 253044 | 09MECHAN | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98473 | 0.82307 | 16.165 | Yes
2025W1-N11-SVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97979 | 0.82975 | 15.004 | Yes
2025W1-N11-SVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97979 | 0.83118 | 14.861 | Yes
2025W1-N11-SVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98164 | 0.83207 | 14.957 | Yes
2025W1-N11-SVD253025 | 253025 | 09GIVENS | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98135 | 0.8288 | 15.255 | Yes
2025W1-N11-SVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98826 | 0.81703 | 17.123 | Yes
2025W1-N11-SVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98826 | 0.82293 | 16.533 | Yes
2025W1-N11-SVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99248 | 0.82484 | 16.764 | Yes
2025W1-N11-SVD253021 | 253021 | 09DARBY | 138 | 209 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99052 | 0.8158 | 17.472 | Yes
2025W1-N11-SVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99634 | 0.8862 | 11.014 | Yes
2025W1-N11-SVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99634 | 0.88839 | 10.795 | Yes
2025W1-N11-SVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9969 | 0.88675 | 11.015 | Yes
2025W1-N11-SVD247980 | 247980 | 05RUSTIC SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99841 | 0.88754 | 11.086 | Yes
2025W1-N11-SVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99699 | 0.89871 | 9.829 | Yes
2025W1-N11-SVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99699 | 0.90111 | 9.588 | Yes
2025W1-N11-SVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99764 | 0.89919 | 9.845 | Yes
2025W1-N11-SVD247979 | 247979 | 05NORFLD SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99906 | 0.90029 | 9.877 | Yes
2025W1-N11-SVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0064 | 0.84127 | 16.511 | Yes
2025W1-N11-SVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0064 | 0.84909 | 15.73 | Yes
2025W1-N11-SVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0087 | 0.85014 | 15.86 | Yes
2025W1-N11-SVD247972 | 247972 | 05CONDIT SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0088 | 0.84008 | 16.875 | Yes
2025W1-N11-SVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99291 | 0.87327 | 11.963 | Yes
2025W1-N11-SVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99291 | 0.87897 | 11.393 | Yes
2025W1-N11-SVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99019 | 0.87404 | 11.615 | Yes
2025W1-N11-SVD247945 | 247945 | 05ELLIOTT 2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.87816 | 11.604 | Yes
2025W1-N11-SVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99218 | 0.79894 | 19.324 | Yes
2025W1-N11-SVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99218 | 0.80494 | 18.724 | Yes
2025W1-N11-SVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99433 | 0.80567 | 18.866 | Yes
2025W1-N11-SVD247931 | 247931 | 05VINE_GS_X | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99551 | 0.79789 | 19.762 | Yes
2025W1-N11-SVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99729 | 0.86952 | 12.777 | Yes
2025W1-N11-SVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99729 | 0.87303 | 12.427 | Yes
2025W1-N11-SVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99567 | 0.87024 | 12.543 | Yes
2025W1-N11-SVD247930 | 247930 | 05FIDLSTX SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99859 | 0.87222 | 12.637 | Yes
2025W1-N11-SVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98659 | 0.80618 | 18.04 | Yes
2025W1-N11-SVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98659 | 0.81159 | 17.5 | Yes
2025W1-N11-SVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98838 | 0.8123 | 17.608 | Yes
2025W1-N11-SVD247896 | 247896 | 05BOLTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98924 | 0.80516 | 18.409 | Yes
2025W1-N11-SVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98242 | 0.7851 | 19.732 | Yes
2025W1-N11-SVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98242 | 0.79329 | 18.914 | Yes
2025W1-N11-SVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98565 | 0.79398 | 19.167 | Yes
2025W1-N11-SVD247873 | 247873 | 05BRITTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98615 | 0.78394 | 20.221 | Yes
2025W1-N11-SVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98411 | 0.84534 | 13.877 | Yes
2025W1-N11-SVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98411 | 0.84643 | 13.768 | Yes
2025W1-N11-SVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98328 | 0.84603 | 13.725 | Yes
2025W1-N11-SVD247862 | 247862 | 05TUSCANY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98538 | 0.84562 | 13.977 | Yes
2025W1-N11-SVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99613 | 0.8906 | 10.553 | Yes
2025W1-N11-SVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99613 | 0.89538 | 10.075 | Yes
2025W1-N11-SVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99419 | 0.89129 | 10.291 | Yes
2025W1-N11-SVD247791 | 247791 | 05ELK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9968 | 0.89463 | 10.216 | Yes
2025W1-N11-SVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99656 | 0.79631 | 20.025 | Yes
2025W1-N11-SVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99656 | 0.80453 | 19.203 | Yes
2025W1-N11-SVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.80524 | 19.488 | Yes
2025W1-N11-SVD247767 | 247767 | 05HAZELTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.79521 | 20.635 | Yes
2025W1-N11-SVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98628 | 0.8018 | 18.448 | Yes
2025W1-N11-SVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98628 | 0.81159 | 17.469 | Yes
2025W1-N11-SVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9903 | 0.81225 | 17.805 | Yes
2025W1-N11-SVD247741 | 247741 | 05HYATT SW2 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98943 | 0.80043 | 18.9 | Yes
2025W1-N11-SVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98863 | 0.79342 | 19.522 | Yes
2025W1-N11-SVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98863 | 0.80602 | 18.261 | Yes
2025W1-N11-SVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99301 | 0.80671 | 18.63 | Yes
2025W1-N11-SVD247728 | 247728 | 05VASSEL_XFL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99453 | 0.79218 | 20.235 | Yes
2025W1-N11-SVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99204 | 0.89082 | 10.122 | Yes
2025W1-N11-SVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99204 | 0.89712 | 9.492 | Yes
2025W1-N11-SVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.8916 | 9.713 | Yes
2025W1-N11-SVD247679 | 247679 | 05LEE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.89632 | 9.658 | Yes
2025W1-N11-SVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9943 | 0.80453 | 18.977 | Yes
2025W1-N11-SVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9943 | 0.81019 | 18.411 | Yes
2025W1-N11-SVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99649 | 0.81092 | 18.557 | Yes
2025W1-N11-SVD247623 | 247623 | 05GROVES2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99791 | 0.80348 | 19.443 | Yes
2025W1-N11-SVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99881 | 0.83096 | 16.785 | Yes
2025W1-N11-SVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99881 | 0.8334 | 16.541 | Yes
2025W1-N11-SVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99953 | 0.83414 | 16.54 | Yes
2025W1-N11-SVD247562 | 247562 | 05LOCKBOURNE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.83001 | 17.051 | Yes
2025W1-N11-SVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97813 | 0.78634 | 19.179 | Yes
2025W1-N11-SVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97813 | 0.79443 | 18.37 | Yes
2025W1-N11-SVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98129 | 0.79511 | 18.618 | Yes
2025W1-N11-SVD247509 | 247509 | 05HAYDEN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98147 | 0.78517 | 19.631 | Yes
2025W1-N11-SVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99728 | 0.85094 | 14.634 | Yes
2025W1-N11-SVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99728 | 0.85162 | 14.566 | Yes
2025W1-N11-SVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99798 | 0.85164 | 14.634 | Yes
2025W1-N11-SVD247497 | 247497 | 05CLOUSE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.8507 | 14.939 | Yes
2025W1-N11-SVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0044 | 0.90908 | 9.534 | Yes
2025W1-N11-SVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0044 | 0.91038 | 9.404 | Yes
2025W1-N11-SVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.005 | 0.91095 | 9.408 | Yes
2025W1-N11-SVD247336 | 247336 | 05APPLE V SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.90839 | 9.654 | Yes
2025W1-N11-SVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0036 | 0.89898 | 10.458 | Yes
2025W1-N11-SVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0036 | 0.89943 | 10.413 | Yes
2025W1-N11-SVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.89999 | 10.419 | Yes
2025W1-N11-SVD247303 | 247303 | 05WAKATOMIKA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.89827 | 10.626 | Yes
2025W1-N11-SVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97694 | 0.783 | 19.395 | Yes
2025W1-N11-SVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97694 | 0.79148 | 18.546 | Yes
2025W1-N11-SVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98033 | 0.79216 | 18.817 | Yes
2025W1-N11-SVD247199 | 247199 | 05AMLIN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98046 | 0.7818 | 19.866 | Yes
2025W1-N11-SVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9948 | 0.86967 | 12.513 | Yes
2025W1-N11-SVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9948 | 0.87296 | 12.184 | Yes
2025W1-N11-SVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.87037 | 12.279 | Yes
2025W1-N11-SVD247148 | 247148 | 05SBLMSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99595 | 0.87217 | 12.379 | Yes
2025W1-N11-SVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99657 | 0.87477 | 12.18 | Yes
2025W1-N11-SVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99657 | 0.87671 | 11.987 | Yes
2025W1-N11-SVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99711 | 0.87539 | 12.172 | Yes
2025W1-N11-SVD247083 | 247083 | 05NPHISS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99872 | 0.87583 | 12.289 | Yes
2025W1-N11-SVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0081 | 0.86148 | 14.659 | Yes
2025W1-N11-SVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0081 | 0.86304 | 14.502 | Yes
2025W1-N11-SVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.86221 | 14.522 | Yes
2025W1-N11-SVD247067 | 247067 | 05GOODHP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0088 | 0.86217 | 14.663 | Yes
2025W1-N11-SVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98478 | 0.84458 | 14.02 | Yes
2025W1-N11-SVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98478 | 0.84552 | 13.927 | Yes
2025W1-N11-SVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98403 | 0.84528 | 13.875 | Yes
2025W1-N11-SVD247019 | 247019 | 05NEVILLE SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98608 | 0.84469 | 14.139 | Yes
2025W1-N11-SVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99251 | 0.79616 | 19.635 | Yes
2025W1-N11-SVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99251 | 0.8036 | 18.89 | Yes
2025W1-N11-SVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9953 | 0.80433 | 19.097 | Yes
2025W1-N11-SVD246907 | 246907 | 05W.CAMPUS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99605 | 0.79504 | 20.101 | Yes
2025W1-N11-SVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99099 | 0.87107 | 11.992 | Yes
2025W1-N11-SVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99099 | 0.8733 | 11.769 | Yes
2025W1-N11-SVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98956 | 0.87173 | 11.783 | Yes
2025W1-N11-SVD246890 | 246890 | 05HOPETN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.87256 | 11.939 | Yes
2025W1-N11-SVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99568 | 0.87637 | 11.931 | Yes
2025W1-N11-SVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99568 | 0.87836 | 11.732 | Yes
2025W1-N11-SVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99427 | 0.877 | 11.727 | Yes
2025W1-N11-SVD246889 | 246889 | 05BIERSR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99667 | 0.87763 | 11.904 | Yes
2025W1-N11-SVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99228 | 0.8743 | 11.798 | Yes
2025W1-N11-SVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99228 | 0.87642 | 11.586 | Yes
2025W1-N11-SVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99065 | 0.87488 | 11.577 | Yes
2025W1-N11-SVD246888 | 246888 | 05BIERSR | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99335 | 0.87571 | 11.764 | Yes
2025W1-N11-SVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99868 | 0.87337 | 12.53 | Yes
2025W1-N11-SVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99868 | 0.87409 | 12.458 | Yes
2025W1-N11-SVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99932 | 0.874 | 12.533 | Yes
2025W1-N11-SVD246851 | 246851 | 05CULBERTSON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.87321 | 12.723 | Yes
2025W1-N11-SVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99812 | 0.79833 | 19.98 | Yes
2025W1-N11-SVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99812 | 0.80632 | 19.181 | Yes
2025W1-N11-SVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.80706 | 19.43 | Yes
2025W1-N11-SVD246765 | 246765 | 05OUTERB | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.79722 | 20.543 | Yes
2025W1-N11-SVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99031 | 0.80545 | 18.486 | Yes
2025W1-N11-SVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99031 | 0.81055 | 17.976 | Yes
2025W1-N11-SVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99226 | 0.81128 | 18.098 | Yes
2025W1-N11-SVD246761 | 246761 | 05THREEC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99372 | 0.80443 | 18.93 | Yes
2025W1-N11-SVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98922 | 0.79594 | 19.328 | Yes
2025W1-N11-SVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98922 | 0.80809 | 18.113 | Yes
2025W1-N11-SVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.80889 | 18.461 | Yes
2025W1-N11-SVD246753 | 246753 | 05VASSEL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99451 | 0.79471 | 19.981 | Yes
2025W1-N11-SVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98864 | 0.79332 | 19.532 | Yes
2025W1-N11-SVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98864 | 0.80591 | 18.273 | Yes
2025W1-N11-SVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99302 | 0.8066 | 18.642 | Yes
2025W1-N11-SVD246752 | 246752 | 05VASSEL | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99449 | 0.79208 | 20.241 | Yes
2025W1-N11-SVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9661 | 0.78116 | 18.494 | Yes
2025W1-N11-SVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9661 | 0.79662 | 16.948 | Yes
2025W1-N11-SVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97139 | 0.79726 | 17.413 | Yes
2025W1-N11-SVD246751 | 246751 | 05VASSEL | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97503 | 0.77992 | 19.511 | Yes
2025W1-N11-SVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98886 | 0.79681 | 19.204 | Yes
2025W1-N11-SVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98886 | 0.8037 | 18.516 | Yes
2025W1-N11-SVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99135 | 0.80442 | 18.693 | Yes
2025W1-N11-SVD246716 | 246716 | 05PHILLIPI | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99211 | 0.79572 | 19.639 | Yes
2025W1-N11-SVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98642 | 0.80262 | 18.38 | Yes
2025W1-N11-SVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98642 | 0.81208 | 17.434 | Yes
2025W1-N11-SVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99043 | 0.81274 | 17.769 | Yes
2025W1-N11-SVD246523 | 246523 | 05HYATT SW1 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98942 | 0.80125 | 18.817 | Yes
2025W1-N11-SVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99489 | 0.78489 | 21 | Yes
2025W1-N11-SVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99489 | 0.79552 | 19.937 | Yes
2025W1-N11-SVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99912 | 0.79624 | 20.289 | Yes
2025W1-N11-SVD246385 | 246385 | 05JUGST 7-11 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.78372 | 21.665 | Yes
2025W1-N11-SVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.989 | 0.78861 | 20.039 | Yes
2025W1-N11-SVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.989 | 0.79746 | 19.153 | Yes
2025W1-N11-SVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99241 | 0.79818 | 19.423 | Yes
2025W1-N11-SVD246370 | 246370 | 05HUNTLEY2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99308 | 0.78744 | 20.564 | Yes
2025W1-N11-SVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98489 | 0.78712 | 19.778 | Yes
2025W1-N11-SVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98489 | 0.79679 | 18.811 | Yes
2025W1-N11-SVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98875 | 0.79749 | 19.126 | Yes
2025W1-N11-SVD246312 | 246312 | 05BABBITT | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9901 | 0.78598 | 20.413 | Yes
2025W1-N11-SVD246310 | 246310 | 05MEIGS SW1Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0004 | 0.91819 | 8.217 | Yes
2025W1-N11-SVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99898 | 0.85524 | 14.374 | Yes
2025W1-N11-SVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99898 | 0.85646 | 14.252 | Yes
2025W1-N11-SVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.85714 | 14.288 | Yes
2025W1-N11-SVD246308 | 246308 | 05NEWARKC_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.85431 | 14.711 | Yes
2025W1-N11-SVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99565 | 0.78068 | 21.497 | Yes
2025W1-N11-SVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99565 | 0.79105 | 20.46 | Yes
2025W1-N11-SVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99995 | 0.79175 | 20.819 | Yes
2025W1-N11-SVD246177 | 246177 | 05ANGUIN 1-2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.77953 | 22.175 | Yes
2025W1-N11-SVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99325 | 0.79634 | 19.691 | Yes
2025W1-N11-SVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99325 | 0.80377 | 18.948 | Yes
2025W1-N11-SVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99602 | 0.8045 | 19.152 | Yes
2025W1-N11-SVD246094 | 246094 | 05VINE_X | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99676 | 0.79523 | 20.153 | Yes
2025W1-N11-SVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0018 | 0.82389 | 17.79 | Yes
2025W1-N11-SVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.82596 | 17.583 | Yes
2025W1-N11-SVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0034 | 0.82674 | 17.663 | Yes
2025W1-N11-SVD246021 | 246021 | 05W.LANCAST2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.82287 | 18.28 | Yes
2025W1-N11-SVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99653 | 0.87481 | 12.172 | Yes
2025W1-N11-SVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99653 | 0.87677 | 11.976 | Yes
2025W1-N11-SVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99706 | 0.87543 | 12.163 | Yes
2025W1-N11-SVD246010 | 246010 | 05PHILO2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99868 | 0.87589 | 12.279 | Yes
2025W1-N11-SVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99921 | 0.85363 | 14.558 | Yes
2025W1-N11-SVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99921 | 0.85593 | 14.328 | Yes
2025W1-N11-SVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.8566 | 14.4 | Yes
2025W1-N11-SVD245964 | 245964 | 05N.NEWARK2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.85268 | 14.899 | Yes
2025W1-N11-SVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98943 | 0.80561 | 18.382 | Yes
2025W1-N11-SVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98943 | 0.81515 | 17.428 | Yes
2025W1-N11-SVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99316 | 0.81632 | 17.684 | Yes
2025W1-N11-SVD245962 | 245962 | 05DLAWAR3 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99291 | 0.80436 | 18.855 | Yes
2025W1-N11-SVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98941 | 0.80558 | 18.383 | Yes
2025W1-N11-SVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98941 | 0.81512 | 17.429 | Yes
2025W1-N11-SVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99314 | 0.81629 | 17.685 | Yes
2025W1-N11-SVD245952 | 245952 | 05DLAWAR1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99289 | 0.80433 | 18.856 | Yes
2025W1-N11-SVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99226 | 0.79572 | 19.653 | Yes
2025W1-N11-SVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99226 | 0.80313 | 18.913 | Yes
2025W1-N11-SVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99503 | 0.80386 | 19.117 | Yes
2025W1-N11-SVD245853 | 245853 | 05HESS SOUTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99578 | 0.79461 | 20.118 | Yes
2025W1-N11-SVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9901 | 0.8442 | 14.59 | Yes
2025W1-N11-SVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9901 | 0.8481 | 14.2 | Yes
2025W1-N11-SVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99073 | 0.84875 | 14.199 | Yes
2025W1-N11-SVD245769 | 245769 | 05ADKINS | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99133 | 0.84335 | 14.799 | Yes
2025W1-N11-SVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99706 | 0.78614 | 21.093 | Yes
2025W1-N11-SVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99706 | 0.79634 | 20.072 | Yes
2025W1-N11-SVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0012 | 0.79705 | 20.419 | Yes
2025W1-N11-SVD245492 | 245492 | 05BABBIT 5-6 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.78499 | 21.758 | Yes
2025W1-N11-SVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99689 | 0.78562 | 21.127 | Yes
2025W1-N11-SVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99689 | 0.79585 | 20.104 | Yes
2025W1-N11-SVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.79656 | 20.452 | Yes
2025W1-N11-SVD245491 | 245491 | 05BABBIT 3-4 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.78447 | 21.794 | Yes
2025W1-N11-SVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99523 | 0.78017 | 21.505 | Yes
2025W1-N11-SVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99523 | 0.79054 | 20.469 | Yes
2025W1-N11-SVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99952 | 0.79124 | 20.828 | Yes
2025W1-N11-SVD245358 | 245358 | 05EMPEROR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0009 | 0.77903 | 22.183 | Yes
2025W1-N11-SVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99446 | 0.81133 | 18.313 | Yes
2025W1-N11-SVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99446 | 0.81739 | 17.707 | Yes
2025W1-N11-SVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99738 | 0.81811 | 17.927 | Yes
2025W1-N11-SVD244871 | 244871 | 05RIDGELY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99869 | 0.81028 | 18.842 | Yes
2025W1-N11-SVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98883 | 0.79852 | 19.031 | Yes
2025W1-N11-SVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98883 | 0.80446 | 18.437 | Yes
2025W1-N11-SVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99123 | 0.80519 | 18.604 | Yes
2025W1-N11-SVD244868 | 244868 | 05BRICE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99268 | 0.79748 | 19.52 | Yes
2025W1-N11-SVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99689 | 0.78566 | 21.123 | Yes
2025W1-N11-SVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99689 | 0.79589 | 20.1 | Yes
2025W1-N11-SVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.7966 | 20.448 | Yes
2025W1-N11-SVD244745 | 244745 | 05BABBIT 1-2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.78451 | 21.79 | Yes
2025W1-N11-SVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99784 | 0.85776 | 14.007 | Yes
2025W1-N11-SVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99784 | 0.8587 | 13.914 | Yes
2025W1-N11-SVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99812 | 0.85845 | 13.967 | Yes
2025W1-N11-SVD244560 | 244560 | 05ISABELLA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.8578 | 14.238 | Yes
2025W1-N11-SVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99153 | 0.90249 | 8.904 | Yes
2025W1-N11-SVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99153 | 0.90738 | 8.415 | Yes
2025W1-N11-SVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98913 | 0.90314 | 8.599 | Yes
2025W1-N11-SVD244540 | 244540 | 05RHODES | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99194 | 0.90669 | 8.525 | Yes
2025W1-N11-SVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99799 | 0.80082 | 19.716 | Yes
2025W1-N11-SVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99799 | 0.80797 | 19.002 | Yes
2025W1-N11-SVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.80871 | 19.21 | Yes
2025W1-N11-SVD244338 | 244338 | 05POTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0021 | 0.79973 | 20.234 | Yes
2025W1-N11-SVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0005 | 0.87276 | 12.774 | Yes
2025W1-N11-SVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0005 | 0.87697 | 12.354 | Yes
2025W1-N11-SVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99879 | 0.8735 | 12.529 | Yes
2025W1-N11-SVD244283 | 244283 | 05MINERAL SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.87615 | 12.575 | Yes
2025W1-N11-SVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98736 | 0.8093 | 17.806 | Yes
2025W1-N11-SVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98736 | 0.81431 | 17.305 | Yes
2025W1-N11-SVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98896 | 0.81502 | 17.394 | Yes
2025W1-N11-SVD244258 | 244258 | 05PARSONS1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99007 | 0.80829 | 18.178 | Yes
2025W1-N11-SVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9899 | 0.80152 | 18.838 | Yes
2025W1-N11-SVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9899 | 0.80709 | 18.281 | Yes
2025W1-N11-SVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99207 | 0.80782 | 18.425 | Yes
2025W1-N11-SVD244232 | 244232 | 05SHANNONRSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.80049 | 19.303 | Yes
2025W1-N11-SVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.86386 | 13.619 | Yes
2025W1-N11-SVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0001 | 0.86667 | 13.337 | Yes
2025W1-N11-SVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99928 | 0.86458 | 13.47 | Yes
2025W1-N11-SVD244230 | 244230 | 05SUNDAY SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.86581 | 13.621 | Yes
2025W1-N11-SVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0022 | 0.86924 | 13.293 | Yes
2025W1-N11-SVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0022 | 0.8732 | 12.897 | Yes
2025W1-N11-SVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.86999 | 13.061 | Yes
2025W1-N11-SVD244198 | 244198 | 05LEMASTER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.87236 | 13.143 | Yes
2025W1-N11-SVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9827 | 0.79858 | 18.412 | Yes
2025W1-N11-SVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9827 | 0.80557 | 17.713 | Yes
2025W1-N11-SVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98521 | 0.80626 | 17.895 | Yes
2025W1-N11-SVD244023 | 244023 | 05COLE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98551 | 0.79747 | 18.804 | Yes
2025W1-N11-SVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98442 | 0.80716 | 17.726 | Yes
2025W1-N11-SVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98442 | 0.8135 | 17.092 | Yes
2025W1-N11-SVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98652 | 0.81418 | 17.234 | Yes
2025W1-N11-SVD244022 | 244022 | 05COLE | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98686 | 0.80608 | 18.078 | Yes
2025W1-N11-SVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99533 | 0.79859 | 19.674 | Yes
2025W1-N11-SVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99533 | 0.80595 | 18.938 | Yes
2025W1-N11-SVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99856 | 0.80669 | 19.187 | Yes
2025W1-N11-SVD244020 | 244020 | 05MINK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1 | 0.79751 | 20.249 | Yes
2025W1-N11-SVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99343 | 0.81383 | 17.96 | Yes
2025W1-N11-SVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99343 | 0.82291 | 17.052 | Yes
2025W1-N11-SVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99679 | 0.82405 | 17.274 | Yes
2025W1-N11-SVD243915 | 243915 | 05BERRYWOOD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99666 | 0.81259 | 18.407 | Yes
2025W1-N11-SVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99787 | 0.89532 | 10.256 | Yes
2025W1-N11-SVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9988 | 0.89587 | 10.294 | Yes
2025W1-N11-SVD243903 | 243903 | 05GUNN RD SW | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.91672 | 8.377 | Yes
2025W1-N11-SVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99768 | 0.9059 | 9.179 | Yes
2025W1-N11-SVD243902 | 243902 | 05HARDIN SW | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99844 | 0.90644 | 9.2 | Yes
2025W1-N11-SVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99372 | 0.79855 | 19.517 | Yes
2025W1-N11-SVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99372 | 0.80463 | 18.909 | Yes
2025W1-N11-SVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99592 | 0.80537 | 19.055 | Yes
2025W1-N11-SVD243876 | 243876 | 05ST.CXX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99716 | 0.79749 | 19.967 | Yes
2025W1-N11-SVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99489 | 0.78492 | 20.998 | Yes
2025W1-N11-SVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99489 | 0.79556 | 19.934 | Yes
2025W1-N11-SVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99913 | 0.79627 | 20.286 | Yes
2025W1-N11-SVD243856 | 243856 | 05JUG ST 1-6 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.78375 | 21.663 | Yes
2025W1-N11-SVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98555 | 0.78784 | 19.77 | Yes
2025W1-N11-SVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98555 | 0.79806 | 18.749 | Yes
2025W1-N11-SVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98951 | 0.79876 | 19.075 | Yes
2025W1-N11-SVD243855 | 243855 | 05JUG ST | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99081 | 0.78668 | 20.413 | Yes
2025W1-N11-SVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99439 | 0.80401 | 19.038 | Yes
2025W1-N11-SVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99439 | 0.80979 | 18.46 | Yes
2025W1-N11-SVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.81053 | 18.587 | Yes
2025W1-N11-SVD243854 | 243854 | 05REAVER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99752 | 0.80297 | 19.455 | Yes
2025W1-N11-SVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9898 | 0.8168 | 17.299 | Yes
2025W1-N11-SVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9898 | 0.82057 | 16.922 | Yes
2025W1-N11-SVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99097 | 0.82129 | 16.968 | Yes
2025W1-N11-SVD243593 | 243593 | 05ZUBER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99199 | 0.81582 | 17.617 | Yes
2025W1-N11-SVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9979 | 0.80125 | 19.665 | Yes
2025W1-N11-SVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9979 | 0.80826 | 18.963 | Yes
2025W1-N11-SVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0007 | 0.80901 | 19.164 | Yes
2025W1-N11-SVD243592 | 243592 | 05YEARLG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.80015 | 20.175 | Yes
2025W1-N11-SVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99154 | 0.79075 | 20.078 | Yes
2025W1-N11-SVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99154 | 0.80101 | 19.053 | Yes
2025W1-N11-SVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99539 | 0.80173 | 19.367 | Yes
2025W1-N11-SVD243591 | 243591 | 05SPRINGRDSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99668 | 0.78957 | 20.71 | Yes
2025W1-N11-SVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98706 | 0.78834 | 19.871 | Yes
2025W1-N11-SVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98706 | 0.79963 | 18.742 | Yes
2025W1-N11-SVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99117 | 0.80034 | 19.083 | Yes
2025W1-N11-SVD243590 | 243590 | 05WESTAR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9926 | 0.78714 | 20.546 | Yes
2025W1-N11-SVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98937 | 0.79632 | 19.305 | Yes
2025W1-N11-SVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98937 | 0.80336 | 18.601 | Yes
2025W1-N11-SVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99195 | 0.80409 | 18.786 | Yes
2025W1-N11-SVD243588 | 243588 | 05WILSON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99269 | 0.79522 | 19.748 | Yes
2025W1-N11-SVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98714 | 0.81011 | 17.703 | Yes
2025W1-N11-SVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98714 | 0.81508 | 17.206 | Yes
2025W1-N11-SVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98873 | 0.81579 | 17.294 | Yes
2025W1-N11-SVD243586 | 243586 | 05WHITER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98973 | 0.8091 | 18.063 | Yes
2025W1-N11-SVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99564 | 0.7976 | 19.804 | Yes
2025W1-N11-SVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99564 | 0.80457 | 19.106 | Yes
2025W1-N11-SVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9983 | 0.80531 | 19.299 | Yes
2025W1-N11-SVD243584 | 243584 | 05VINE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99934 | 0.79651 | 20.284 | Yes
2025W1-N11-SVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0043 | 0.83394 | 17.031 | Yes
2025W1-N11-SVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0043 | 0.84215 | 16.21 | Yes
2025W1-N11-SVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.84323 | 16.369 | Yes
2025W1-N11-SVD243583 | 243583 | 05TRENT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.83272 | 17.424 | Yes
2025W1-N11-SVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98707 | 0.79444 | 19.263 | Yes
2025W1-N11-SVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98707 | 0.80143 | 18.564 | Yes
2025W1-N11-SVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98968 | 0.80214 | 18.753 | Yes
2025W1-N11-SVD243582 | 243582 | 05TRABUE1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99037 | 0.79333 | 19.704 | Yes
2025W1-N11-SVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99655 | 0.79831 | 19.824 | Yes
2025W1-N11-SVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99655 | 0.80585 | 19.07 | Yes
2025W1-N11-SVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99975 | 0.80659 | 19.316 | Yes
2025W1-N11-SVD243581 | 243581 | 05TAYLOR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0011 | 0.79722 | 20.392 | Yes
2025W1-N11-SVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99309 | 0.80117 | 19.192 | Yes
2025W1-N11-SVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99309 | 0.80704 | 18.605 | Yes
2025W1-N11-SVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99519 | 0.80778 | 18.741 | Yes
2025W1-N11-SVD243580 | 243580 | 05SULVNT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99635 | 0.80012 | 19.623 | Yes
2025W1-N11-SVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.002 | 0.86954 | 13.243 | Yes
2025W1-N11-SVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.002 | 0.87374 | 12.823 | Yes
2025W1-N11-SVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.87029 | 12.996 | Yes
2025W1-N11-SVD243579 | 243579 | 05STROUD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0036 | 0.87289 | 13.066 | Yes
2025W1-N11-SVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99502 | 0.79345 | 20.157 | Yes
2025W1-N11-SVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99502 | 0.80254 | 19.248 | Yes
2025W1-N11-SVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9985 | 0.80327 | 19.523 | Yes
2025W1-N11-SVD243577 | 243577 | 05STELZR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99961 | 0.7923 | 20.732 | Yes
2025W1-N11-SVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99871 | 0.80026 | 19.846 | Yes
2025W1-N11-SVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99871 | 0.80809 | 19.062 | Yes
2025W1-N11-SVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.80883 | 19.286 | Yes
2025W1-N11-SVD243576 | 243576 | 05ST.CLX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.79913 | 20.337 | Yes
2025W1-N11-SVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0029 | 0.80381 | 19.912 | Yes
2025W1-N11-SVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0029 | 0.811 | 19.193 | Yes
2025W1-N11-SVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0057 | 0.81175 | 19.394 | Yes
2025W1-N11-SVD243575 | 243575 | 05ST.CLR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.8027 | 20.409 | Yes
2025W1-N11-SVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0009 | 0.82796 | 17.289 | Yes
2025W1-N11-SVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0009 | 0.83639 | 16.446 | Yes
2025W1-N11-SVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.83749 | 16.621 | Yes
2025W1-N11-SVD243574 | 243574 | 05SUNBURY SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0037 | 0.82674 | 17.697 | Yes
2025W1-N11-SVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9899 | 0.8015 | 18.84 | Yes
2025W1-N11-SVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9899 | 0.80707 | 18.283 | Yes
2025W1-N11-SVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99208 | 0.8078 | 18.427 | Yes
2025W1-N11-SVD243572 | 243572 | 05SHANON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99352 | 0.80046 | 19.306 | Yes
2025W1-N11-SVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9871 | 0.86711 | 12 | Yes
2025W1-N11-SVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9871 | 0.86962 | 11.749 | Yes
2025W1-N11-SVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.86777 | 11.785 | Yes
2025W1-N11-SVD243570 | 243570 | 05CLAYBN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98802 | 0.86887 | 11.915 | Yes
2025W1-N11-SVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98697 | 0.84477 | 14.221 | Yes
2025W1-N11-SVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98697 | 0.84545 | 14.153 | Yes
2025W1-N11-SVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98633 | 0.84546 | 14.087 | Yes
2025W1-N11-SVD243569 | 243569 | 05SCIPPO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98832 | 0.84462 | 14.37 | Yes
2025W1-N11-SVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98499 | 0.84451 | 14.049 | Yes
2025W1-N11-SVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98499 | 0.84541 | 13.959 | Yes
2025W1-N11-SVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98425 | 0.84521 | 13.905 | Yes
2025W1-N11-SVD243568 | 243568 | 05SCIOTO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9863 | 0.84459 | 14.171 | Yes
2025W1-N11-SVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98401 | 0.78855 | 19.546 | Yes
2025W1-N11-SVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98401 | 0.79773 | 18.628 | Yes
2025W1-N11-SVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98759 | 0.79843 | 18.915 | Yes
2025W1-N11-SVD243566 | 243566 | 05SAWMILL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98812 | 0.78733 | 20.079 | Yes
2025W1-N11-SVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99015 | 0.89773 | 9.242 | Yes
2025W1-N11-SVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99015 | 0.901 | 8.915 | Yes
2025W1-N11-SVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9883 | 0.8983 | 9 | Yes
2025W1-N11-SVD243563 | 243563 | 05ROZELL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99057 | 0.90035 | 9.022 | Yes
2025W1-N11-SVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9874 | 0.86994 | 11.746 | Yes
2025W1-N11-SVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9874 | 0.8727 | 11.47 | Yes
2025W1-N11-SVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98578 | 0.8706 | 11.518 | Yes
2025W1-N11-SVD243562 | 243562 | 05ROSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98825 | 0.87196 | 11.629 | Yes
2025W1-N11-SVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99179 | 0.79727 | 19.452 | Yes
2025W1-N11-SVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99179 | 0.80492 | 18.687 | Yes
2025W1-N11-SVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99468 | 0.80564 | 18.904 | Yes
2025W1-N11-SVD243560 | 243560 | 05ROBERT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99529 | 0.79613 | 19.917 | Yes
2025W1-N11-SVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98103 | 0.78488 | 19.615 | Yes
2025W1-N11-SVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98103 | 0.79665 | 18.438 | Yes
2025W1-N11-SVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98522 | 0.79734 | 18.788 | Yes
2025W1-N11-SVD243553 | 243553 | 05POLARS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98676 | 0.78366 | 20.31 | Yes
2025W1-N11-SVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99046 | 0.80842 | 18.205 | Yes
2025W1-N11-SVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99046 | 0.81166 | 17.88 | Yes
2025W1-N11-SVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99217 | 0.81242 | 17.975 | Yes
2025W1-N11-SVD243552 | 243552 | 05PICKR8 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.80738 | 18.677 | Yes
2025W1-N11-SVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99232 | 0.79568 | 19.664 | Yes
2025W1-N11-SVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99232 | 0.80308 | 18.924 | Yes
2025W1-N11-SVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99509 | 0.80381 | 19.128 | Yes
2025W1-N11-SVD243551 | 243551 | 05OSU | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.79456 | 20.13 | Yes
2025W1-N11-SVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99351 | 0.81447 | 17.903 | Yes
2025W1-N11-SVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99351 | 0.81821 | 17.53 | Yes
2025W1-N11-SVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99473 | 0.81894 | 17.579 | Yes
2025W1-N11-SVD243550 | 243550 | 05OBETZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99592 | 0.81349 | 18.243 | Yes
2025W1-N11-SVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98417 | 0.87665 | 10.751 | Yes
2025W1-N11-SVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98417 | 0.87972 | 10.445 | Yes
2025W1-N11-SVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98239 | 0.87728 | 10.51 | Yes
2025W1-N11-SVD243549 | 243549 | 05MULBRY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98482 | 0.87902 | 10.581 | Yes
2025W1-N11-SVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99358 | 0.8008 | 19.278 | Yes
2025W1-N11-SVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99358 | 0.8066 | 18.698 | Yes
2025W1-N11-SVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99569 | 0.80734 | 18.835 | Yes
2025W1-N11-SVD243548 | 243548 | 05MOUND ST | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99692 | 0.79975 | 19.717 | Yes
2025W1-N11-SVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99471 | 0.79308 | 20.163 | Yes
2025W1-N11-SVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99471 | 0.80231 | 19.24 | Yes
2025W1-N11-SVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99825 | 0.80304 | 19.521 | Yes
2025W1-N11-SVD243547 | 243547 | 05MORSE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99937 | 0.79193 | 20.744 | Yes
2025W1-N11-SVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99143 | 0.90197 | 8.946 | Yes
2025W1-N11-SVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99143 | 0.90686 | 8.457 | Yes
2025W1-N11-SVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98904 | 0.90262 | 8.642 | Yes
2025W1-N11-SVD243545 | 243545 | 05MILTON SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99186 | 0.90617 | 8.569 | Yes
2025W1-N11-SVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99569 | 0.79434 | 20.135 | Yes
2025W1-N11-SVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99569 | 0.80306 | 19.262 | Yes
2025W1-N11-SVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99903 | 0.8038 | 19.523 | Yes
2025W1-N11-SVD243542 | 243542 | 05MIFFLIN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.79319 | 20.694 | Yes
2025W1-N11-SVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99808 | 0.811 | 18.708 | Yes
2025W1-N11-SVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99808 | 0.81655 | 18.153 | Yes
2025W1-N11-SVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99994 | 0.81729 | 18.265 | Yes
2025W1-N11-SVD243540 | 243540 | 05MCCOMB | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.80997 | 19.102 | Yes
2025W1-N11-SVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99168 | 0.80014 | 19.154 | Yes
2025W1-N11-SVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99168 | 0.80546 | 18.621 | Yes
2025W1-N11-SVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.8062 | 18.74 | Yes
2025W1-N11-SVD243539 | 243539 | 05MARION RD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99491 | 0.7991 | 19.581 | Yes
2025W1-N11-SVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97954 | 0.78609 | 19.345 | Yes
2025W1-N11-SVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97954 | 0.79846 | 18.107 | Yes
2025W1-N11-SVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98375 | 0.79915 | 18.46 | Yes
2025W1-N11-SVD243538 | 243538 | 05MALISX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98535 | 0.78486 | 20.049 | Yes
2025W1-N11-SVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97963 | 0.78611 | 19.352 | Yes
2025W1-N11-SVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97963 | 0.79848 | 18.114 | Yes
2025W1-N11-SVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98384 | 0.79917 | 18.467 | Yes
2025W1-N11-SVD243537 | 243537 | 05MALIS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98541 | 0.78488 | 20.053 | Yes
2025W1-N11-SVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99001 | 0.80185 | 18.816 | Yes
2025W1-N11-SVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99001 | 0.807 | 18.301 | Yes
2025W1-N11-SVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99193 | 0.80773 | 18.42 | Yes
2025W1-N11-SVD243536 | 243536 | 05LS-II | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99334 | 0.80082 | 19.252 | Yes
2025W1-N11-SVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98768 | 0.78822 | 19.945 | Yes
2025W1-N11-SVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98768 | 0.79685 | 19.082 | Yes
2025W1-N11-SVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99102 | 0.79756 | 19.346 | Yes
2025W1-N11-SVD243535 | 243535 | 05LINWRT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99167 | 0.78705 | 20.462 | Yes
2025W1-N11-SVD243534 | 243534 | 05LICK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99446 | 0.91274 | 8.172 | Yes
2025W1-N11-SVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99692 | 0.8029 | 19.402 | Yes
2025W1-N11-SVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99692 | 0.81007 | 18.685 | Yes
2025W1-N11-SVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0002 | 0.81079 | 18.938 | Yes
2025W1-N11-SVD243532 | 243532 | 05KIRK | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0016 | 0.80183 | 19.982 | Yes
2025W1-N11-SVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99981 | 0.85993 | 13.988 | Yes
2025W1-N11-SVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99981 | 0.86334 | 13.647 | Yes
2025W1-N11-SVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99853 | 0.86068 | 13.784 | Yes
2025W1-N11-SVD243531 | 243531 | 05KIMBRY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.86248 | 13.925 | Yes
2025W1-N11-SVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99351 | 0.79588 | 19.763 | Yes
2025W1-N11-SVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99351 | 0.80378 | 18.974 | Yes
2025W1-N11-SVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99652 | 0.8045 | 19.202 | Yes
2025W1-N11-SVD243529 | 243529 | 05KENNY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99731 | 0.79475 | 20.256 | Yes
2025W1-N11-SVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99274 | 0.79142 | 20.132 | Yes
2025W1-N11-SVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99274 | 0.80035 | 19.238 | Yes
2025W1-N11-SVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99609 | 0.80108 | 19.501 | Yes
2025W1-N11-SVD243528 | 243528 | 05KARL ROAD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99691 | 0.79027 | 20.664 | Yes
2025W1-N11-SVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98726 | 0.80168 | 18.558 | Yes
2025W1-N11-SVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98726 | 0.81126 | 17.599 | Yes
2025W1-N11-SVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99095 | 0.81232 | 17.863 | Yes
2025W1-N11-SVD243527 | 243527 | 05HYATTX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9909 | 0.80043 | 19.047 | Yes
2025W1-N11-SVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97749 | 0.78687 | 19.062 | Yes
2025W1-N11-SVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97749 | 0.79668 | 18.081 | Yes
2025W1-N11-SVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98128 | 0.79738 | 18.39 | Yes
2025W1-N11-SVD243526 | 243526 | 05HYATT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98185 | 0.78562 | 19.622 | Yes
2025W1-N11-SVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98899 | 0.7886 | 20.038 | Yes
2025W1-N11-SVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98899 | 0.79746 | 19.152 | Yes
2025W1-N11-SVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9924 | 0.79817 | 19.422 | Yes
2025W1-N11-SVD243525 | 243525 | 05HUNTLEY1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99307 | 0.78743 | 20.563 | Yes
2025W1-N11-SVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9923 | 0.79575 | 19.655 | Yes
2025W1-N11-SVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9923 | 0.80315 | 18.915 | Yes
2025W1-N11-SVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99507 | 0.80388 | 19.118 | Yes
2025W1-N11-SVD243524 | 243524 | 05HESS NORTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99583 | 0.79463 | 20.119 | Yes
2025W1-N11-SVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99464 | 0.79316 | 20.148 | Yes
2025W1-N11-SVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99464 | 0.80233 | 19.231 | Yes
2025W1-N11-SVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99817 | 0.80306 | 19.512 | Yes
2025W1-N11-SVD243523 | 243523 | 05HCREAN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99931 | 0.79201 | 20.73 | Yes
2025W1-N11-SVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99666 | 0.8283 | 16.836 | Yes
2025W1-N11-SVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99666 | 0.83093 | 16.573 | Yes
2025W1-N11-SVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99744 | 0.83166 | 16.578 | Yes
2025W1-N11-SVD243522 | 243522 | 05HARRISON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99849 | 0.82734 | 17.114 | Yes
2025W1-N11-SVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98504 | 0.79992 | 18.511 | Yes
2025W1-N11-SVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98504 | 0.80585 | 17.919 | Yes
2025W1-N11-SVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98709 | 0.80656 | 18.053 | Yes
2025W1-N11-SVD243519 | 243519 | 05HALLRD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98791 | 0.79887 | 18.904 | Yes
2025W1-N11-SVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99421 | 0.80449 | 18.972 | Yes
2025W1-N11-SVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99421 | 0.81015 | 18.407 | Yes
2025W1-N11-SVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.81088 | 18.552 | Yes
2025W1-N11-SVD243518 | 243518 | 05GROVES1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99782 | 0.80345 | 19.437 | Yes
2025W1-N11-SVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97899 | 0.78589 | 19.309 | Yes
2025W1-N11-SVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97899 | 0.79551 | 18.348 | Yes
2025W1-N11-SVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98272 | 0.79621 | 18.65 | Yes
2025W1-N11-SVD243516 | 243516 | 05GREIF | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98328 | 0.78467 | 19.862 | Yes
2025W1-N11-SVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9907 | 0.79072 | 19.999 | Yes
2025W1-N11-SVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9907 | 0.80175 | 18.895 | Yes
2025W1-N11-SVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99478 | 0.80246 | 19.232 | Yes
2025W1-N11-SVD243513 | 243513 | 05GENOA | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99614 | 0.78951 | 20.663 | Yes
2025W1-N11-SVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98943 | 0.78902 | 20.041 | Yes
2025W1-N11-SVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98943 | 0.79784 | 19.16 | Yes
2025W1-N11-SVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99282 | 0.79855 | 19.427 | Yes
2025W1-N11-SVD243512 | 243512 | 05DIAMONDISS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9935 | 0.78785 | 20.565 | Yes
2025W1-N11-SVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99245 | 0.80003 | 19.242 | Yes
2025W1-N11-SVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99245 | 0.80594 | 18.651 | Yes
2025W1-N11-SVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99457 | 0.80668 | 18.789 | Yes
2025W1-N11-SVD243511 | 243511 | 05GAY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99573 | 0.79898 | 19.676 | Yes
2025W1-N11-SVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99486 | 0.79465 | 20.021 | Yes
2025W1-N11-SVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99486 | 0.80344 | 19.142 | Yes
2025W1-N11-SVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99836 | 0.80417 | 19.419 | Yes
2025W1-N11-SVD243510 | 243510 | 05GAHANN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9996 | 0.79351 | 20.609 | Yes
2025W1-N11-SVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98554 | 0.79667 | 18.887 | Yes
2025W1-N11-SVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98554 | 0.80308 | 18.246 | Yes
2025W1-N11-SVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98785 | 0.80379 | 18.405 | Yes
2025W1-N11-SVD243509 | 243509 | 05FISHRD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98862 | 0.7956 | 19.302 | Yes
2025W1-N11-SVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99728 | 0.79896 | 19.832 | Yes
2025W1-N11-SVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99728 | 0.80599 | 19.129 | Yes
2025W1-N11-SVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99996 | 0.80673 | 19.324 | Yes
2025W1-N11-SVD243508 | 243508 | 05ITALNV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.79786 | 20.316 | Yes
2025W1-N11-SVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99209 | 0.79597 | 19.612 | Yes
2025W1-N11-SVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99209 | 0.80332 | 18.877 | Yes
2025W1-N11-SVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99484 | 0.80405 | 19.079 | Yes
2025W1-N11-SVD243507 | 243507 | 05FIFTH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99561 | 0.79486 | 20.075 | Yes
2025W1-N11-SVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99286 | 0.87327 | 11.96 | Yes
2025W1-N11-SVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99286 | 0.87897 | 11.389 | Yes
2025W1-N11-SVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99014 | 0.87403 | 11.611 | Yes
2025W1-N11-SVD243506 | 243506 | 05ELLIOTT 1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.87816 | 11.599 | Yes
2025W1-N11-SVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99977 | 0.80023 | 19.954 | Yes
2025W1-N11-SVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99977 | 0.80801 | 19.175 | Yes
2025W1-N11-SVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0029 | 0.80875 | 19.417 | Yes
2025W1-N11-SVD243502 | 243502 | 05E.BROAD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0042 | 0.79912 | 20.511 | Yes
2025W1-N11-SVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98049 | 0.78412 | 19.637 | Yes
2025W1-N11-SVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98049 | 0.7925 | 18.8 | Yes
2025W1-N11-SVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98381 | 0.79319 | 19.063 | Yes
2025W1-N11-SVD243499 | 243499 | 05DUBLIN CS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98422 | 0.78294 | 20.128 | Yes
2025W1-N11-SVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98942 | 0.80559 | 18.383 | Yes
2025W1-N11-SVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98942 | 0.81514 | 17.428 | Yes
2025W1-N11-SVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99315 | 0.8163 | 17.684 | Yes
2025W1-N11-SVD243498 | 243498 | 05DLAWAR2 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99289 | 0.80434 | 18.855 | Yes
2025W1-N11-SVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98716 | 0.86683 | 12.034 | Yes
2025W1-N11-SVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98716 | 0.8693 | 11.787 | Yes
2025W1-N11-SVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9857 | 0.86749 | 11.82 | Yes
2025W1-N11-SVD243497 | 243497 | 05DELANO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98809 | 0.86855 | 11.954 | Yes
2025W1-N11-SVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98318 | 0.78592 | 19.726 | Yes
2025W1-N11-SVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98318 | 0.79407 | 18.911 | Yes
2025W1-N11-SVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98639 | 0.79477 | 19.162 | Yes
2025W1-N11-SVD243495 | 243495 | 05DAVIDS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98691 | 0.78475 | 20.216 | Yes
2025W1-N11-SVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98737 | 0.78782 | 19.954 | Yes
2025W1-N11-SVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98737 | 0.79471 | 19.266 | Yes
2025W1-N11-SVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99006 | 0.79544 | 19.462 | Yes
2025W1-N11-SVD243494 | 243494 | 05CTYPLN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99111 | 0.78674 | 20.437 | Yes
2025W1-N11-SVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99235 | 0.81165 | 18.07 | Yes
2025W1-N11-SVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99235 | 0.82085 | 17.15 | Yes
2025W1-N11-SVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99581 | 0.822 | 17.381 | Yes
2025W1-N11-SVD243493 | 243493 | 05CRVERD | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99565 | 0.81041 | 18.524 | Yes
2025W1-N11-SVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99127 | 0.90081 | 9.046 | Yes
2025W1-N11-SVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99127 | 0.90571 | 8.556 | Yes
2025W1-N11-SVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9889 | 0.90147 | 8.743 | Yes
2025W1-N11-SVD243492 | 243492 | 05CORWIN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9917 | 0.90501 | 8.669 | Yes
2025W1-N11-SVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99302 | 0.79201 | 20.101 | Yes
2025W1-N11-SVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99302 | 0.80265 | 19.037 | Yes
2025W1-N11-SVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99703 | 0.80336 | 19.366 | Yes
2025W1-N11-SVD243491 | 243491 | 05CORRID | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99822 | 0.79082 | 20.74 | Yes
2025W1-N11-SVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98901 | 0.82977 | 15.924 | Yes
2025W1-N11-SVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98901 | 0.83338 | 15.564 | Yes
2025W1-N11-SVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99132 | 0.83407 | 15.724 | Yes
2025W1-N11-SVD243488 | 243488 | 05CONESVILLE | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99227 | 0.82875 | 16.352 | Yes
2025W1-N11-SVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99212 | 0.79167 | 20.044 | Yes
2025W1-N11-SVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99212 | 0.80032 | 19.18 | Yes
2025W1-N11-SVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99537 | 0.80104 | 19.433 | Yes
2025W1-N11-SVD243487 | 243487 | 05CHK TAP Z | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99611 | 0.79053 | 20.559 | Yes
2025W1-N11-SVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99292 | 0.79538 | 19.754 | Yes
2025W1-N11-SVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99292 | 0.80305 | 18.987 | Yes
2025W1-N11-SVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99575 | 0.80377 | 19.197 | Yes
2025W1-N11-SVD243486 | 243486 | 05CLINTX | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.79426 | 20.22 | Yes
2025W1-N11-SVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99397 | 0.79511 | 19.886 | Yes
2025W1-N11-SVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99397 | 0.80317 | 19.079 | Yes
2025W1-N11-SVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99703 | 0.8039 | 19.313 | Yes
2025W1-N11-SVD243485 | 243485 | 05CLINTO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99785 | 0.79397 | 20.388 | Yes
2025W1-N11-SVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99387 | 0.79539 | 19.848 | Yes
2025W1-N11-SVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99387 | 0.80235 | 19.153 | Yes
2025W1-N11-SVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99655 | 0.80308 | 19.347 | Yes
2025W1-N11-SVD243484 | 243484 | 05CITYCO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99759 | 0.7943 | 20.329 | Yes
2025W1-N11-SVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99064 | 0.84528 | 14.536 | Yes
2025W1-N11-SVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99064 | 0.84555 | 14.509 | Yes
2025W1-N11-SVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99018 | 0.84598 | 14.42 | Yes
2025W1-N11-SVD243483 | 243483 | 05CRCLVS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99205 | 0.84471 | 14.734 | Yes
2025W1-N11-SVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.008 | 0.8469 | 16.113 | Yes
2025W1-N11-SVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.008 | 0.85443 | 15.36 | Yes
2025W1-N11-SVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0102 | 0.85546 | 15.469 | Yes
2025W1-N11-SVD243482 | 243482 | 05CENTBG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0103 | 0.84573 | 16.455 | Yes
2025W1-N11-SVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99206 | 0.80011 | 19.195 | Yes
2025W1-N11-SVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99206 | 0.80592 | 18.614 | Yes
2025W1-N11-SVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99415 | 0.80666 | 18.749 | Yes
2025W1-N11-SVD243481 | 243481 | 05CANAL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99535 | 0.79906 | 19.629 | Yes
2025W1-N11-SVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99142 | 0.80159 | 18.983 | Yes
2025W1-N11-SVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99142 | 0.80714 | 18.427 | Yes
2025W1-N11-SVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99345 | 0.80788 | 18.558 | Yes
2025W1-N11-SVD243480 | 243480 | 05BUCKYST_BP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99475 | 0.80055 | 19.42 | Yes
2025W1-N11-SVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98542 | 0.78862 | 19.68 | Yes
2025W1-N11-SVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98542 | 0.79741 | 18.801 | Yes
2025W1-N11-SVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98884 | 0.79812 | 19.073 | Yes
2025W1-N11-SVD243479 | 243479 | 05BROOKS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98939 | 0.78743 | 20.196 | Yes
2025W1-N11-SVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99759 | 0.82218 | 17.541 | Yes
2025W1-N11-SVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99759 | 0.83085 | 16.675 | Yes
2025W1-N11-SVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.83196 | 16.867 | Yes
2025W1-N11-SVD243478 | 243478 | 05BRKSHR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.82095 | 17.964 | Yes
2025W1-N11-SVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99749 | 0.88149 | 11.6 | Yes
2025W1-N11-SVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99749 | 0.88609 | 11.14 | Yes
2025W1-N11-SVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99558 | 0.8822 | 11.337 | Yes
2025W1-N11-SVD243476 | 243476 | 05BOLINSMLSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99846 | 0.88532 | 11.314 | Yes
2025W1-N11-SVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99306 | 0.79145 | 20.161 | Yes
2025W1-N11-SVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99306 | 0.80118 | 19.189 | Yes
2025W1-N11-SVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99678 | 0.8019 | 19.488 | Yes
2025W1-N11-SVD243475 | 243475 | 05BLENDO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99794 | 0.79028 | 20.765 | Yes
2025W1-N11-SVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99677 | 0.79669 | 20.008 | Yes
2025W1-N11-SVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99677 | 0.80485 | 19.192 | Yes
2025W1-N11-SVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.80559 | 19.447 | Yes
2025W1-N11-SVD243474 | 243474 | 05BLACKL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.79558 | 20.576 | Yes
2025W1-N11-SVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98999 | 0.80573 | 18.426 | Yes
2025W1-N11-SVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98999 | 0.81077 | 17.922 | Yes
2025W1-N11-SVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99191 | 0.8115 | 18.041 | Yes
2025W1-N11-SVD243473 | 243473 | 05BIXBY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99338 | 0.80471 | 18.866 | Yes
2025W1-N11-SVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99783 | 0.80209 | 19.574 | Yes
2025W1-N11-SVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99783 | 0.80889 | 18.894 | Yes
2025W1-N11-SVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0005 | 0.80963 | 19.084 | Yes
2025W1-N11-SVD243472 | 243472 | 05BEXLEY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.801 | 20.07 | Yes
2025W1-N11-SVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98775 | 0.78987 | 19.788 | Yes
2025W1-N11-SVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98775 | 0.7983 | 18.945 | Yes
2025W1-N11-SVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99101 | 0.79901 | 19.201 | Yes
2025W1-N11-SVD243471 | 243471 | 05BETHEL | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99157 | 0.78869 | 20.288 | Yes
2025W1-N11-SVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98912 | 0.81341 | 17.571 | Yes
2025W1-N11-SVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98912 | 0.81837 | 17.075 | Yes
2025W1-N11-SVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99069 | 0.81907 | 17.162 | Yes
2025W1-N11-SVD243469 | 243469 | 05BEATTY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99158 | 0.8124 | 17.917 | Yes
2025W1-N11-SVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99004 | 0.79798 | 19.206 | Yes
2025W1-N11-SVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99004 | 0.80439 | 18.566 | Yes
2025W1-N11-SVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9927 | 0.80512 | 18.758 | Yes
2025W1-N11-SVD243467 | 243467 | 05E.BROAD3 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99413 | 0.79693 | 19.719 | Yes
2025W1-N11-SVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98862 | 0.79751 | 19.111 | Yes
2025W1-N11-SVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98862 | 0.80361 | 18.501 | Yes
2025W1-N11-SVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99113 | 0.80435 | 18.679 | Yes
2025W1-N11-SVD243466 | 243466 | 05ASTOR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99258 | 0.79647 | 19.612 | Yes
2025W1-N11-SVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98327 | 0.7965 | 18.677 | Yes
2025W1-N11-SVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98327 | 0.8043 | 17.897 | Yes
2025W1-N11-SVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98611 | 0.805 | 18.112 | Yes
2025W1-N11-SVD243461 | 243461 | 05ROBRT1 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98612 | 0.79535 | 19.077 | Yes
2025W1-N11-SVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98278 | 0.79588 | 18.69 | Yes
2025W1-N11-SVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98278 | 0.80368 | 17.911 | Yes
2025W1-N11-SVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98562 | 0.80437 | 18.125 | Yes
2025W1-N11-SVD243460 | 243460 | 05ROBRT2 | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98563 | 0.79472 | 19.091 | Yes
2025W1-N11-SVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98672 | 0.79916 | 18.756 | Yes
2025W1-N11-SVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98672 | 0.8059 | 18.082 | Yes
2025W1-N11-SVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98982 | 0.8066 | 18.322 | Yes
2025W1-N11-SVD243459 | 243459 | 05KIRK | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.7981 | 19.336 | Yes
2025W1-N11-SVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9864 | 0.80223 | 18.417 | Yes
2025W1-N11-SVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9864 | 0.81183 | 17.457 | Yes
2025W1-N11-SVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99042 | 0.81249 | 17.792 | Yes
2025W1-N11-SVD243458 | 243458 | 05HYATT | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98946 | 0.80087 | 18.86 | Yes
2025W1-N11-SVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98297 | 0.79812 | 18.484 | Yes
2025W1-N11-SVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98297 | 0.8058 | 17.717 | Yes
2025W1-N11-SVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98577 | 0.80649 | 17.929 | Yes
2025W1-N11-SVD243457 | 243457 | 05HAYDEN | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98574 | 0.79696 | 18.878 | Yes
2025W1-N11-SVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9882 | 0.79245 | 19.575 | Yes
2025W1-N11-SVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9882 | 0.80393 | 18.427 | Yes
2025W1-N11-SVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99238 | 0.80463 | 18.775 | Yes
2025W1-N11-SVD243456 | 243456 | 05CORRID | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99355 | 0.79123 | 20.232 | Yes
2025W1-N11-SVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99722 | 0.83538 | 16.184 | Yes
2025W1-N11-SVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99722 | 0.83957 | 15.766 | Yes
2025W1-N11-SVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99982 | 0.84023 | 15.959 | Yes
2025W1-N11-SVD243455 | 243455 | 05CONES | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.83434 | 16.645 | Yes
2025W1-N11-SVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98771 | 0.81394 | 17.377 | Yes
2025W1-N11-SVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98771 | 0.81814 | 16.957 | Yes
2025W1-N11-SVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98921 | 0.81883 | 17.038 | Yes
2025W1-N11-SVD243454 | 243454 | 05BIXBY | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99079 | 0.81296 | 17.782 | Yes
2025W1-N11-SVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9864 | 0.82134 | 16.506 | Yes
2025W1-N11-SVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9864 | 0.82625 | 16.015 | Yes
2025W1-N11-SVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98773 | 0.82693 | 16.08 | Yes
2025W1-N11-SVD243453 | 243453 | 05BEATTY | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98838 | 0.82038 | 16.8 | Yes
2025W1-N11-SVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99749 | 0.86767 | 12.982 | Yes
2025W1-N11-SVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99749 | 0.8687 | 12.879 | Yes
2025W1-N11-SVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99814 | 0.86831 | 12.983 | Yes
2025W1-N11-SVD243161 | 243161 | 05ZANESV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99964 | 0.86781 | 13.182 | Yes
2025W1-N11-SVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0056 | 0.88126 | 12.433 | Yes
2025W1-N11-SVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0056 | 0.88193 | 12.365 | Yes
2025W1-N11-SVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.88255 | 12.377 | Yes
2025W1-N11-SVD243160 | 243160 | 05WTRNWY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.88038 | 12.645 | Yes
2025W1-N11-SVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0066 | 0.89898 | 10.766 | Yes
2025W1-N11-SVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0066 | 0.90099 | 10.564 | Yes
2025W1-N11-SVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.90159 | 10.576 | Yes
2025W1-N11-SVD243153 | 243153 | 05WMTVER | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0072 | 0.89813 | 10.905 | Yes
2025W1-N11-SVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99979 | 0.81749 | 18.23 | Yes
2025W1-N11-SVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99979 | 0.82243 | 17.736 | Yes
2025W1-N11-SVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.82315 | 17.956 | Yes
2025W1-N11-SVD243150 | 243150 | 05WMILLP | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0045 | 0.81645 | 18.806 | Yes
2025W1-N11-SVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0018 | 0.82388 | 17.789 | Yes
2025W1-N11-SVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.82595 | 17.582 | Yes
2025W1-N11-SVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.82672 | 17.662 | Yes
2025W1-N11-SVD243149 | 243149 | 05W.LANCAST1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.82286 | 18.279 | Yes
2025W1-N11-SVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99478 | 0.80721 | 18.757 | Yes
2025W1-N11-SVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99478 | 0.81293 | 18.186 | Yes
2025W1-N11-SVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99783 | 0.81365 | 18.418 | Yes
2025W1-N11-SVD243146 | 243146 | 05WHEBRO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99956 | 0.80616 | 19.34 | Yes
2025W1-N11-SVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0008 | 0.90045 | 10.036 | Yes
2025W1-N11-SVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0008 | 0.90126 | 9.955 | Yes
2025W1-N11-SVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.90093 | 10.049 | Yes
2025W1-N11-SVD243145 | 243145 | 05WCOSHC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0019 | 0.90041 | 10.154 | Yes
2025W1-N11-SVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99936 | 0.86206 | 13.73 | Yes
2025W1-N11-SVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99936 | 0.8644 | 13.496 | Yes
2025W1-N11-SVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99891 | 0.86277 | 13.614 | Yes
2025W1-N11-SVD243107 | 243107 | 05SPENCR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0015 | 0.86352 | 13.793 | Yes
2025W1-N11-SVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0017 | 0.8281 | 17.364 | Yes
2025W1-N11-SVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.82964 | 17.21 | Yes
2025W1-N11-SVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0032 | 0.8304 | 17.279 | Yes
2025W1-N11-SVD243104 | 243104 | 05SLANCS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0055 | 0.82709 | 17.842 | Yes
2025W1-N11-SVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0055 | 0.89307 | 11.241 | Yes
2025W1-N11-SVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.8954 | 11.008 | Yes
2025W1-N11-SVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.89601 | 11.029 | Yes
2025W1-N11-SVD243098 | 243098 | 05SHARPR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0061 | 0.8922 | 11.394 | Yes
2025W1-N11-SVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99915 | 0.89817 | 10.099 | Yes
2025W1-N11-SVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99915 | 0.89981 | 9.934 | Yes
2025W1-N11-SVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.89864 | 10.17 | Yes
2025W1-N11-SVD243094 | 243094 | 05SCOSHC | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0013 | 0.89899 | 10.235 | Yes
2025W1-N11-SVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99991 | 0.819 | 18.091 | Yes
2025W1-N11-SVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99991 | 0.82301 | 17.69 | Yes
2025W1-N11-SVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.82375 | 17.866 | Yes
2025W1-N11-SVD243089 | 243089 | 05SBALTM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0044 | 0.81796 | 18.64 | Yes
2025W1-N11-SVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0018 | 0.8635 | 13.831 | Yes
2025W1-N11-SVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0018 | 0.86507 | 13.674 | Yes
2025W1-N11-SVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.003 | 0.86572 | 13.726 | Yes
2025W1-N11-SVD243079 | 243079 | 05REFORM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0038 | 0.86258 | 14.127 | Yes
2025W1-N11-SVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99052 | 0.83442 | 15.61 | Yes
2025W1-N11-SVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99052 | 0.83766 | 15.286 | Yes
2025W1-N11-SVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99268 | 0.83835 | 15.433 | Yes
2025W1-N11-SVD243076 | 243076 | 05CONESPREPZ | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9936 | 0.83341 | 16.02 | Yes
2025W1-N11-SVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0017 | 0.8738 | 12.791 | Yes
2025W1-N11-SVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0017 | 0.8738 | 12.79 | Yes
2025W1-N11-SVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.87443 | 12.799 | Yes
2025W1-N11-SVD243075 | 243075 | 05POWELS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0033 | 0.8729 | 13.042 | Yes
2025W1-N11-SVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9965 | 0.87483 | 12.167 | Yes
2025W1-N11-SVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9965 | 0.87679 | 11.971 | Yes
2025W1-N11-SVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99704 | 0.87545 | 12.159 | Yes
2025W1-N11-SVD243074 | 243074 | 05PHILO1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99866 | 0.87591 | 12.274 | Yes
2025W1-N11-SVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0055 | 0.87839 | 12.716 | Yes
2025W1-N11-SVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0055 | 0.87901 | 12.654 | Yes
2025W1-N11-SVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.87963 | 12.668 | Yes
2025W1-N11-SVD243070 | 243070 | 05OHIOCT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.8775 | 12.936 | Yes
2025W1-N11-SVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99961 | 0.8709 | 12.871 | Yes
2025W1-N11-SVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99961 | 0.87129 | 12.832 | Yes
2025W1-N11-SVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0003 | 0.87154 | 12.877 | Yes
2025W1-N11-SVD243068 | 243068 | 05NZANEV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.8704 | 13.103 | Yes
2025W1-N11-SVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99921 | 0.85367 | 14.553 | Yes
2025W1-N11-SVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99921 | 0.85598 | 14.323 | Yes
2025W1-N11-SVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0006 | 0.85665 | 14.395 | Yes
2025W1-N11-SVD243063 | 243063 | 05N.NEWARK1 | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.85273 | 14.893 | Yes
2025W1-N11-SVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99665 | 0.90835 | 8.83 | Yes
2025W1-N11-SVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99665 | 0.91213 | 8.452 | Yes
2025W1-N11-SVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99718 | 0.90891 | 8.826 | Yes
2025W1-N11-SVD243062 | 243062 | 05NMUSKG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99829 | 0.91122 | 8.706 | Yes
2025W1-N11-SVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99313 | 0.8161 | 17.703 | Yes
2025W1-N11-SVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99313 | 0.82153 | 17.16 | Yes
2025W1-N11-SVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99587 | 0.82224 | 17.363 | Yes
2025W1-N11-SVD243058 | 243058 | 05NEWARK CTR | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99709 | 0.81505 | 18.204 | Yes
2025W1-N11-SVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0061 | 0.8955 | 11.059 | Yes
2025W1-N11-SVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0061 | 0.89682 | 10.926 | Yes
2025W1-N11-SVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0068 | 0.89742 | 10.937 | Yes
2025W1-N11-SVD243044 | 243044 | 05MILLWO | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.89468 | 11.22 | Yes
2025W1-N11-SVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9979 | 0.84527 | 15.263 | Yes
2025W1-N11-SVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9979 | 0.84548 | 15.242 | Yes
2025W1-N11-SVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9988 | 0.84599 | 15.281 | Yes
2025W1-N11-SVD243025 | 243025 | 05JUNCTN | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.001 | 0.84454 | 15.644 | Yes
2025W1-N11-SVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99646 | 0.83854 | 15.792 | Yes
2025W1-N11-SVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99646 | 0.83983 | 15.662 | Yes
2025W1-N11-SVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99633 | 0.8393 | 15.703 | Yes
2025W1-N11-SVD243023 | 243023 | 05HOCKNG | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99929 | 0.8389 | 16.039 | Yes
2025W1-N11-SVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99912 | 0.83389 | 16.524 | Yes
2025W1-N11-SVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99912 | 0.83775 | 16.137 | Yes
2025W1-N11-SVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0014 | 0.83845 | 16.29 | Yes
2025W1-N11-SVD243018 | 243018 | 05HEATH | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0027 | 0.83288 | 16.977 | Yes
2025W1-N11-SVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0079 | 0.92212 | 8.583 | Yes
2025W1-N11-SVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0079 | 0.92376 | 8.42 | Yes
2025W1-N11-SVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0086 | 0.92432 | 8.428 | Yes
2025W1-N11-SVD243011 | 243011 | 05FULTON | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.92124 | 8.614 | Yes
2025W1-N11-SVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0039 | 0.87081 | 13.31 | Yes
2025W1-N11-SVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0039 | 0.87191 | 13.2 | Yes
2025W1-N11-SVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0049 | 0.87254 | 13.235 | Yes
2025W1-N11-SVD243007 | 243007 | 05FRAZEY | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0056 | 0.86991 | 13.571 | Yes
2025W1-N11-SVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99779 | 0.87319 | 12.46 | Yes
2025W1-N11-SVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99779 | 0.8744 | 12.339 | Yes
2025W1-N11-SVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9984 | 0.87382 | 12.458 | Yes
2025W1-N11-SVD243001 | 243001 | 05EZANEV | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99974 | 0.87352 | 12.622 | Yes
2025W1-N11-SVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99905 | 0.87368 | 12.538 | Yes
2025W1-N11-SVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99905 | 0.87432 | 12.473 | Yes
2025W1-N11-SVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99971 | 0.8743 | 12.541 | Yes
2025W1-N11-SVD242998 | 242998 | 05EPOINT | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0008 | 0.87343 | 12.736 | Yes
2025W1-N11-SVD242987 | 242987 | 05DEXTER | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0001 | 0.91754 | 8.259 | Yes
2025W1-N11-SVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99741 | 0.85814 | 13.927 | Yes
2025W1-N11-SVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99741 | 0.85958 | 13.783 | Yes
2025W1-N11-SVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99751 | 0.85883 | 13.868 | Yes
2025W1-N11-SVD242986 | 242986 | 05CROOKS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99972 | 0.85868 | 14.104 | Yes
2025W1-N11-SVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99679 | 0.86728 | 12.952 | Yes
2025W1-N11-SVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99679 | 0.86902 | 12.777 | Yes
2025W1-N11-SVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99717 | 0.86793 | 12.925 | Yes
2025W1-N11-SVD242979 | 242979 | 05CANNELV SS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99906 | 0.86814 | 13.091 | Yes
2025W1-N11-SVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0071 | 0.90856 | 9.857 | Yes
2025W1-N11-SVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0071 | 0.91061 | 9.653 | Yes
2025W1-N11-SVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0078 | 0.91119 | 9.665 | Yes
2025W1-N11-SVD242963 | 242963 | 05HEDDSS | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0071 | 0.9077 | 9.943 | Yes
2025W1-N11-SVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0063 | 0.90226 | 10.406 | Yes
2025W1-N11-SVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0063 | 0.90387 | 10.245 | Yes
2025W1-N11-SVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.007 | 0.90446 | 10.255 | Yes
2025W1-N11-SVD242950 | 242950 | 05ACADEM | 138 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.90147 | 10.545 | Yes
2025W1-N11-SVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98594 | 0.80747 | 17.847 | Yes
2025W1-N11-SVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98594 | 0.81216 | 17.378 | Yes
2025W1-N11-SVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98905 | 0.81285 | 17.62 | Yes
2025W1-N11-SVD242949 | 242949 | 05WMILLP | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99103 | 0.80645 | 18.458 | Yes
2025W1-N11-SVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99008 | 0.9086 | 8.148 | Yes
2025W1-N11-SVD242945 | 242945 | 05SW LIM | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9905 | 0.90913 | 8.136 | Yes
2025W1-N11-SVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99472 | 0.85342 | 14.13 | Yes
2025W1-N11-SVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99472 | 0.85466 | 14.007 | Yes
2025W1-N11-SVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99646 | 0.85529 | 14.118 | Yes
2025W1-N11-SVD242941 | 242941 | 05OHIOCT | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99766 | 0.85249 | 14.517 | Yes
2025W1-N11-SVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0068 | 0.92185 | 8.496 | Yes
2025W1-N11-SVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0068 | 0.92538 | 8.143 | Yes
2025W1-N11-SVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0069 | 0.92239 | 8.451 | Yes
2025W1-N11-SVD242940 | 242940 | 05MUSKNG | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0074 | 0.92441 | 8.295 | Yes
2025W1-N11-SVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99286 | 0.83774 | 15.512 | Yes
2025W1-N11-SVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99286 | 0.86466 | 12.819 | Yes
2025W1-N11-SVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99528 | 0.83832 | 15.697 | Yes
2025W1-N11-SVD242939 | 242939 | 05MARYSV | 345 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99767 | 0.86269 | 13.498 | Yes
2025W1-N11-SVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.009 | 0.92783 | 8.117 | Yes
2025W1-N11-SVD242931 | 242931 | 05BEVERL | 345 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.009 | 0.92835 | 8.065 | Yes
2025W1-N11-SVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96944 | 0.8081 | 16.134 | Yes
2025W1-N11-SVD242928 | 242928 | 05MARYSV | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97132 | 0.80868 | 16.264 | Yes
2025W1-N11-SVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96782 | 0.78297 | 18.484 | Yes
2025W1-N11-SVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96782 | 0.80004 | 16.777 | Yes
2025W1-N11-SVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97283 | 0.80067 | 17.216 | Yes
2025W1-N11-SVD242926 | 242926 | 05MALIS | 765 | 205 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9766 | 0.78173 | 19.487 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.93472 | 0.76171 | 17.301 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93472 | 0.76349 | 17.123 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90087 | 0.76026 | 14.06 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90087 | 0.76833 | 13.254 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90087 | 0.77601 | 12.486 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9366 | 0.76411 | 17.249 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93693 | 0.76078 | 17.615 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.93918 | 0.75498 | 18.42 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.93594 | 0.75495 | 18.099 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93093 | 0.7566 | 17.433 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91613 | 0.76865 | 14.748 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91613 | 0.77811 | 13.802 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93599 | 0.80717 | 12.882 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93599 | 0.8288 | 10.719 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91699 | 0.76703 | 14.996 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91699 | 0.76973 | 14.726 | Yes
2025W1-N11-SVD241987 | 241987 | AE2-217_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91699 | 0.81208 | 10.491 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97638 | 0.8123 | 16.408 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97638 | 0.81454 | 16.184 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.96265 | 0.84804 | 11.461 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97867 | 0.8152 | 16.347 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97833 | 0.81124 | 16.709 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.96123 | 0.81137 | 14.986 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.97853 | 0.85187 | 12.666 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.95705 | 0.80992 | 14.713 | Yes
2025W1-N11-SVD241980 | 241980 | AD2-163_POI | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95705 | 0.84935 | 10.77 | Yes
2025W1-N11-SVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9862 | 0.88435 | 10.185 | Yes
2025W1-N11-SVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9862 | 0.88602 | 10.018 | Yes
2025W1-N11-SVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98632 | 0.88489 | 10.143 | Yes
2025W1-N11-SVD241968 | 241968 | AD1-140 TAP | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9869 | 0.88546 | 10.144 | Yes
2025W1-N11-SVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.0002 | 0.87196 | 12.821 | Yes
2025W1-N11-SVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.0002 | 0.87278 | 12.738 | Yes
2025W1-N11-SVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.87252 | 13.005 | Yes
2025W1-N11-SVD241957 | 241957 | AC2-195 TAP | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0028 | 0.87174 | 13.107 | Yes
2025W1-N11-SVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96029 | 0.79771 | 16.258 | Yes
2025W1-N11-SVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96029 | 0.80063 | 15.966 | Yes
2025W1-N11-SVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96169 | 0.80129 | 16.04 | Yes
2025W1-N11-SVD241952 | 241952 | 02DEERCREEK | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96246 | 0.79674 | 16.573 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9292 | 0.75517 | 17.403 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9292 | 0.7567 | 17.25 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89758 | 0.75963 | 13.795 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89758 | 0.7628 | 13.479 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89758 | 0.76863 | 12.896 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93104 | 0.75732 | 17.372 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93128 | 0.75427 | 17.701 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.93325 | 0.72866 | 20.459 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.9296 | 0.72863 | 20.097 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92618 | 0.7591 | 16.708 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9088 | 0.74648 | 16.231 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9088 | 0.77081 | 13.798 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93073 | 0.78846 | 14.228 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93073 | 0.82331 | 10.742 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90895 | 0.74472 | 16.423 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90895 | 0.76108 | 14.788 | Yes
2025W1-N11-SVD240710 | 240710 | 02MELISSA | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90895 | 0.79426 | 11.469 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.92932 | 0.75535 | 17.398 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.92932 | 0.75688 | 17.244 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.89763 | 0.75988 | 13.775 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.89763 | 0.76263 | 13.5 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.89763 | 0.76883 | 12.881 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93117 | 0.7575 | 17.366 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.93141 | 0.75444 | 17.697 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.93339 | 0.72951 | 20.388 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.92975 | 0.72947 | 20.028 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92628 | 0.75894 | 16.734 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90898 | 0.74717 | 16.181 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90898 | 0.77101 | 13.796 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93084 | 0.78902 | 14.182 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93084 | 0.82344 | 10.74 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90916 | 0.74541 | 16.375 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.90916 | 0.76133 | 14.783 | Yes
2025W1-N11-SVD240709 | 240709 | 02N TITUS | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.90916 | 0.7948 | 11.437 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.94506 | 0.77366 | 17.14 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.94506 | 0.77676 | 16.83 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91379 | 0.8092 | 10.459 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91379 | 0.81253 | 10.126 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94747 | 0.77738 | 17.009 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94738 | 0.7726 | 17.478 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.95131 | 0.83139 | 11.991 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.94925 | 0.83138 | 11.787 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93435 | 0.81419 | 12.015 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93435 | 0.83388 | 10.046 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93603 | 0.8104 | 12.563 | Yes
2025W1-N11-SVD240706 | 240706 | 02NATIONAL | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93603 | 0.83276 | 10.327 | Yes
2025W1-N11-SVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96407 | 0.7931 | 17.098 | Yes
2025W1-N11-SVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96407 | 0.7973 | 16.678 | Yes
2025W1-N11-SVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96726 | 0.79792 | 16.934 | Yes
2025W1-N11-SVD240637 | 240637 | 02URECMITCHL | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96658 | 0.79186 | 17.473 | Yes
2025W1-N11-SVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97068 | 0.80008 | 17.059 | Yes
2025W1-N11-SVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97068 | 0.80441 | 16.627 | Yes
2025W1-N11-SVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97403 | 0.80504 | 16.899 | Yes
2025W1-N11-SVD240635 | 240635 | 02HARRIOT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9733 | 0.79879 | 17.451 | Yes
2025W1-N11-SVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99922 | 0.86736 | 13.186 | Yes
2025W1-N11-SVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99922 | 0.86818 | 13.104 | Yes
2025W1-N11-SVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0017 | 0.86793 | 13.382 | Yes
2025W1-N11-SVD239308 | 239308 | 02MR-ETH | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.8671 | 13.492 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9618 | 0.80185 | 15.995 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9618 | 0.803 | 15.88 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94195 | 0.79795 | 14.4 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.94195 | 0.82431 | 11.764 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96347 | 0.80366 | 15.981 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96346 | 0.80093 | 16.253 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9618 | 0.84095 | 12.085 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.96199 | 0.85187 | 11.012 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9409 | 0.758 | 18.289 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.9409 | 0.82613 | 11.477 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.96257 | 0.80722 | 15.535 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93491 | 0.75622 | 17.869 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93491 | 0.79946 | 13.544 | Yes
2025W1-N11-SVD239278 | 239278 | 02BRDVIE | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93491 | 0.81506 | 11.985 | Yes
2025W1-N11-SVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97962 | 0.81436 | 16.527 | Yes
2025W1-N11-SVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97962 | 0.818 | 16.163 | Yes
2025W1-N11-SVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98293 | 0.81862 | 16.431 | Yes
2025W1-N11-SVD239264 | 239264 | 02DBP | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9823 | 0.81304 | 16.926 | Yes
2025W1-N11-SVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98034 | 0.81642 | 16.392 | Yes
2025W1-N11-SVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98034 | 0.8195 | 16.084 | Yes
2025W1-N11-SVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98359 | 0.82012 | 16.347 | Yes
2025W1-N11-SVD239218 | 239218 | 02SSCIOT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98307 | 0.81511 | 16.796 | Yes
2025W1-N11-SVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97734 | 0.80752 | 16.982 | Yes
2025W1-N11-SVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97734 | 0.81185 | 16.549 | Yes
2025W1-N11-SVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98078 | 0.81248 | 16.831 | Yes
2025W1-N11-SVD239134 | 239134 | 02TANGY | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98005 | 0.80617 | 17.388 | Yes
2025W1-N11-SVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98684 | 0.80892 | 17.791 | Yes
2025W1-N11-SVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98684 | 0.81575 | 17.109 | Yes
2025W1-N11-SVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99075 | 0.8164 | 17.435 | Yes
2025W1-N11-SVD239133 | 239133 | 02TANGY | 345 | 202 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.98929 | 0.80748 | 18.181 | Yes
2025W1-N11-SVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99948 | 0.86675 | 13.273 | Yes
2025W1-N11-SVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99948 | 0.86755 | 13.193 | Yes
2025W1-N11-SVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.86732 | 13.471 | Yes
2025W1-N11-SVD239073 | 239073 | 02ROBERT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.86646 | 13.584 | Yes
2025W1-N11-SVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99741 | 0.86024 | 13.717 | Yes
2025W1-N11-SVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99741 | 0.86092 | 13.649 | Yes
2025W1-N11-SVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.86082 | 13.928 | Yes
2025W1-N11-SVD238969 | 238969 | 02MRGP + | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.8598 | 14.058 | Yes
2025W1-N11-SVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97408 | 0.80489 | 16.919 | Yes
2025W1-N11-SVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97408 | 0.80869 | 16.539 | Yes
2025W1-N11-SVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97726 | 0.80933 | 16.793 | Yes
2025W1-N11-SVD238964 | 238964 | 02MLCRK+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97661 | 0.80361 | 17.3 | Yes
2025W1-N11-SVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99945 | 0.86666 | 13.279 | Yes
2025W1-N11-SVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99945 | 0.86746 | 13.199 | Yes
2025W1-N11-SVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.002 | 0.86723 | 13.477 | Yes
2025W1-N11-SVD238928 | 238928 | 02LTV+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0023 | 0.86638 | 13.591 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9402 | 0.7693 | 17.091 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9402 | 0.77152 | 16.868 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90239 | 0.7536 | 14.879 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90239 | 0.77917 | 12.322 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90239 | 0.78501 | 11.739 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94213 | 0.77215 | 16.998 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94253 | 0.76832 | 17.421 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-002C_SRT-A | ATSI_P1-2_OES-138-002D_SRT-A | 0.94544 | 0.79935 | 14.61 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-002D_SRT-A | ATSI_P1-2_OES-138-002C_SRT-A | 0.94293 | 0.79933 | 14.361 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93493 | 0.75001 | 18.492 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92595 | 0.78697 | 13.897 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.92595 | 0.80683 | 11.911 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94192 | 0.83442 | 10.75 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94192 | 0.83854 | 10.337 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.92744 | 0.7805 | 14.694 | Yes
2025W1-N11-SVD238908 | 238908 | 02LONDON | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.92744 | 0.80549 | 12.195 | Yes
2025W1-N11-SVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.98862 | 0.83999 | 14.864 | Yes
2025W1-N11-SVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.98862 | 0.84018 | 14.845 | Yes
2025W1-N11-SVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9914 | 0.84057 | 15.083 | Yes
2025W1-N11-SVD238861 | 238861 | 02KIRBY | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.99146 | 0.83893 | 15.253 | Yes
2025W1-N11-SVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1 | 0.8738 | 12.624 | Yes
2025W1-N11-SVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1 | 0.87465 | 12.539 | Yes
2025W1-N11-SVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0024 | 0.87436 | 12.804 | Yes
2025W1-N11-SVD238777 | 238777 | 02HAMIL+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0026 | 0.87362 | 12.901 | Yes
2025W1-N11-SVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 1.005 | 0.91698 | 8.806 | Yes
2025W1-N11-SVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 1.005 | 0.91729 | 8.775 | Yes
2025W1-N11-SVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0063 | 0.91775 | 8.854 | Yes
2025W1-N11-SVD238745 | 238745 | 02GALION | 345 | 202 | 8 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0059 | 0.91637 | 8.954 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.93881 | 0.76726 | 17.155 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.93881 | 0.76867 | 17.015 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.90956 | 0.77037 | 13.919 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.90956 | 0.78049 | 12.907 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.90956 | 0.78143 | 12.813 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94058 | 0.7693 | 17.128 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.94076 | 0.76636 | 17.44 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93635 | 0.77756 | 15.879 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94002 | 0.83915 | 10.087 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.91793 | 0.74944 | 16.849 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91793 | 0.78265 | 13.528 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94049 | 0.79416 | 14.634 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.94049 | 0.83612 | 10.438 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.91761 | 0.74765 | 16.996 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.91761 | 0.77185 | 14.576 | Yes
2025W1-N11-SVD238703 | 238703 | 02ESPRNG | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.91761 | 0.80071 | 11.69 | Yes
2025W1-N11-SVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99972 | 0.86873 | 13.099 | Yes
2025W1-N11-SVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99972 | 0.86953 | 13.019 | Yes
2025W1-N11-SVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0022 | 0.8693 | 13.291 | Yes
2025W1-N11-SVD238667 | 238667 | 02DUALR+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0025 | 0.86846 | 13.401 | Yes
2025W1-N11-SVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.99739 | 0.85806 | 13.932 | Yes
2025W1-N11-SVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.99739 | 0.85859 | 13.88 | Yes
2025W1-N11-SVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0001 | 0.85864 | 14.147 | Yes
2025W1-N11-SVD238640 | 238640 | 02CRISS | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 1.0004 | 0.85745 | 14.291 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.96224 | 0.8031 | 15.914 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.96224 | 0.80372 | 15.851 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.94 | 0.80418 | 13.582 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.94 | 0.80813 | 13.187 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.94 | 0.83494 | 10.506 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96361 | 0.80437 | 15.924 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.96381 | 0.80223 | 16.158 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.96153 | 0.83119 | 13.034 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.9626 | 0.85909 | 10.351 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93885 | 0.7574 | 18.145 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93885 | 0.81024 | 12.862 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.96512 | 0.81124 | 15.389 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93918 | 0.75555 | 18.363 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93918 | 0.80577 | 13.341 | Yes
2025W1-N11-SVD238623 | 238623 | 02CLARK | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93918 | 0.81913 | 12.005 | Yes
2025W1-N11-SVD238605 | 238605 | 02CARDNT | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.9964 | 0.89629 | 10.011 | Yes
2025W1-N11-SVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.97474 | 0.80508 | 16.966 | Yes
2025W1-N11-SVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.97474 | 0.80913 | 16.56 | Yes
2025W1-N11-SVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97805 | 0.80977 | 16.828 | Yes
2025W1-N11-SVD238574 | 238574 | 02BELPT+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.97735 | 0.80376 | 17.359 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#711_6224_SRT-A | 0.9567 | 0.79458 | 16.212 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#17216_SRT-A | AEP_P1-2_#707_8315_SRT-A | 0.9567 | 0.79538 | 16.132 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93276 | 0.79597 | 13.679 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93276 | 0.80171 | 13.105 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#5809_1984_SRT-A | ATSI_P1-2_OES-138-022A_SRT-A | 0.93276 | 0.8221 | 11.066 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#707_8315_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95815 | 0.79602 | 16.213 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | AEP_P1-2_#711_6224_SRT-A | AEP_P1-2_#17216_SRT-A | 0.95834 | 0.79371 | 16.464 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-022A_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.95557 | 0.81833 | 13.725 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-035BA_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95729 | 0.85426 | 10.302 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.93406 | 0.75528 | 17.877 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | ATSI_P1-2_OES-138-935TB_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93406 | 0.80383 | 13.023 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | 0.95952 | 0.80718 | 15.234 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | ATSI_P1-2_OES-138-935TB_SRT-A | 0.93405 | 0.75345 | 18.061 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | AEP_P1-2_#5809_1984_SRT-A | 0.93405 | 0.79754 | 13.652 | Yes
2025W1-N11-SVD238529 | 238529 | 02AIRPK+ | 138 | 202 | 10 | DAY_P1_13828_URBANA_BROADVIEW (FE)_SRT-A | DAY_P1_13809_GREENE_AD1-140_TAP (FE)_138KV_SRT-A | 0.93405 | 0.8148 | 11.926 | Yes
2025W1-N11-SVD217013 | 217013 | HILLSDALE | 230 | 231 | 5 | PS_P1-2_F-2258_SRT-A | PS_P1-2_V-2222_SRT-A | 1.0305 | 0.94607 | 8.437 | Yes
2025W1-N11-SVD217013 | 217013 | HILLSDALE | 230 | 231 | 5 | PS_P1-2_V-2222_SRT-A | PS_P1-2_F-2258_SRT-A | 1.0371 | 0.9129 | 12.417 | Yes
2025W1-N11-SVD208072 | 208072 | SIEG | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.99977 | 0.91438 | 8.54 | Yes
2025W1-N11-SVD208072 | 208072 | SIEG | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.99977 | 0.91438 | 8.54 | Yes
2025W1-N11-SVD207969 | 207969 | TRES | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.98521 | 0.83483 | 15.038 | Yes
2025W1-N11-SVD207969 | 207969 | TRES | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.98521 | 0.83483 | 15.038 | Yes
2025W1-N11-SVD207967 | 207967 | LOFT | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.98105 | 0.82985 | 15.12 | Yes
2025W1-N11-SVD207967 | 207967 | LOFT | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.98105 | 0.82985 | 15.12 | Yes
2025W1-N11-SVD207966 | 207966 | BWAY | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.98449 | 0.83339 | 15.11 | Yes
2025W1-N11-SVD207966 | 207966 | BWAY | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.98449 | 0.83339 | 15.11 | Yes
2025W1-N11-SVD207963 | 207963 | SLYK | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.98466 | 0.83359 | 15.107 | Yes
2025W1-N11-SVD207963 | 207963 | SLYK | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.98466 | 0.83359 | 15.107 | Yes
2025W1-N11-SVD207960 | 207960 | EPAL TR2 | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.99851 | 0.88745 | 11.106 | Yes
2025W1-N11-SVD207960 | 207960 | EPAL TR2 | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.99851 | 0.88745 | 11.106 | Yes
2025W1-N11-SVD207959 | 207959 | EPAL TR1 | 230 | 229 | 8 | PL_60_P12_000226_SRT-A | PL_60_P12_000226A_SRT-A | 0.99854 | 0.88765 | 11.089 | Yes
2025W1-N11-SVD207959 | 207959 | EPAL TR1 | 230 | 229 | 8 | PL_60_P12_000226A_SRT-A | PL_60_P12_000226_SRT-A | 0.99854 | 0.88765 | 11.089 | Yes
2025W1-N11-SVD206264 | 206264 | 28LK ILIFF | 230 | 228 | 8 | JC_P1-2_JCN-230-013_SRT-A | PS_P1-2_E-2205_SRT-A | 1.0243 | 0.83362 | 19.068 | Yes
2025W1-N11-SVD206264 | 206264 | 28LK ILIFF | 230 | 228 | 8 | PS_P1-2_E-2205_SRT-A | JC_P1-2_JCN-230-013_SRT-A | 1.0105 | 0.82978 | 18.068 | Yes
2025W1-N11-SVD206260 | 206260 | 28NEWTON | 230 | 228 | 8 | JC_P1-2_JCN-230-013_SRT-A | PS_P1-2_E-2205_SRT-A | 1.0237 | 0.8334 | 19.031 | Yes
2025W1-N11-SVD206260 | 206260 | 28NEWTON | 230 | 228 | 8 | PS_P1-2_E-2205_SRT-A | JC_P1-2_JCN-230-013_SRT-A | 1.0107 | 0.82958 | 18.114 | Yes
2025W1-N11-SVD206244 | 206244 | 28MONTVILE | 230 | 228 | 8 | JC_P1-2_JCN-230-013_SRT-A | PS_P1-2_E-2205_SRT-A | 1.0273 | 0.83513 | 19.213 | Yes
2025W1-N11-SVD206244 | 206244 | 28MONTVILE | 230 | 228 | 8 | JC_P1-2_JCN-230-017_SRT-A | PS_P1-2_E-2205_SRT-A | 1.0283 | 0.79608 | 23.224 | Yes
2025W1-N11-SVD206244 | 206244 | 28MONTVILE | 230 | 228 | 8 | PS_P1-2_E-2205_SRT-A | JC_P1-2_JCN-230-017_SRT-A | 1.0142 | 0.79562 | 21.853 | Yes
2025W1-N11-SVD206244 | 206244 | 28MONTVILE | 230 | 228 | 8 | PS_P1-2_E-2205_SRT-A | JC_P1-2_JCN-230-013_SRT-A | 1.0142 | 0.83121 | 18.294 | Yes

## Load Drop
PJM N-1-1 Load Drop Result (Summer 2030 Case)
FG# | Contingency 1 | Contingency 2 | MW Drop | PJM Accepting Proposals | Reasons for Exclusions | Comment
N/A | DVP_P1-2: LN 2292_SRT-A | DVP_P1-2: LN 2218_SRT-A | 799.87 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2218_SRT-A | DVP_P1-2: LN 2292_SRT-A | 799.87 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 201_SRT-A | DVP_P1-2: LN 2311_SRT-A | 607.63 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 201_SRT-A | 607.63 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2292_SRT-A | DVP_P1-2: LN 9412_SRT-A | 559.46 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 9412_SRT-A | DVP_P1-2: LN 2292_SRT-A | 559.46 | No | To be adressed through supplemental process.
N/A | DVP_P1-3: 8WSHNGSTAR-TX#1_SRT-A | DVP_P1-2: LN 2291_SRT-A | 514.29 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2291_SRT-A | DVP_P1-3: 8WSHNGSTAR-TX#1_SRT-A | 514.29 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2202_SRT-A | DVP_P1-2: LN 255_SRT-A | 499.34 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2202_SRT-A | 499.34 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2088_SRT-A | 499.34 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2074_SRT-A | 499.34 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2088_SRT-A | DVP_P1-2: LN 255_SRT-A | 499.34 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2074_SRT-A | DVP_P1-2: LN 255_SRT-A | 499.34 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2298_SRT-A | 495.84 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2298_SRT-A | DVP_P1-2: LN 255_SRT-A | 495.83 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 255_SRT-A | DVP_P1-2: LN 2304_SRT-A | 483.68 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2304_SRT-A | DVP_P1-2: LN 255_SRT-A | 483.68 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2140_SRT-A | DVP_P1-2: LN 2251_SRT-A | 466.36 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2251_SRT-A | DVP_P1-2: LN 2140_SRT-A | 466.36 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 206_SRT-A | DVP_P1-2: LN 2178_SRT-A | 430.05 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2178_SRT-A | DVP_P1-2: LN 206_SRT-A | 430.05 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2140_SRT-A | Base Case | 419.35 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2094_SRT-A | DVP_P1-2: LN 2227_SRT-A | 407.55 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2227_SRT-A | DVP_P1-2: LN 2094_SRT-A | 407.55 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 9016_SRT-A | DVP_P1-2: LN 2199_SRT-A | 357.48 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2199_SRT-A | DVP_P1-2: LN 9016_SRT-A | 357.48 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2263_SRT-A | DVP_P1-2: LN 2311_SRT-A | 356.92 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2311_SRT-A | DVP_P1-2: LN 2263_SRT-A | 356.92 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 9450_SRT-A | DVP_P1-2: LN 2246_SRT-A | 353.84 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2246_SRT-A | DVP_P1-2: LN 9450_SRT-A | 353.84 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2246_SRT-A | DVP_P1-2: LN 2163_SRT-A | 353.84 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2163_SRT-A | DVP_P1-2: LN 2246_SRT-A | 353.84 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 9412_SRT-A | DVP_P1-2: LN 2218_SRT-A | 330.56 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2218_SRT-A | DVP_P1-2: LN 9412_SRT-A | 330.56 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 9016_SRT-A | DVP_P1-2: LN 2331_SRT-A | 326.11 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2331_SRT-A | DVP_P1-2: LN 9016_SRT-A | 326.11 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2276_SRT-A | DVP_P1-2: LN 2199_SRT-A | 312.28 | No | To be adressed through supplemental process.
N/A | DVP_P1-2: LN 2199_SRT-A | DVP_P1-2: LN 2276_SRT-A | 312.28 | No | To be adressed through supplemental process.