## Summer GenDeliv
2032 RTEP PJM Generator Deliverability Result (Summer)
PJM Comment | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | Conductor/Transformer Rating (MVA) | PJM Accepting Proposals
Require solution | 2025W1-32GD-S1 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 5815.2 | 6448.9 | 142.87 | 158.44 | DVP_P1-2: LN 576_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S2 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1227.2 | 1288.1 | 145.57 | 152.8 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S3 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5590.2 | 5974.1 | 141.92 | 151.66 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S4 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1219.9 | 1273.5 | 144.7 | 151.07 | PL_48_P71_103285_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S5 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 4336.2 | 4761.8 | 134.68 | 147.9 | DVP_P1-2: LN 574_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S6 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5325 | 5736.1 | 135.19 | 145.62 | DVP_P4-2: 557T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S7 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 6642.9 | 7287 | 132.57 | 145.42 | DVP_P4-2: 57602_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S8 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 6642.9 | 7286.9 | 132.57 | 145.42 | DVP_P4-2: WT576_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S9 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5111.9 | 5543.5 | 129.78 | 140.73 | DVP_P4-2: H2T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S10 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 5097 | 5507.3 | 129.4 | 139.82 | DVP_P4-2: H1T574_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S11 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3117 | 4199.2 | 4347.5 | 134.72 | 139.48 | DVP_P4-2: 562T578_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S12 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 4069.7 | 4069.7 | 138.85 | 138.85 | DVP_P4-2: 56372_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S13 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 4059.5 | 4059.5 | 138.5 | 138.5 | DVP_P4-2: H6T563_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S14 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 5142 | 5446.4 | 130.54 | 138.27 | DVP_P4-2: 557T574_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Not soliciting proposals - transformer | N/A | 314902 | 8CARSON | 314282 | 6CARSON | 2 | 500/230 | 345 | 1056 | 1449.7 | 1449.7 | 137.28 | 137.28 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S15 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4980 | 5393.5 | 126.43 | 136.92 | DVP_P4-2: 56722_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S16 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 4890.2 | 5571.1 | 120.15 | 136.87 | DVP_P1-2: LN 550_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S17 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 4048.5 | 4367.9 | 125.75 | 135.67 | DVP_P1-2: LN 567_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S18 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3968.2 | 3968.2 | 135.39 | 135.39 | DVP_P4-2: 562T563_SRT-S | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S19 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3669 | 3964.6 | 125.18 | 135.27 | DVP_P4-2: 57602_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S20 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3669 | 3964.6 | 125.18 | 135.26 | DVP_P4-2: WT576_SRT-A | Breaker | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S21 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 3012.7 | 3303.2 | 123.36 | 135.26 | DVP_P1-2: LN 576_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S22 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 3272.6 | 3272.6 | 134.01 | 134.01 | DVP_P1-2: LN 563_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S23 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 4918.7 | 5450.9 | 120.85 | 133.92 | AEP_P1-2_#18461_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S24 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3988.9 | 4289.3 | 123.9 | 133.23 | DVP_P1-2: LN 574_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S25 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3117 | 3985.3 | 4123 | 127.86 | 132.27 | DVP_P4-2: 56272_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S26 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 6596.9 | 6596.9 | 131.65 | 131.65 | DVP_P4-2: H6T563_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S27 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3117 | 3951.1 | 4101.5 | 126.76 | 131.59 | DVP_P4-2: 562T579_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S28 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 4741.9 | 5354.2 | 116.5 | 131.55 | DVP_P1-4: 6DAHLGREN_AF2-091 C_1_2_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S29 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3933.2 | 4234.1 | 122.17 | 131.51 | DVP_P1-2: LN 9518_SRT-A | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S30 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4070.2 | 5351.2 | 5351.2 | 131.47 | 131.47 | DVP_P1-2: LN 563_SRT-A | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S31 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4911.9 | 5146.4 | 124.7 | 130.65 | DVP_P7-1: LN 574-9488_SRT-A | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S32 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3918.3 | 4205.4 | 121.7 | 130.62 | DVP_P1-2: LN 552_SRT-S | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S33 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3547.3 | 4185 | 110.18 | 129.99 | DVP_P1-2: LN 568_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S34 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 1054.9 | 1094.2 | 125.14 | 129.8 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S35 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 3877.3 | 4176.3 | 120.43 | 129.72 | DVP_P1-2: LN 581_SRT-A | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S36 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 1049.6 | 1081.8 | 124.51 | 128.33 | PL_48_P71_103319_SRT-A | Tower | 717/843/768/894 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S37 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4704.7 | 5049.4 | 119.44 | 128.19 | DVP_P4-2: 568T581_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S38 | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 1024.2 | 1026.2 | 127.87 | 128.12 | PL_48_P42_101954_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S39 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1023.4 | 1025.4 | 127.77 | 128.02 | PL_08_P42_102683_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S40 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1023.4 | 1025.4 | 127.77 | 128.02 | PL_08_P42_101955_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S41 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 1023.4 | 1025.3 | 127.77 | 128.01 | PL_08_P42_102684_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S42 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3868.2 | 4084.9 | 120.15 | 126.88 | DVP_P1-2: LN 557_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S43 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3838.3 | 4085 | 119.22 | 126.88 | DVP_P1-2: LN 557_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S44 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4721.8 | 4984.2 | 119.87 | 126.54 | DVP_P4-2: H2T557_SRT-S | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S45 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4701.9 | 4975.8 | 119.37 | 126.32 | DVP_P4-2: 56722_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - transformer | N/A | 247669 | 05JOSHUA 1EQ | 242515 | 05JOSHUA | 1 | 1.0/765 | 205 | 867 | 1100.7 | 1078.4 | 126.96 | 124.38 | AEP_P4_#3174_05CLOVRD 765_AA2_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S46 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3755.9 | 3999.1 | 116.66 | 124.21 | DVP_P1-2: LN 567_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S47 | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 993 | 994.7 | 123.97 | 124.18 | PL_48_P42_103291_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S48 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5537.9 | 6221.7 | 110.51 | 124.16 | DVP_P4-2: 536T550_SRT-A | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S49 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4498.4 | 4888.4 | 114.2 | 124.1 | DVP_P4-2: H1T581_SRT-S | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S50 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5529.9 | 6216.4 | 110.36 | 124.05 | DVP_P4-2: H2T550_SRT-S | Breaker | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Not soliciting proposals - transformer | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1052 | 1332.4 | 1301.5 | 126.65 | 123.72 | DVP_P4-2: H1T574_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S51 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 4530.3 | 4858.9 | 115.01 | 123.35 | DVP_P4-2: 568T581_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S52 | 207915 | GLBR | 208120 | SU10 | 1 | 230 | 229 | 801 | 984.3 | 986.2 | 122.89 | 123.12 | PL_48_P12_101741_SRT-A | Single | 647/801/746/903 (SN/SE/WN/WE) | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S53 | 207915 | GLBR | 208120 | SU10 | 2 | 230 | 229 | 801 | 983.6 | 985.4 | 122.79 | 123.03 | PL_08_P12_101740_SRT-A | Single | 647/801/746/903 (SN/SE/WN/WE) | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S54 | 208120 | SU10 | 208113 | SUSQ | 1 | 230 | 229 | 1079 | 1283.2 | 1320.5 | 118.93 | 122.38 | PL_48_P71_102649_SRT-A | Tower | 933/1079/998/1143 (SN/SE/WN/WE) | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S55 | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1079 | 1283.2 | 1320.5 | 118.93 | 122.38 | PL_48_P42_000438_SRT-A | Breaker | 933/1079/998/1143 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S56 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3622.7 | 3916.9 | 112.52 | 121.66 | AEP_P1-2_#18461_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - transformer | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 2 | 500/138 | 201 | 527 | 634.1 | 640.3 | 120.33 | 121.51 | AP_P2-3_MP-500-016_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 235235 | 01FLINTRUN | 235100 | 01FLINTRN | 1 | 500/138 | 201 | 527 | 634.1 | 640.3 | 120.33 | 121.51 | AP_P2-3_MP-500-017_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S57 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5478 | 6035.5 | 109.32 | 120.45 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S58 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3608 | 3869.5 | 112.07 | 120.19 | AEP_P1-2_#18461_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Not soliciting proposals - transformer | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1265 | 1509.6 | 1514.9 | 119.34 | 119.75 | DVP_P4-2: WT576_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1265 | 1509.6 | 1514.9 | 119.34 | 119.75 | DVP_P4-2: 57602_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 314914 | 8MDLTHAN | 314322 | 6MDLTHAN | 1 | 500/230 | 345 | 1057.5 | 1309.6 | 1260.9 | 123.84 | 119.24 | DVP_P1-2: LN 576_SRT-A | Single |  | No
Require solution | 2025W1-32GD-S59 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 3279 | 3836.9 | 101.85 | 119.18 | DVP_P1-2: LN 568_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S60 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3219.5 | 3511.9 | 3826.9 | 109.08 | 118.87 | AP_P1-2_PE-765-242508-237805_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S61 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4382.2 | 4679.8 | 111.25 | 118.81 | DVP_P4-2: 545T552_SRT-A | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S62 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4026.9 | 4678.9 | 102.23 | 118.78 | DVP_P4-2: H1T568_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S63 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5328.4 | 5940.6 | 106.33 | 118.55 | DVP_P7-1: LN 2076-2145_2_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Not soliciting proposals - transformer | N/A | 314218 | 6ELMONT | 314908 | 8ELMONT | 1 | 230/500 | 345 | 1065 | 1264.9 | 1258.1 | 118.77 | 118.14 | DVP_P4-2: H2T557_SRT-S | Breaker |  | No
Require solution | 2025W1-32GD-S64 | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4752.8 | 4803.2 | 116.77 | 118.01 | DVP_P1-2: LN 585_3_SRT-A | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | Yes
Require solution | 2025W1-32GD-S65 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5306.3 | 5908.5 | 105.89 | 117.91 | DVP_P7-1: LN 2076-2145_3_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S66 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4349.2 | 4643.3 | 110.41 | 117.88 | DVP_P4-2: H1T552_SRT-S | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S67 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4344.9 | 4641.9 | 110.3 | 117.85 | DVP_P4-2: H3T552_SRT-S | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S68 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 2725.4 | 2876.1 | 111.6 | 117.77 | DVP_P1-2: LN 582_2_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S69 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3219.5 | 3527.9 | 3785 | 109.58 | 117.56 | AP_P1-2_PE-765-242508-237805_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S70 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3939 | 4311.6 | 4616.2 | 109.46 | 117.19 | DVP_P4-2: H4T581_SRT-A | Breaker | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S71 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 3973.1 | 4612 | 100.87 | 117.09 | DVP_P4-2: H2T568_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Not soliciting proposals - transformer | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3097 | 3598.1 | 3614.4 | 116.18 | 116.71 | AEP_P4_#7443_05DUMONT 765_A_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3097 | 3591.8 | 3611.7 | 115.98 | 116.62 | AEP_P4_#7442_05SORENS 765_K2_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 247669 | 05JOSHUA 1EQ | 242515 | 05JOSHUA | 1 | 1.0/765 | 205 | 867 | 1036.6 | 1010.3 | 119.56 | 116.52 | AEP_P1-2_#3174_6_SRT-A | Single |  | No
Not soliciting proposals - transformer | N/A | 243232 | 05SORENS | 246999 | 05SORENS | 3 | 345/765 | 205 | 3097 | 3584.3 | 3604 | 115.73 | 116.37 | AEP_P4_#7444_05DUMONT 765_A2_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S72 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4237.9 | 4577.7 | 107.59 | 116.21 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S73 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 3955.9 | 4569.5 | 100.43 | 116.01 | DVP_P4-2: 568T571_SRT-S | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4335.2 | 4794.2 | 104.66 | 115.75 | AEP_P1-2_#17216_SRT-A | Single |  | No
Require solution | 2025W1-32GD-S74 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3939 | 4300.4 | 4556.2 | 109.17 | 115.67 | DVP_P4-2: 9517T581_SRT-A | Breaker | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4330 | 4788.9 | 104.54 | 115.62 | AEP_P4_#7217_05VASSEL 765_C1_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S75 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5312.4 | 5747.9 | 106.02 | 114.71 | DVP_P7-1: LN 2076-2145_4_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S76 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2598 | 2827.1 | 2971.8 | 108.82 | 114.39 | DVP_P2-2: SURRY B1_SRT-S | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 6287.8 | 6313.4 | 113.85 | 114.31 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S77 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4205.4 | 4496.9 | 106.76 | 114.16 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S78 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5090.5 | 5709.6 | 101.59 | 113.94 | DVP_P7-1: LN 2114-535_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S79 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5076.6 | 5709.1 | 101.31 | 113.93 | DVP_P7-1: LN 11-2199_SRT-A | Tower | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4247.3 | 4713.5 | 102.54 | 113.8 | AEP_P4_#17219_05GUERNSEY 765_A_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S80 | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 3380.5 | 3521 | 109.08 | 113.62 | AP_P2-3_PE-500-019F_SRT-SL | Breaker | PEPCO: 2738/3099/3672: 3064/3567/4088 : 2738/3099/3672 DOM: 3803/3803/4373 : 4832/4832/5287 : 4668/4668/5141 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S81 | 208120 | SU10 | 208113 | SUSQ | 2 | 230 | 229 | 1079 | 1191.8 | 1216 | 110.45 | 112.69 | PL_48_P42_000439_SRT-A | Breaker | 933/1079/998/1143 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S82 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3467.2 | 3615.8 | 107.69 | 112.31 | DVP_P1-2: LN 552_SRT-S | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S83 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4278.7 | 4405.9 | 108.62 | 111.85 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S84 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4213.8 | 4387.5 | 106.98 | 111.39 | DVP_P7-1: LN 208-259_SRT-S | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S85 | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4489.4 | 4526.5 | 110.3 | 111.21 | DVP_P1-4: 8CARSON_AE2-094 TAP_1_SRT-SW | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | Yes
Require solution | 2025W1-32GD-S86 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 4116.3 | 4377.8 | 104.5 | 111.14 | DVP_P4-2: 9517T581_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S87 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4122.6 | 4362.7 | 104.66 | 110.76 | DVP_P7-1: LN 2076-2145_2_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S88 | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3289.1 | 3766.2 | 96.68 | 110.71 | AP_P1-2_PE-765-242508-237805_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | Yes
Require solution | 2025W1-32GD-S89 | 970672 | AG2-436 TP | 941030 | AE2-094 TAP | 1 | 500 | 345 | 4070.2 | 4466.3 | 4502.7 | 109.73 | 110.63 | DVP_P1-2: LN 511_SRT-S | Single | 4295/4330/4996 : 4979/5022/5953 : 4849/4893/5804 | Yes
Not soliciting proposals - transformer | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1265 | 1448.8 | 1397.3 | 114.53 | 110.46 | DVP_P4-2: 562T563_SRT-S | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4343.4 | 4794.2 | 99.87 | 110.24 | AEP_P1-2_#17216_SRT-A | Single |  | No
Require solution | 2025W1-32GD-S90 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 2946.2 | 3548.1 | 91.51 | 110.21 | AP_P1-2_PE-765-242508-237805_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S91 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4113.3 | 4340 | 104.42 | 110.18 | DVP_P7-1: LN 2076-2145_4_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4338.2 | 4788.9 | 99.75 | 110.11 | AEP_P4_#7217_05VASSEL 765_C1_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S92 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4109.8 | 4336.4 | 104.34 | 110.09 | DVP_P7-1: LN 2076-2145_3_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S93 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3045.8 | 3224.2 | 103.92 | 110 | DVP_P7-1: LN 211-228_SRT-S | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S94 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 3759.8 | 4329.7 | 95.45 | 109.92 | DVP_P4-2: H1T568_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S95 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 2391.9 | 2683.7 | 97.94 | 109.89 | AEP_P1-2_#18461_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S96 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4154.7 | 4326.4 | 105.48 | 109.84 | DVP_P7-1: LN 211-228_SRT-S | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Not soliciting proposals - transformer | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1057.5 | 1213.4 | 1161.4 | 114.74 | 109.83 | DVP_P1-2: LN 563_SRT-A | Single |  | No
Require solution | 2025W1-32GD-S97 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4159.6 | 4322.3 | 105.6 | 109.73 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S98 | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4436.3 | 4464.9 | 109 | 109.7 | DVP_P1-2: LN 585_2_SRT-A | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | Yes
Require solution | 2025W1-32GD-S99 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2442.1 | 2387.5 | 2678.4 | 97.77 | 109.67 | AP_P1-2_PE-765-242508-237805_SRT-A | Single | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S100 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2901.4 | 3210.4 | 98.99 | 109.53 | AEP_P2-2_#1372_05JOSHUA 765_1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S101 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4131.3 | 4313.1 | 104.88 | 109.5 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - transformer | N/A | 314322 | 6MDLTHAN | 314914 | 8MDLTHAN | 1 | 230/500 | 345 | 1265 | 1435.3 | 1385 | 113.46 | 109.49 | DVP_P4-2: 56372_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S102 | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 3243 | 3389.3 | 104.65 | 109.37 | AP_P2-3_PE-500-019B_SRT-A | Breaker | PEPCO: 2738/3099/3672: 3064/3567/4088 : 2738/3099/3672 DOM: 3803/3803/4373 : 4832/4832/5287 : 4668/4668/5141 | Yes
Require solution | 2025W1-32GD-S103 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 3369 | 3518.7 | 104.64 | 109.29 | DVP_P1-2: LN 581_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Not soliciting proposals - transformer | N/A | 313440 | 8VINTHIL | 314125 | 6VINTHIL | 2 | 500/230 | 345 | 1440 | 1548.1 | 1571.8 | 107.51 | 109.15 | DVP_P4-2: H1T2114_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S104 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2895 | 3194.8 | 98.77 | 109 | DVP_P7-1: LN 2076-2145_2_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S105 | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3284.6 | 3706 | 96.55 | 108.94 | AP_P1-2_PE-765-237805-237806_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | Yes
Require solution | 2025W1-32GD-S106 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4071.5 | 4281.6 | 103.36 | 108.7 | DVP_P7-1: LN 2076-2145_2_SRT-A | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S107 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 4330 | 4430.2 | 4703.1 | 102.31 | 108.62 | Base Case | Single | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S108 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5047.6 | 5441.2 | 100.73 | 108.59 | DVP_P2-2: GERMANNA_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5959.2 | 5995.1 | 107.9 | 108.55 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S109 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5004.9 | 5439.5 | 99.88 | 108.55 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4255.5 | 4713.6 | 97.85 | 108.38 | AEP_P4_#17219_05GUERNSEY 765_A_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S110 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3012.9 | 3176.6 | 102.79 | 108.38 | DVP_P7-1: LN 177-2113_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S111 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4066.1 | 4268.3 | 103.23 | 108.36 | DVP_P7-1: LN 2076-2145_3_SRT-A | Tower | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S112 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 2992.5 | 3486.5 | 92.95 | 108.29 | DVP_P1-2: LN 550_SRT-A | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S113 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 3707.5 | 4265.2 | 94.12 | 108.28 | DVP_P4-2: H2T568_SRT-A | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S114 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3219.5 | 2944.6 | 3486 | 91.46 | 108.28 | AP_P1-2_PE-765-237805-237806_SRT-A | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S115 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5102.9 | 5420 | 101.83 | 108.16 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S116 | 314922 | 8POSSUM | 200019 | BURCHES | 1 | 500 | 233/345 | 3099 | 3262.6 | 3352 | 105.28 | 108.16 | PEPCO_P4_PP41_SRT-A | Breaker | PEPCO: 2738/3099/3672: 3064/3567/4088 : 2738/3099/3672 DOM: 3803/3803/4373 : 4832/4832/5287 : 4668/4668/5141 | Yes
Require solution | 2025W1-32GD-S117 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 3011.2 | 3169.5 | 102.74 | 108.14 | DVP_P7-1: LN 19-2154_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Not soliciting proposals - transformer | N/A | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 935.3 | 990.5 | 1011.3 | 105.91 | 108.12 | DVP_P1-2: LN 557_SRT-A | Single |  | No
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5945.2 | 5967.3 | 107.64 | 108.04 | AEP_P4_#6189_05HANG R 765_D1_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S118 | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3552.3 | 3671.5 | 104.42 | 107.93 | DVP_P1-2: LN 539_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | Yes
Require solution | 2025W1-32GD-S119 | 314908 | 8ELMONT | 314911 | 8LADYSMITH | 1 | 500 | 345 | 5011 | 5024.7 | 5404.9 | 100.27 | 107.86 | PL_08_P22_102799_SRT-A | Bus | 4330/4330/5011 : 4980/5023/5928 : 4849/4893/5774 | Yes
Require solution | 2025W1-32GD-S120 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2995.9 | 3161.4 | 102.21 | 107.86 | DVP_P7-1: LN 2024-2102_SRT-A | Tower | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution | 2025W1-32GD-S121 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 4086.1 | 4245.7 | 103.73 | 107.79 | DVP_P2-2: BASIN B7_SRT-A | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S122 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 3966.7 | 4242 | 100.7 | 107.69 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 243206 | 05DUMONT | 290606 | 05DUMONT_RS | Z1 | 765 | 205 | 5001 | 5380.6 | 5379.8 | 107.59 | 107.57 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S123 | 314911 | 8LADYSMITH | 313483 | 8KRAKEN | 1 | 500 | 345 | 3219.5 | 2996.2 | 3460.1 | 93.06 | 107.47 | DVP_P1-4: 6DAHLGREN_AF2-091 C_1_2_SRT-A | Single | 3396/3425/3939 : 4337/4375/4759 : 4186/4222/4628 | Yes
Require solution | 2025W1-32GD-S124 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3939 | 3973.4 | 4231.8 | 100.87 | 107.43 | AP_P2-2_WP-500-DRT14_SRT-SL | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S125 | 314934 | 8SPOTSYL | 314916 | 8MORRSVL | 1 | 500 | 345 | 3117 | 3213.2 | 3338.8 | 103.09 | 107.12 | DVP_P2-2: MORRISVILLE B1_SRT-S | Bus | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4628 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4763.2 | 4893.2 | 104.2 | 107.05 | AEP_P4_#2942_05KAMMER 765_PP_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S126 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4033.7 | 4214.5 | 102.4 | 107 | DVP_P7-1: LN 222-86_SRT-A | Tower | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S127 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3939 | 3689.5 | 4213.9 | 93.67 | 106.98 | DVP_P4-2: 568T571_SRT-S | Breaker | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S128 | 207973 | FRAC | 208072 | SIEG | 1 | 230 | 229 | 628 | 674.1 | 670.5 | 107.34 | 106.76 | PL_60_P71_000890_SRT-A | Tower | 513/628/564/682 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5863.9 | 5893.6 | 106.17 | 106.71 | AEP_P4_#709_05HANG R 765_D2_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5632.1 | 5886.9 | 101.98 | 106.59 | AEP_P4_#3139_05FLTLCK 765_B_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S129 | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3515.7 | 3626.2 | 103.35 | 106.59 | DVP_P1-2: LN 569_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | Yes
Require solution | 2025W1-32GD-S130 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2982.9 | 3121.9 | 101.77 | 106.51 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Not soliciting proposals - see problem statement for details | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 6287.8 | 6347.1 | 105.43 | 106.42 | AEP_P4_#7334_05JEFRSO 765_A2_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S131 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 4043.8 | 4191.5 | 102.66 | 106.41 | DVP_P2-2: BREMO B1_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Require solution | 2025W1-32GD-S132 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2941.5 | 3114.5 | 100.36 | 106.26 | AEP_P2-2_#1377_05J.FERR 765_1_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Not soliciting proposals - transformer | N/A | 313440 | 8VINTHIL | 314125 | 6VINTHIL | 2 | 500/230 | 345 | 1440 | 1505.2 | 1528.6 | 104.53 | 106.15 | DVP_P4-2: H1T2101_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 313440 | 8VINTHIL | 314125 | 6VINTHIL | 1 | 500/230 | 345 | 1440 | 1505.2 | 1528.6 | 104.53 | 106.15 | DVP_P4-2: H2T2101_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S133 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3939 | 3979 | 4178.4 | 101.02 | 106.08 | PL_08_P22_102799_SRT-A | Bus | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4074.6 | 4370.7 | 98.37 | 105.52 | AEP_P1-2_#7441_100545_SRT-A | Single |  | No
Not soliciting proposals - transformer | N/A | 314214 | 6CHCKAHM | 314903 | 8CHCKAHM | 1 | 230/500 | 345 | 1107 | 1181.7 | 1165.9 | 106.75 | 105.32 | DVP_P4-2: 56702_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S134 | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4996 | 5207.6 | 5260.5 | 104.24 | 105.29 | DVP_P4-5: W72_SRT-A | Breaker | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | Yes
Require solution | 2025W1-32GD-S135 | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4996 | 5207.3 | 5260.1 | 104.23 | 105.29 | DVP_P4-2: 58572_SRT-A | Breaker | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 4062.1 | 4358.2 | 98.07 | 105.22 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 200018 | CHALK PT | 223983 | CHALK230 | 2 | 500/230 | 233 | 796 | 799.5 | 836.3 | 100.45 | 105.07 | PEPCO_P4_PP80_SRT-A | Breaker |  | No
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S136 | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 841.7 | 839.9 | 105.08 | 104.85 | PL_08_P42_102625_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4365 | 4785.1 | 95.49 | 104.68 | 34506 34542_SRT-A | Tower |  | No
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S137 | 208040 | MONT | 207915 | GLBR | 2 | 230 | 229 | 801 | 839.2 | 837.4 | 104.77 | 104.54 | PL_08_P42_102682_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4641.5 | 4771.1 | 101.54 | 104.38 | AEP_P4_#37_05MOUNTN 765_B1_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4641.8 | 4770.8 | 101.55 | 104.37 | AP_P2-3_MP-500-021_SRT-SL | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4642.4 | 4770.5 | 101.56 | 104.36 | AP_P2-3_MP-500-020_SRT-SL | Breaker |  | No
Require solution | 2025W1-32GD-S138 | 314924 | 8SURRY | 314903 | 8CHCKAHM | 1 | 500 | 345 | 2931 | 2892.5 | 3052 | 98.69 | 104.13 | DVP_P2-2: BASIN B7_SRT-A | Bus | 3425/3425/3939 : 4375/4375/5031 : 4222/4222/4855 | Yes
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S139 | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 834.3 | 832.8 | 104.16 | 103.97 | PL_08_P42_102075_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S140 | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 834.3 | 832.8 | 104.16 | 103.97 | PL_08_P42_102623_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5683 | 5737.8 | 102.9 | 103.89 | AEP_P7-1_#17567_SRT-SL | Tower |  | No
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S141 | 208040 | MONT | 207915 | GLBR | 2 | 230 | 229 | 801 | 831.9 | 830.3 | 103.85 | 103.66 | PL_08_P42_102074_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S142 | 314940 | 8ROGERS RD | 970672 | AG2-436 TP | 1 | 500 | 345 | 4070.2 | 4149.6 | 4207 | 101.95 | 103.36 | DVP_P1-2: LN 511_SRT-S | Single | 4295/4330/4996 : 4979/5022/5953 : 4849/4893/5804 | Yes
Require solution | 2025W1-32GD-S143 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 3159.2 | 3324.8 | 98.13 | 103.27 | DVP_P1-2: LN 581_SRT-A | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Require solution | 2025W1-32GD-S144 | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 3401.9 | 3402.2 | 3511.5 | 100.01 | 103.22 | DVP_P1-2: LN 5007_SRT-A | Single | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5541.7 | 5699.6 | 100.34 | 103.2 | 34506 34542_SRT-A | Tower |  | No
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5646.7 | 5696.6 | 102.24 | 103.14 | AEP_P7-1_#17566_SRT-SL | Tower |  | No
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5631.7 | 5679.7 | 101.97 | 102.84 | AEP_P7-1_#16837_SRT-SL | Tower |  | No
Require solution | 2025W1-32GD-S145 | 314914 | 8MDLTHAN | 314918 | 8NO ANNA | 1 | 500 | 345 | 3396 | 3334.5 | 3491.8 | 98.19 | 102.82 | Base Case | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4628 | Yes
Not soliciting proposals - transformer | N/A | 314903 | 8CHCKAHM | 314214 | 6CHCKAHM | 1 | 500/230 | 345 | 1107 | 1125.6 | 1136.9 | 101.68 | 102.7 | DVP_P4-2: H2T557_SRT-S | Breaker |  | No
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S146 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 967.7 | 1061.7 | 93.59 | 102.68 | PL_48_P42_000438_SRT-A | Breaker | Same as base case | Yes
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S147 | 200022 | SUSQ | 208116 | SUSQTR21 | 21 | 500/230 | 229 | 1034 | 967.7 | 1061.7 | 93.59 | 102.68 | PL_48_P71_102649_SRT-A | Tower | Same as base case | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 3958.7 | 4251 | 95.57 | 102.63 | AEP_P4_#7446_05MARYSV 765_B2_SRT-A | Breaker |  | No
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S148 | 208109 | SUNB | 207970 | NESC230 | 1 | 230 | 229 | 624 | 658 | 640.1 | 105.45 | 102.58 | PL_08_P71_101751_SRT-A | Tower |  | Yes
Require solution | 2025W1-32GD-S149 | 314936 | 8RAWLINGS | 314902 | 8CARSON | 1 | 500 | 345 | 4070.2 | 4157.8 | 4168.7 | 102.15 | 102.42 | DVP_P1-2: LN 585_SRT-A | Single | 4294/4330/4996: 4979/5022/5953 : 4849/4893/5804 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S150 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 847.1 | 862.3 | 100.48 | 102.29 | PL:48:P42:000428 _SRT-A | Breaker | 717/843/768/894 (SN/SE/WN/WE) | Yes
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S151 | 208013 | SUMT2_B4 | 208090 | SUMT | 2 | 230 | 229 | 801 | 820.2 | 819.2 | 102.4 | 102.28 | PL_02_P42_001053_SRT-A | Breaker | 647/801/746/903 (SN/SE/WN/WE) | Yes
Require solution | 2025W1-32GD-S152 | 314902 | 8CARSON | 314914 | 8MDLTHAN | 1 | 500 | 345 | 3425 | 3359 | 3494.6 | 98.07 | 102.03 | Base Case | Single | 3425/3425/3939 : 3983/4018/5030 : 3879/3914/4855 | Yes
Not soliciting proposals - terminal equipment limited | N/A | 246999 | 05SORENS | 290607 | 05SORENSN_RM | Z1 | 765 | 205 | 5523 | 5572 | 5615.6 | 100.89 | 101.68 | AEP_P7-1_#16838_SRT-SL | Tower |  | No
Not soliciting proposals - terminal equipment limited | N/A | 242928 | 05MARYSV | 290620 | 05MARYSVL_RM | Z1 | 765 | 205 | 4571 | 4481.1 | 4646.5 | 98.03 | 101.65 | AEP_P4_#8085_05MARYSV 345_H_SRT-A | Breaker |  | No
Require solution | 2025W1-32GD-S153 | 314918 | 8NO ANNA | 314934 | 8SPOTSYL | 1 | 500 | 345 | 3219.5 | 3101.5 | 3265.4 | 96.33 | 101.43 | DVP_P1-2: LN 552_SRT-S | Single | 3396/3425/3939 : 3938/4018/4759 : 3879/3914/4855 | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S154 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 834.1 | 853.8 | 98.95 | 101.28 | PL_40_P12_000182_SRT-A | Single | 717/843/768/894 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 5959.2 | 6038 | 99.92 | 101.24 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker |  | No
Not soliciting proposals - transformer | N/A | 290022 | 05J.FERR 1EQ | 242514 | 05J.FERR | 1 | 1.0/765 | 205 | 1945 | 1864.7 | 1966.3 | 95.87 | 101.09 | DVP_P4-2: 562T563_SRT-S | Breaker |  | No
Require solution | 2025W1-32GD-S155 | 289543 | 05YEAT | 313440 | 8VINTHIL | 1 | 500 | 345 | 4146 | 3982.6 | 4180.1 | 96.06 | 100.82 | DVP_P7-1: LN 2101-569_SRT-A | Tower | 3572/3619/4146 : 5154/5154/5927 : 3753/4443/4851 | Yes
Not soliciting proposals - transformer | N/A | 242520 | 05J.FERR | 290022 | 05J.FERR 1EQ | 1 | 500/1.0 | 205 | 1945 | 1865.1 | 1960.4 | 95.89 | 100.79 | DVP_P4-2: 562T563_SRT-S | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 290621 | 05MARYSVL_RF | 242928 | 05MARYSV | Z1 | 765 | 205 | 4142 | 3991.1 | 4169 | 96.36 | 100.65 | AEP_P4_#2942_05KAMMER 765_PP_SRT-A | Breaker |  | No
Ensure to right size to the 2032 loading level | 2025W1-32GD-S156 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 829.2 | 848.3 | 98.37 | 100.63 | PL_48_P42_103276_SRT-A | Breaker | 717/843/768/894 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 5945.2 | 6001.1 | 99.68 | 100.62 | AEP_P4_#6189_05HANG R 765_D1_SRT-A | Breaker |  | No
Ensure to right size to the 2032 loading level | 2025W1-32GD-S157 | 208113 | SUSQ | 207972 | TOMH | 2 | 230 | 229 | 843 | 829.1 | 848 | 98.35 | 100.59 | PL_48_P42_001156_SRT-A | Breaker | 717/843/768/894 (SN/SE/WN/WE) | Yes
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S158 | 208109 | SUNB | 207970 | NESC230 | 1 | 230 | 229 | 624 | 643.4 | 627.2 | 103.11 | 100.51 | PL_48_P71_101752_SRT-A | Tower |  | Yes
Ensure to right size to the 2032 loading level | 2025W1-32GD-S159 | 208113 | SUSQ | 207972 | TOMH | 1 | 230 | 229 | 843 | 832.2 | 847.3 | 98.72 | 100.51 | PL_48_P12_102309_SRT-A | Single | 717/843/768/894 (SN/SE/WN/WE) | Yes
Not soliciting proposals - terminal equipment limited | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4082.7 | 4370.7 | 93.88 | 100.5 | AEP_P1-2_#7441_100545_SRT-A | Single |  | No
Not soliciting proposals - terminal equipment limited | N/A | 243206 | 05DUMONT | 290606 | 05DUMONT_RS | Z1 | 765 | 205 | 5001 | 5011.7 | 5025.3 | 100.21 | 100.49 | AEP_P4_#1760_05JEFRSO 765_A_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 5576.6 | 5993.1 | 93.5 | 100.49 | AEP_P4_#707_05MARYSV 765_B1_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2870.4 | 2857.2 | 100.93 | 100.46 | PL_10_P42_100569_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2869.3 | 2856 | 100.89 | 100.42 | PN_P2-3_PN-500-001C-DRT_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 200011 | KEYSTONE | 200009 | JUNI | 1 | 500 | 229/226 | 2844 | 2869.3 | 2856 | 100.89 | 100.42 | PL_10_P12_000086_SRT-A | Single |  | No
Not soliciting proposals - terminal equipment limited | N/A | 290607 | 05SORENSN_RM | 290608 | 05MARYSVL_RS | 1 | 765 | 205 | 5964 | 5632.1 | 5983.7 | 94.44 | 100.33 | AEP_P4_#3139_05FLTLCK 765_B_SRT-A | Breaker |  | No
Not soliciting proposals - terminal equipment limited | N/A | 962760 | AG1-125 TP | 290621 | 05MARYSVL_RF | 1 | 765 | 205 | 4349 | 4070.3 | 4358.2 | 93.59 | 100.21 | AEP_P4_#7441_05SORENS 765_J1_SRT-A | Breaker |  | No
Require solution - related to the 2030 violations in PPL and requires holistic solution | 2025W1-32GD-S160 | 208040 | MONT | 207915 | GLBR | 1 | 230 | 229 | 801 | 803.5 | 801.9 | 100.31 | 100.11 | PL_08_P12_101739_SRT-A | Single | 647/801/746/903 (SN/SE/WN/WE) | Yes