# loaVERSION 2 – August 21, 2026

# PJM RTEP - 2026 RTEP Proposal Window #1

PROBLEM STATEMENT & REQUIREMENTS

## Document Scope: Violations in 2031 Summer/Winter/Light Load reliability analysis; 2034 Summer/Winter/Light Load Reliability Analysis; 2031 TO FERC 715 Analysis; 2031 Short Circuit Analysis.

This 2026 RTEP Proposal Window #1 Problem Statement Version 2 updates the Problem Statement for the 2026 RTEP Proposal Window #1, which opened on July 20, 2026, to reflect reductions in load projections in the ComEd Zone of PJM and associated changes to the generation profile,  as well as updates from the PJM Generation Interconnection Cycle status. This update does not constitute the opening of a new proposal window.

# 2026 RTEP Proposal Window #1

### Purpose of Proposal Window

PJM seeks technical solutions, also called proposals, to resolve potential reliability criteria violations on facilities identified below in accordance with all applicable planning criteria (PJM, NERC, SERC, RF, and Local Transmission Owner criteria).

The 2026 RTEP competitive process window No. 1 focuses on addressing the near-term reliability needs of PJM interconnection identified through PJM’s five-year planning analyses as summarized by the planning criteria listed below. PJM plans to further refine and complement the planning solutions needed for the entire PJM interconnection part of the 2027 RTEP cycle once the 2026 PJM Reliability Backstop Procurement (RBP) is concluded and announced.

PJM is not specifically encouraging right-sized solutions to address needs in the 8-year planning models at this time. However, window participants may propose right-sizing developments where they identify opportunities to maximize the use of rights-of-way or to right-size upgrades to existing lines triggered by the 5-year analysis where doing so may result in a more efficient or cost-effective solution. In all cases, window participants are encouraged to submit solutions addressing the needs identified in the updated 5-year models, as well as any right-sizing opportunities they may propose for PJM consideration, with an explanation of how the proposed right-sizing solution would result in a more efficient or cost-effective solution.

The planning models provided for the 8-year horizon are provided primarily for informational purposes and to provide visibility into potential system needs beyond the near, 5-year planning needs. Any longer-term needs will be evaluated as part of the 2027 RTEP.

#### Criteria Applied by PJM for this Proposal Window

- 2031 Summer Baseline Thermal and Voltage N-1 Contingency Analysis

- 2031 Summer Generator Deliverability/IPD Analysis

- 2031 Summer N-1-1 Thermal and Voltage Analysis

- 2031 Winter Baseline Thermal and Voltage N-1 Contingency Analysis

- 2031 Winter Generator Deliverability/IPD Analysis

- 2031 Winter N-1-1 Thermal and Voltage Analysis

- 2031 Light Load Baseline Thermal and Voltage N-1 Contingency Analysis

- 2031 Light Load Generator Deliverability/IPD Analysis

- 2031 Winter/Summer Load Deliverability Analysis

- 2031 Short Circuit Analysis

- AEP FERC Form 715

- AMPT FERC Form 715

- ComEd FERC Form 715

- DEOK FERC Form 715

- DOM FERC Form 715

- FE FERC Form 715

- PPL FERC Form 715

- PSEG FERC Form 715

- ODEC FERC Form 715

- PECO FERC Form 715

- BGE FERC Form 715

- 2034 Summer Generator Deliverability

- 2034 Winter Generator Deliverability

- 2034 Light Load Generator Deliverability

### Terminology for Proposal Windows

Through the analyses listed above, PJM has compiled a list of criteria violations. The violations and the impacted facilities are identified by a table of flowgates. Descriptions of the column headings are provided below. Different analyses often use different column headings.

#### Typical thermal analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| FG # | Flowgate Number | A sequential numbering of the identified potential violations |
| Fr Bus | From Bus Number | PSS/E model bus number corresponding to one end of line identified as a potential violation |
| Fr Name | From Bus Name | PSS/E model bus name corresponding to one end of line identified as a potential violation |
| To Bus | To Bus Number | PSS/E model bus number corresponding to other end of line identified as a potential violation |
| To Name | To Bus Name | PSS/E model bus name corresponding to other end of line identified as a potential violation |
| Monitored Facility | Monitored Facility | The circuit on which a potential violation is occurring |
| Base Rate (MVA) | Base Rate (MVA) | Normal Facility Rating (Rate A) |
| % Overload | Percentage Overload | Percentage above corresponding Facility Rating |
| CKT | Circuit ID | Circuit number of identified potential violation |
| KVs | Kilovolt level (A/B) | Kilovolt level of both sides of potential violation, if A does not equal B, potential violation is a transformer |
| Areas | Area Numbers (A/B) | Area numbers of both ends of potential violation (A=From Bus Area Number, B=To Bus Area Number) If A does not equal B, potential violation is a tie line |
| Rating | Facility Rating | Applicable thermal rating (MVA) of facility |
| DC Ld(%) | Direct Current Loading percentage | Percentage above Facility Rating determined from DC testing |
| AC Ld(%) | Alternating Current Loading percentage | Percentage above Facility Rating determined from AC testing |
| Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower) |
| Cont Name | Contingency Name | Contingency name as identified in associated contingency file or embedded in the spreadsheet |
| Contingency | Contingency | Contingency description |
| Violation Date | Violation Date | Date on which violation is expected to occur |
| Analysis Case | Analysis Case | Case title to use in replicating analysis |

#### Typical voltage analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| FG # | Flowgate Number | A sequential numbering of the identified potential violations |
| Bus # | Bus Number | PSS/E model bus number corresponding to bus identified as a potential violation |
| KVs | Kilovolt level | Kilovolt level of bus identified as potential violation |
| Area | Area Number | Area number of bus identified as potential violation |
| ContVolt | Contingency Voltage (P.U.) | Per Unit Voltage at identified bus after contingency is applied |
| BaseVolt | Basecase Voltage (P.U.) | Per Unit Voltage at identified bus before contingency is applied |
| Low Limit | Low Voltage Limit(P.U.) | Threshold of Per Unit Low voltage, if ContVolt is under this limit, a potential violation is identified |
| Upper Limit | High Voltage Limit(P.U.) | Threshold of Per Unit High voltage, if ContVolt is over this limit, a potential violation is identified |
| Cont Type | Contingency Type | Contingency categorization (e.g., Single, Bus, Line_FB, Tower) |
| Vdrop (%) | Voltage drop | The percentage that the voltage has dropped as a result of the contingency |
| Contingency | Contingency | Contingency name as identified in associated contingency file |
| Contingency 1 | First Contingency | N-1 (first) contingency identified |
| Contingency 2 | Second Contingency | N-1-1 (second) contingency identified in N-1-1 analysis |

#### Typical short circuit analysis column headings:

| Column Heading | Title | Description |
| --- | --- | --- |
| Flowgate # | Flowgate Number | A sequential numbering of the identified potential violations |
| TO | Transmission Owner | Transmission Owner company name |
| BUS_NO | Bus Number | ASPEN model bus number corresponding to bus identified as the location of an over duty breaker |
| BUS | Bus Name | ASPEN model bus name corresponding to bus identified as the location of an over duty breaker |
| BREAKER | Breaker ID | Breaker ID of the identified over duty breaker |
| RATINGTYPE | Rating Type | Short circuit current calculation methodology. Either 'S' for Symmetrical Current or 'T' for Total Current |
| Notes | Notes | Breaker Interrupting Rating Class (kA or MVA) |
| DUTY_P | Duty Percent | The percentage of worst case interrupting duty (amps) to the breaker's interrupting capability (amps) |
| DUTY_A | Duty Amps | The worst case interrupting duty (amps) |
| BKR_CAPA | Breaker Capability Amps | The breaker's interrupting capability rating (amps) |

### Proposal Window Exclusion Definitions

The following definitions explain the basis for excluding flowgates from the competitive planning process and designating projects to the incumbent Transmission Owner.

Flowgates excluded from competition will include the underlined language in the comment field.

- Immediate Need Exclusion: For immediate reliability needs that must be addressed within three years or less and for which PJM determines a proposal window may not be feasible, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer to Operating Agreement, Schedule 6 § 1.5.8(m)(1)

- Below 200kV Exclusion: Due to the lower voltage level of the identified violations, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer to Operating Agreement, Schedule 6 § 1.5.8(n)

- Substation Equipment Exclusion: For thermal reliability violations on existing transmission substation equipment, these reliability violations are excluded from the competitive proposal window process. As a result, the local Transmission Owner will be the Designated Entity. Refer Operating Agreement, Schedule 6 § 1.5.8(p)

- Supplemental Projects scope: These cover violations to be addressed through supplemental solutions, including addressing load loss criteria and issues related to the distribution of future planning load that is included part of the forecast (load mapping issues to local transmission networks)

- 2034, 8-year exclusions: All violations reflected by this planning assessment will be addressed following the award of the PJM 2026 RBP and currently is planned for inclusion part of the 2027 RTEP.

- Resolved Violations: Violations for which PJM has already selected a transmission project that is expected to resolve the violation, including projects with planned in-service dates beyond the five-year planning horizon.

### Analysis Procedure

Participants are expected to develop solutions to the identified criteria violations and perform analysis to validate that the solutions remove these violations in compliance with the PJM planning manuals and criteria listed in PJM Manual 14B. The competitive planning process is documented in PJM Manual 14F.

Proposed solutions must also meet Transmission Owner Planning Criteria.

Although PJM does its best to provide complete and accurate results, changes to the list of violations under consideration are possible. Flowgates may be added or removed from consideration in the proposal window as part of future updates. For regional transfer enhancements, proposed solutions must address flowgates at higher transfer levels already established in the PJM RTEP window basecase models. PJM plans to address any corrections and minor adjustments to the 2031 and 2034 baseline scenarios to be posted as part of the window opening.  PJM works with PJM Transmission Owners, Generation Owners, neighboring ISOs and Transmission Owners and other affected parties to verify the quality of the analysis. PJM endeavors to minimize such changes and will clearly communicate any changes to the participants.

PJM regularly updates the system model to reflect changes to the transmission system. Analyses are performed to verify that violations continue to be valid, no new violations have appeared, and proposed solutions still address the targeted violation(s).

Based on its evaluation of the proposals received, PJM will determine the more efficient or cost-effective enhancements or expansions for any violation.

### Scope of Work

PJM is seeking proposals to resolve identified reliability criteria violations in all zones as demonstrated in the 2031 RTEP model suite and associated flowgates. The 2034 RTEP model suite and posted 2034 results are primarily for reference only at this time. PJM anticipates evaluating the broader longer term needs (needed more than five years out) and refining the planned solutions as part of the 2027 RTEP cycle once the PJM RBP auction results are finalized.

#### OBJECTIVES:

- Develop complete solutions to address the identified criteria violations;

- Develop solutions to address all new criteria violations generated as a consequence of the proposed solution. Solutions to these secondary violations are required for the proposal to be considered.

- Adhere to all applicable planning criteria, including PJM, NERC, SERC, RF and Local Transmission Owner Criteria.

- All solutions, need to consider impacts on short circuit levels with particular emphasis on ComEd and Dominion zones.

#### REQUIREMENTS:

- Holistic solutions are to be designed such that they are robust and expandable as the needs evolve within the areas. A robust solution ensures, at a minimum, near-term reliability needs are addressed while also allowing for efficient and prudent consideration of future and evolving needs. The proposing entities are encouraged to outline their rationale, benefits and general merits of their proposed developments as part of their submissions.

#### ASSUMPTIONS and Key Zone Reliability Needs:

- ComEd:

- PJM identified a number of violations in the ComEd zone in 2031.

The ComEd load in the 2031 case, consistent with recent updates to its load forecast, has increased by approximately 2.7 GW (reflecting the recent 1.3 GW reduction) compared to the 2030 study year evaluated in the 2025 RTEP cycle. The 2031 models show flows from south and west to north and east to serve these additional loads. There has also been 1 GW of generation deactivation in the ComEd zone (expected to be deactivated by 2031), along with the partial Elwood reactivation. The generation profile is also updated with the inclusion of additional generation from the interconnection process required to meet the load forecast, most of which is generation surrounding the outskirts of the ComEd zone.

For 2031; all of these system changes in the ComEd zone results in 16 overloaded 345 kV facilities. The underlying 138 kV system is also impacted, resulting in 40 overloaded facilities (including transformers), particularly under N-1-1 conditions. PJM has also identified overlapping facilities between the reliability needs identified through the applicable Transmission Owner’s Attachment M-3 local planning processes and the needs identified in this competitive planning window, as reflected in the associated M-3 solutions included in the posted results, notably, the ComEd M-3 solutions (pg. 8-14) presented at the July 2026 TEAC.

PJM has added these M-3 solutions to the posted study files for transparency and to ensure proposing entities can take the recently presented solutions into consideration when developing proposals. PJM has also reflected the withdrawal of ComEd-2024-016 (load at Beverly Rd 345 kV) and ComEd-2025-016 (load at Rowell 345 kV) that was previously modeled in earlier versions of the preliminary files.

Please note that ComEd has specific rating criteria that is part of the Exelon Transmission Planning Criteria (pg. 4) that utilizes both short-term emergency and load dump ratings, which are reflected in Rate 4 and Rate 3 in the PSS/E cases, respectively.

Consideration of short circuit impacts of the proposed developments will be required on existing and planned facilities in and around the ComEd zone.

The ComEd zone also fails in the load deliverability study to meet PJM Capacity Emergency Transfer Objective (CETO) which is a metric used by PJM to estimate the amount of power needed to be delivered into a specific PJM Zone or Region under specific stressed operating scenarios (usually Summer Peak). Accordingly, PJM expects all regional bulk enhancements proposed to address the transfer-in needs for ComEd, consider assessing the proposed solutions ability to address not only the pre-established transfer in conditions in the cases, but also higher transfers as reflected in the PJM 2026 Forecasted load growth levels (considering the recent reduction in the ComEd zone load for 2031 and 2034) and potential future retirements into PJM of conventional thermal assets. The details are in the Load Deliverability Analysis section. PJM will take load deliverability performance into consideration when evaluating proposals, to ensure the ComEd LDA passes the load deliverability test. Due to the complexity of conducting detailed Load Deliverability procedures, assessments of proposed solutions performance via the classical DC, AC and voltage stability transfer analysis, combined with unit outages inside the ComEd zone are highly encouraged which should be reflective of similar PJM analysis.

- Dominion / PJM South:

No major transmission needs were identified in Dominion for 2031. However, a number of needs that are scattered across the zone are summarized below.

In central Virginia, the Elmont 500/230kV transformer is overloaded in 2031 Summer analysis. This facility has already been identified as part of an M-3 need and will be addressed through the corresponding M-3 project (DOM-2023-0023).

In the Western portion of Dominion, voltage drop issues are observed around the Farmville substation in 2031 Winter N-1-1 analysis.

In the North Carolina portion of Dominion’s footprint, there are voltage drop issues around the Weyerhauser substation in 2031 Summer and Winter N-1-1 analysis.

Dominion submitted EOL criteria violations as part of its FERC Form 715, which includes 500kV lines Suffolk – Surry & Septa – Surry, and will be open to competition.

PJM performed analysis on the 2031 RTEP cases including Dominion’s HVDC link (b4053.3) awarded from the 2025W1. The project resolved all 230kV thermal overloads with the exception of the Elmont 500/230kV transformer from the 2031 RTEP analysis, and will be excluded from competition (to avoid duplicating solutions). Operational measures will be used to manage these anticipated issues until the HVDC link goes into service in 2032.

- AEP:

No major reliability violations were identified in the AEP zone. However, multiple 138 kV thermal overloads have been identified in the Columbus area around the Beatty substation and electrically adjacent facilities, with several branches exceeding conductor ratings, forming a geographically clustered set of violations that suggests competitive window consideration.

AEP also submitted violations as part of its FERC Form 715, including one local cluster of geographically proximate overloads that further support competitive window consideration.

Additional 138 kV issues, including isolated line constraints and terminal equipment limitations, have been identified; however, these are excluded from the competitive window. PJM does not anticipate regional solutions for the AEP zone.

- APS/ATSI/DLCO/AMPT:

- ATSI submitted violations as part of its FERC Form 715, specifically for load loss greater than 300 MW at the North Star Steel 345 kV facility. Based on short-circuit analysis both with and without the Fulton-Melbourne and the Dowling-Melbourne 345 kV lines in service, the 138 kV system cannot provide sufficient power to support the arc furnaces at North Star Steel.

- AMPT submitted N-1-1 violations as part of its FERC Form 715, notably on the East Fayette-Kexton 69 kV tie line, which could possibly impact the 345 kV transmission system so has been included for competition.

- MAAC (Mid Atlantic):

- There are no major reliability violations identified in the Mid-Atlantic region.

- Power flow increased south-to-northeast Mid-Atlantic along the PECO system – driven by load growth in PPL, PECO and PSEG zones - resulted in overloads on the 230 kV facilities (Cooper-Peach Bottom-Nottingham 230 kV) within PECO zone, as well as on one PECO/ACE tie facility (Mickleton-Delco Tap 230 kV).

- The Cooper-Peach Bottom-Nottingham 230 kV also restricts the imports into the EMAAC LDA, resulting in failure to meet the CETL/CETO margin.

- Multiple lines on the PECO/DPL (Edgemoor-Linwood 230 kV) tie and PECO transformer (Limerick) are overloaded; these facilities have already been identified as part of an M-3 need and will be addressed through the corresponding M-3 project.

- Multiple 138 kV facilities are overloaded in DPL zone for N-1-1 analysis and will be addressed accordingly.

- Penelec zone - In the Towanda area in northeast PENELEC near the NYISO border, the East Towanda-Canyon-North Meshoppen 230 kV line, the East Towanda 230/115 kV Transformer #3, and the North Meshoppen 230/115 kV Transformer #4 are overloaded in various summer analyses. These violations are affected by the interchange and flows into NY. These violations will be quarantined in the 2026 RTEP window and deferred to a separate process in consultation with NYISO.

Summer Load Deliverability:

PJM conducted Load deliverability analysis on the 2026 RTEP W1 2031 scenarios. The majority of the LDAs, taking into account all planned transmission enhancements respecting the anticipated in-service dates, showed a healthy CETL/CETO margin above 100%.

However, with the limited amount of Generation reserves in the 2031 base cases, there is not enough capacity to serve the resource adequacy needs of these larger LDAs under stressed conditions:

- PJM West: There are not enough resources/generators to create the CETO case (no sufficient reserves in the model) – The LDA will meet the CETL/CETO ratio of 100% or higher with sufficient resources outside of PJM West. Generation development inside PJM West will decrease the CETO metric and naturally lead to higher CETL/CETO metrics.

- AEP and Dominion: Due to a generation deficiency in developing the CETO cases, the forced outage rates of generators outside the LDA(s) are assumed to be zero. The LDA will meet the CETL/CETO ratio of 100% or higher with sufficient resources outside of AEP and Dominion. Generation development inside these PJM zones will decrease the CETO metric and naturally lead to higher CETL/CETO metrics.

- EMAAC: Reliability violations identified (CETL/CETO <100%) primarily due to low new generation entry and load growth.

|  | CETO | CETL | CETL/CETO (%) |
| --- | --- | --- | --- |
| EMAAC | 6533 | 5718 | 88% |

  - The following facilities are limiting the CETL/Import

| Monitored Facility | Contingency |
| --- | --- |
| 213869 PCHBTMTP 230 214087 COOPER2 230 1 | DPL_P1_2_CKT 5025_SRT-A |
| 213846 NOTTREAC 230 213869 PCHBTMTP 230 1 | DPL_P1_2_CKT 5025_SRT-A |
| 213844 NOTTNGHM 230 213846 NOTTREAC 230 1 | DPL_P1_2_CKT 5025_SRT-A |

- ComEd: ComEd zone already experiencing basecase (starting case) violations, that resulted in limiting the import to ComEd LDA. Load deliverability analysis can’t be performed for the ComEd LDA without fixing the baseline violations.

Winter Load Deliverability:

PJM conducted Load deliverability analysis on the 2026 RTEP W1 2031 scenarios. The majority of the LDAs showed a healthy CETL/CETO margin above 100%. However, with the limited amount of Generation reserves in the 2031 base cases, there is not enough capacity to serve the resource adequacy needs of these larger LDAs under stressed conditions:

- PJM West: There are not enough resources/generators to create the CETO case (no sufficient reserves in the model) – The LDA will meet the CETL/CETO ratio of 100% or higher with sufficient resources outside of PJM West. Generation development inside PJM West will decrease the CETO metric and naturally lead to higher CETL/CETO metrics.

- MAAC: Due to a generation deficiency in developing the CETO cases, the forced outage rates of generators outside the LDA(s) are assumed to be zero. The LDA will meet the CETL/CETO ratio of 100% or higher with sufficient resources outside of MAAC.

- EMAAC: Reliability violations identified (CETL/CETO <100%). Generation development inside PJM EMAAC will decrease the CETO metric and naturally lead to higher CETL/CETO metrics.

|  | CETO | CETL | CETL/CETO (%) |
| --- | --- | --- | --- |
| EMAAC | 6533 | 5601 | 89% |

- The following facilities are limiting the CETL

| Monitored Facility | Contingency |
| --- | --- |
| 213869 PCHBTMTP 230 214087 COOPER2 230 1 | DPL_P1_2_CKT 5025_SRT-A |
| 213846 NOTTREAC 230 213869 PCHBTMTP 230 1 | DPL_P1_2_CKT 5025_SRT-A |
| 213844 NOTTNGHM 230 213846 NOTTREAC 230 1 | DPL_P1_2_CKT 5025_SRT-A |

Short Circuit Analysis:

Over duty breakers were identified in a number of zones. PJM will accept proposals that reduce the overall short circuit in a given area in lieu of straight-up breaker replacements where a breaker uprate may not be more efficient or cost-effective.

8 Year, 2034 Analysis:

The 2034 cases are built starting with the 2025 RTEP 2031 cases. Load is adjusted according to the PJM 2026 load forecast along with any recently announced changes, and generation has been updated based on capacity expansion assumptions.

Projects with in service need year beyond 2031 are also added to the case, and the external world outside the PJM footprint is updated with the long term MMWG model, except for the 2034 LL case. Therefore, the MISO Tranche 2 projects are included in 2034 summer and winter cases, but not in the light load case.

#### P5 Analysis:

PJM will exclude from competition any violations associated with the TPL-001 P5 planning event (Fault plus non-redundant component of a Protection System failure to operate). Violations will be addressed by the incumbent Transmission Owner via the Substation Equipment Exclusion. Due to the sensitive nature of the violations, PJM will not include them as part of the posted materials in the Open Window.

#### Tools & Versions:

- PSSE 35.3

- ASPEN 15

- TARA

  - N-0/N-1/N-1-1/IPD: TARA Ver 2501.1.0.7 64-bit

  - Generator Deliverability: TARA Ver 2501.0.0.1 PJM GenDeliv Reform RC14 64-bit

    - To minimize the potential for inconsistent GenDeliv results, PJM recommends the following:

      - Delete the TARA temp folder before starting a new task.

      - Run on a desktop whenever possible. If using a laptop, disable parallel processing.

      - After GenDeliv completes, check the temp folder and ensure there are no *callstack*.csv files, which indicate a TARA crash.

      - Review the final DC loading results in the output Excel file and verify all values are above the required threshold.

  - Load Deliverability: TARA Ver 2401.1

#### WHAT PJM PROVIDES:

The information listed below is provided to allow replication of PJM’s analyses. Some of this data is designated Critical Energy Infrastructure Information (CEII) and must be handled consistent with PJM’s CEII request process at Competitive Planning Process page on the PJM website:

- Power Flow Base Cases: Identifies one or more system configurations to which planning criteria are applied.

- Contingency List: Lists all contingency types (single, bus, tower, line w/ stuck breaker).

- Subsystem Files: Identifies all subsystem zones to be considered in analysis.

- Monitor Files: Identify specific ranges of facilities by area and kV level to be considered in analysis.

- Facility Ratings: (if different from those included in the base cases)

- Violations List: Lists all criteria violations with power flow results and additional technical notes (flowgates). The results indicate the case(s) to which the criteria violations apply.

- Short Circuit Base Case. This case reflects the 2031 RTEP base case.

- Breaker Change Files. Lists all over-duty breakers in a specific TO area.

- TO Criteria Setting Files. Lists settings used for short circuit analysis for each specific TO.

- TARA Generation Deliverability options files.

- Generator Data files used in Generation Deliverability tests

PLEXOS Model

The updated capacity expansion model used to develop the 8-year cases will be posted. This version of the model accounts for the released interconnection process Cycle 1 data and includes 2 scenarios and 6 sensitivities.

As discussed above, PJM is not specifically encouraging right-sizing of solutions based on needs identified beyond the 5-year scenario needs. The 2034 models are provided to inform PJM stakeholders and interested window participants of potential longer-term system needs as reflected by the CapEx results and underlying assumptions, as well as the policies considered, future queued generation project information available at the time. These assumptions will be further refined as part of the 2027 RTEP based on the updated 2027 load forecast, the results of the PJM 2026 Reliability Backstop Procurement (RBP), and advances of the Generation Interconnection queue.

Access will require CEII clearance, Energy Exemplar’s PLEXOS license, and Energy Exemplar’s Eastern Interconnection dataset license.

- PJM Members and stakeholders who currently hold licenses for these products can request access to download this model by submitting a request through the CEII Access Request form here. When filling out the form, please type 8 Year Cases in the description field so that requests may be processed appropriately. Questions about the request process should be directed to CEIIRequest@pjm.com.

- PJM Members, and other stakeholders who have been participating in the TEAC, that do not hold licenses for one or both of these products, can inquire directly with Energy Exemplar at dylan.cronin@energyexemplar.com to purchase these licenses. These entities can also inquire about the possibility of purchasing these licenses at a discount before December 31, 2026.

The Henry Hub prices in the capacity expansion model used by PJM to support the 8-year cases are based on Hitachi Energy's forecast. The model is posted without these prices. If access to these prices in the expansion model is needed, please contact Hitachi Energy at refcasesupport.pges@hitachienergy.com.

### Response Back to PJM (Deliverables)

This section describes the required elements of a complete proposal. The absence of any element renders the proposal incomplete, and the proposal will not be considered for selection.

Often there are several viable solutions to a given violation. Include alternate approaches in separate proposals. PJM will not accept proposals with multiple options.

Four categories of information are described below: three are required for a complete package and one is conditional.

- Technical analysis files and documentation

- Completed proposal submittal template

- Project diagrams

- Company evaluation and operations and maintenance information (if required)

#### Technical Analysis Files and Documentation

Include the following technical information to provide a complete project proposal package:

- A detailed analysis spreadsheet showing the planning analysis results for the project.

- A set of updates to the power flow cases which model the proposed solution. Provide files in a format compatible with PSS/E version 35.3. Provide only solvable and convergent solutions. Include an idv, or equivalent type, file in order to apply changes to other models. Assign a unique identifier when new busses are required. Provide contingencies in a single file for each contingency type. Organize the contingencies into one of three categories:

  - Modified Contingencies

  - New Contingencies

  - Deleted Contingencies

- List of all proposed equipment along with relevant parameters and assumptions.

  - All necessary parameters, e.g., equipment ratings, impedances, line lengths, etc.

  - For reactive devices, settings and outputs

  - For synchronous machines, MW and MVAR output assumptions

- An analysis report of proposed solution which identifies the issues being addressed.

- Additional documentation required to verify the proposal.

### PJM Proposal Submittal

The PJM Competitive Planner Tool is used for proposal(s) submittal and captures project details, such as the criteria violations or system constraints that are being targeted by the proposed solution, the overall and specific project descriptions and the details of cost commitment, if included. The Competitive Planner Tool and user guide are available on the Competitive Planning Process page.

All proposals will be made public and posted on pjm.com after the proposal window is closed. Mark all CEII and business proprietary and confidential information for redaction from this public posting. Redact only information which meets the criteria of CEII or business proprietary and confidential information.

Redaction guidelines can be found in PJM Manual 14F, Section 6.2. Please note that this section provides guidance only. PJM reserves the right to challenge proposed redaction of information in order to ensure the appropriate level of transparency.

#### Project Diagrams

Provide project diagrams in the PJM Competitive Planner Tool to detail how the proposed solution will modify existing infrastructure, how new infrastructure will be configured and where new infrastructure will be sited. Project diagrams should include, but are not limited to, the following detail:

- Single line diagrams

- Substation general arrangement and station layout. If expanding the substation, identify the following:

  - Area to be modified

  - Land ownership or acquisition plan

- Line routing diagram:

  - Identify proposed route of new or upgraded transmission lines

  - Clearly identify where  acquisition of additional right-of-way is required

- Detailed project schedule. Include, at minimum, the following major work activities:

  - Engineering and Design

  - Siting and Permitting

  - ROW and Land acquisition

  - Material procurement

  - Construction

  - Testing/Commissioning

#### Project Mapping Information

PJM creates maps demonstrating the as-proposed route (by the proposing entity), voltage-level, and right-of-way usage for each competitive proposal. When submitting a “Greenfield” component (e.g. a new substation or a new line), submitters are expected to attach mapping files (.shp, .kmz or .kml files) to demonstrate the locations of new substations and routes of new lines. For new lines, please indicate which sections utilize “part” or all of existing right-of-way (highlighted in pink) and which sections utilize new right-of-way (highlighted in green).

Mapping files for non-Greenfield components are not required but are appreciated and may be requested, especially in the case of a proposal involving a planned transmission upgrade (e.g. a supplemental project which is not in service as of yet).

PJM kindly requests that substations and transmission lines follow the color code above and adhere to a general naming convention which reflects the location, voltage level, and upgrade type (e.g. “Station A – Station B 765kV New Line”). Any new substations, substation work, or terminal equipment may be represented by a singular point (“placemark” within Google Earth). If a new line utilizes both existing and new right-of-way, you may create multiple line segments (“paths” within Google Earth) with the correct color coding to differentiate the right-of-way usage along the route. Lastly, PJM requests that all components of a proposal are bundled together into one .kmz package when using Google Earth.

Project Capital Expenditure, Cost Containment Information and Cost Escalation

In accordance with PJM Manual 14F, Section 8.4, PJM will initiate the comparative cost framework to evaluate the costs of project proposals that are submitted through PJM’s competitive proposal window process, with the final comparative cost framework being performed once project proposals are found to pass an engineering screen. The comparative cost framework is a multi-step process that calculates project costs and permits the comparison of costs among projects addressing the same violation(s) or constraint(s) (competing projects) submitted through the proposal window.

A cost commitment provision submitted as part of a project proposal may include, but is not limited to, the capital structure (debt to equity ratio) and caps on: initial capital costs (total costs associated with bringing the project into service); the annual revenue requirement; the rate of return on equity (ROE); the debt cost; the total capital cost; allowance for funds used during construction (AFUDC); construction work in progress (CWIP); abandonment costs and schedule guarantees. A cost commitment proposal may also exclude defined cost elements from the cost commitment provision.

Within the Competitive Planner application, there is a Project Financial Information section that includes a financial form through which projected capital expenditures for the project should be provided. This form must be completed and submitted with each proposal submittal.

In addition, following the close of this Window, PJM may request additional details via email regarding the capital structure of submitted projects, and the cost containment provisions proposed in order to perform the comparative cost assessment of the competing proposals.

For the purpose of the escalation calculations in this Proposal Window, PJM recommends the use of a 2.1% escalation factor to ensure consistency in escalation calculations for all submitted proposals.

#### Company Evaluation and Operations and Maintenance Information

For proposers seeking Designated Entity status, provide additional information which will aid PJM in understanding how the proposed solution will be developed, constructed, operated and maintained. Include this information in the PJM Competitive Planner Tool.

Relevant PJM Operating Agreement language in Schedule 6, Section 1.5.8(f):

(f) Entity-Specific Criteria Considered in Determining the Designated Entity for a Project.  In determining whether the entity proposing a Short-term Project, Long-lead Project or Economic-based Enhancement or Expansion recommended for inclusion in the plan shall be the Designated Entity, the Office of the Interconnection shall consider:  (i) whether in its proposal, the entity indicated its intent to be the Designated Entity; (ii) whether the entity is pre-qualified to be a Designated Entity pursuant to Operating Agreement, Schedule 6, section 1.5.8(a); (iii) information provided either in the proposing entity’s submission  pursuant to the Operating Agreement, Schedule 6, section 1.5.8(a) or 1.5.8(c)(2) relative to the specific proposed project that demonstrates:  (1) the technical and engineering experience of the entity or its affiliate, partner, or parent company, including its previous record regarding construction, maintenance, and operation of transmission facilities relative to the project proposed; (2) ability of the entity or its affiliate, partner, or parent company to construct, maintain, and operate transmission facilities, as proposed, (3) capability of the entity to adhere to standardized construction, maintenance, and operating practices, including the capability for emergency response and restoration of damaged equipment; (4) experience of the entity in acquiring rights of way; (5) evidence of the ability of the entity, its affiliate, partner, or parent company to secure a financial commitment from an approved financial institution(s) agreeing to finance the construction, operation, and maintenance of the project, if it is accepted into the recommended plan; and (iv) any other factors that may be relevant to the proposed project, including but not limited to whether the proposal includes the entity’s previously designated project(s) included in the plan.

#### Transmittal of Proposals

Proposal submissions along with all files required for submission will be done with the PJM Competitive Planner Tool for each submitted proposal.

### Proposal Fees

All proposals, upgrades and greenfield solutions, with the exception of solutions submitted with an estimated cost of $5M or less, submitted for consideration in the 2026 RTEP Proposal Window 1 are subject to an initial $5,000 deposit per the PJM Operating Agreement, Schedule 6, Section 1.5.8(c).

Relevant PJM Operating Agreement language in Schedule 6, Section 1.5.8(c):

(c)(1)	All proposals submitted in the proposal windows must contain:  (i) the name and address of the proposing entity; (ii) a statement whether the entity intends to be the Designated Entity for the proposed project; (iii) the location of proposed project, including source and sink, if applicable; (iv) relevant engineering studies, and other relevant information as described in the PJM Manuals pertaining to the proposed project; (v) a proposed initial construction schedule including projected dates on which needed permits are required to be obtained in order to meet the required in-service date; (vi) cost estimates and analyses that provide sufficient detail for the Office of Interconnection to review and analyze the proposed cost of the project; and (vii) with the exception of project proposals submitted with cost estimates of $5 million or less, a $5,000 non-refundable deposit must be included with each project proposal submitted by a proposing entity that indicates an intention to be the Designated Entity.

(c)(1)(i)  In addition, any proposing entity indicating its intention to be the Designated Entity will be responsible for and must pay all actual costs incurred by the Transmission Provider to evaluate the submitted project proposal.  To the extent the Transmission Provider incurs costs to evaluate multiple submitted project proposals where such costs are not severable by individual project proposal, the Transmission Provider shall invoice equal shares of the non-severable costs among the project proposals that cause such non-severable costs to be incurred.  Notwithstanding this method of invoicing non-severable costs, non-severable costs will be jointly and severally owed by the proposing entities that cause such costs to be incurred.

(c)(1)(ii)  All non-refundable deposits will be credited towards the actual costs incurred by the Transmission Provider as a result of the evaluation of a submitted project proposal.

(c)(1)(iii)  Following the close of a proposal window but before the Transmission Provider incurs any third-party consultant work costs to evaluate a submitted project proposal, the Transmission Provider will issue to the proposing entity an initial invoice seeking payment of estimated costs to evaluate each submitted project proposal.  The estimated costs will be determined by considering the:  potential cost of consultant work, historical estimates for project proposals of similar scope, complexity and nature of the need, and/or technology and nature of the project proposal. The Transmission Provider may issue additional invoices to the proposing entity prior to the completion of the evaluation activities associated with a project proposal if the Transmission Provider receives updated actual cost information and/or upon consideration of the factors specified in this section.

(c)(1)(iv) At the completion of the evaluation activities associated with a project proposal, the Transmission Provider will reconcile the actual costs with monies paid and, to the extent necessary, issue either a final invoice or refund.

(c)(1)(v)  The proposing party must pay any invoiced costs within fifteen (15) calendar days of the Transmission Provider sending the invoice to the proposing entity or its agent.  For good cause shown, this fifteen (15) calendar day time period may be extended by the Transmission Provider.  If the proposing entity fails to pay any invoice within the time period specified and/or extended by the Transmission Provider in accordance with this section, the proposing entity’s pre-qualification status may be suspended and the proposing entity will be ineligible to be a Designated Entity for any projects that do not yet have an executed Designated Entity Agreement.  Such a suspension and/or ineligibility will remain in place until the proposing entity pays in full all outstanding monies owed to the Transmission Provider as a result of the evaluation of the proposing entity’s project proposal(s).

The non-refundable deposit is due at the time of submission. Pay the non-refundable deposit by wire transfer to PJM Interconnection at:

| Wire transfer funds to: | PJM Interconnection, LLC |
| --- | --- |
| Bank Name: | PNC Bank, N.A. New Jersey |
| ABA Number: | 031207607 (Fed Wire and ACH) |
| Account Number: | 80-1358-9826 |
| Provide Reference (see Note below) | Order 1000 |

Note: To ensure the non-refundable deposit is properly accounted for, include a reference to “Order 1000 – Competitive submittal PJM Proposal ID #” in the subject, notes or addenda field of the wire transfer form.  Please note that the PJM Proposal ID # will be displayed on the confirmation email you receive after submitting the proposal and is also identified on the Competitive Planner Tool once a competitive proposal is initially saved.

The proposer also needs to provide the following information to PJM:

Company Info, Primary contact name, Billing email & Tax ID#.

The PJM Proposal ID# can also be located on the Existing Proposal screen in the PJM Competitive Planner Tool as shown in the screenshot below.

### Window Duration and Timeline

As indicated herein, PJM is seeking solutions to address reliability needs identified through PJM’s five-year planning analyses (2031 case model suite), as well as right-sized solutions that resolve the identified near-term (2031) reliability needs. While PJM is not specifically encouraging right-sized solutions based on needs identified in the 2034 planning models, window participants may propose right-sizing opportunities for PJM’s consideration where they identify opportunities to develop a more efficient or cost-effective solution, as discussed herein.

In accordance with Operating Agreement § 1.5.8(c) and Manual 14F § 1.1, PJM opened a 60-day proposal window on July 20, 2026, to identify transmission enhancements or expansion to address reliability driven upgrade with required in-service dates five years. Following the notification from ComEd on July 30, 2026 of a significant reduction in its load forecast, PJM updated the planning analyses and reliability needs associated with the proposal window. PJM will therefore extend the closing date of the proposal window to October 12, 2026, to provide window participants additional time to consider the updated planning information and developer or modify their proposals. Accordingly, the timeline for 2026 RTEP Window 1 is as follows:

- 7/20/2026: Opening of 2026 RTEP Proposal Window 1

- 10/12/2026: Close of 2026 RTEP Proposal Window 1 at 5:00 p.m. Eastern Daylight Time

Notes:

- Confidentiality of individual proposals will be maintained for the duration of the window.

- Proposals received after close of the proposal window will not be accepted.

### Questions

Submit all questions about the proposal window to the PJM Planning Community. Submit questions involving confidential information or CEII under the “Confidential” topic on the Planning Community.

Answers will be provided to all participants in the proposal window.

Please reference 2026 RTEP Proposal Window 1 in all correspondence.

### Specialized Requirements

PJM seeks proposals to evaluate the identified needs in this window.  PJM has not determined specialized requirements that PJM is seeking in project proposals in this window for consideration in its evaluation.

Notice

In accordance with the PJM Open Access Transmission Tariff, Attachment M, the Market Monitoring Unit (MMU) has access to all data submitted to PJM through PJM’s competitive proposal window process.  See PJM Manual 14F, Section 8.4.4.

### Document Revision History

7/20/2026 - V1 -	Original Problem Statement posted to the PJM Competitive Planning Process webpage.

8/21/2026 - V2 -	Updated Problem Statement posted to the PJM Competitive Planning Process webpage.