## Light Load GenDeliv
Will be addressed through the interregional process
2031 RTEP PJM Generator Deliverability Result (Light Load) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | Cont Label | Cont Type | PJM Accepting Proposals | Reason For Exclusion | Comment | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026W1-GD-LL65 | 65 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 663.4 | 664.6 | 132.69 | 132.92 | COMED_P4-6_111-345-B______SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL66 | 66 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 647.1 | 648.2 | 132.34 | 132.55 | COMED_P4-6_111-345-B______SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL1 | 1 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 654.8 | 658 | 130.96 | 131.6 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL2 | 2 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 638.5 | 641.5 | 130.57 | 131.19 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL69 | 69 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 649 | 652.9 | 129.8 | 130.57 | COMED_P4_111-45-L30003__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL143 | 143 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 649 | 652.9 | 129.8 | 130.57 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL68 | 68 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 649 | 652.9 | 129.8 | 130.57 | COMED_P4_111-45-L11124__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL67 | 67 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 500 | 649 | 652.9 | 129.8 | 130.57 | COMED_P4_111-45-TR81____SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL70 | 70 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 632.7 | 636.4 | 129.39 | 130.15 | COMED_P4_111-45-L30003__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL71 | 71 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 632.7 | 636.4 | 129.39 | 130.15 | COMED_P4_111-45-L11124__SRT-A | Breaker | Yes |  | Overlap with Exelon EOL | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL72 | 72 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 632.7 | 636.4 | 129.39 | 130.15 | COMED_P4_111-45-TR81____SRT-A | Breaker | Yes |  | Overlap with Exelon EOL | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL144 | 144 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 489 | 632.7 | 636.4 | 129.39 | 130.15 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | Yes |  | Overlap with Exelon EOL | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL156 | 156 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 557 | 653.4 | 657 | 117.3 | 117.95 | COMED_P7-1_345-L30003_B-R_+_138-L11104_R-R_SRT-A | Tower | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL157 | 157 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 544 | 637.1 | 640.5 | 117.11 | 117.74 | COMED_P7-1_345-L30003_B-R_+_138-L11104_R-R_SRT-A | Tower | Yes |  | Overlap with Exelon EOL | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL158 | 158 | 272054 | MILLER RD; R | 272803 | W PLANO ; R | 1 | 138 | 222 | 557 | 651.1 | 653.8 | 116.89 | 117.38 | COMED_P7-1_345-L30003_B-R_+_345-L16703_R-S_SRT-A | Tower | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL159 | 159 | 272803 | W PLANO ; R | 272251 | PLANO ; R | 1 | 138 | 222 | 544 | 634.8 | 637.3 | 116.69 | 117.16 | COMED_P7-1_345-L30003_B-R_+_345-L16703_R-S_SRT-A | Tower | Yes |  | Overlap with Exelon EOL | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL73 | 73 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1876.3 | 1861.8 | 116.39 | 115.49 | COMED_P4_144-45-BT7-8___SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL74 | 74 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1869.8 | 1861.7 | 115.99 | 115.49 | COMED_P4_144-45-BT7-8___SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL75 | 75 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1873 | 1857.9 | 116.19 | 115.25 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL76 | 76 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1866.5 | 1857.8 | 115.79 | 115.25 | COMED_P4_144-45-BT6-8___SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL77 | 77 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1875.2 | 1856 | 116.33 | 115.14 | COMED_P4_175-45-BT2526__SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL8 | 8 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1875.2 | 1856 | 116.33 | 115.14 | COMED_P1-2_345-L0626__B-R_SRT-A | Single | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL79 | 79 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1871.5 | 1856 | 116.1 | 115.14 | COMED_P4_175-45-BT2122__SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL78 | 78 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1875.2 | 1856 | 116.33 | 115.14 | COMED_P4_175-45-BT2126__SRT-A | Breaker | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL9 | 9 | 270694 | CHERRY VA; B | 270908 | PRAIRIE ; B | 1 | 345 | 222 | 1612 | 1871.5 | 1856 | 116.1 | 115.14 | COMED_P1-2_345-L14427__B-R_SRT-A | Single | Yes |  |  | 1202 | 1479 | 1568 | 1768 | 1486 | 1651 | 1809 | 1912 | 1437 | 1607 | 1768 | 1912
Active | 2026W1-GD-LL80 | 80 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1865 | 1855.9 | 115.69 | 115.13 | COMED_P4_175-45-BT2122__SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL11 | 11 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1865 | 1855.9 | 115.69 | 115.13 | COMED_P1-2_345-L14427__B-R_SRT-A | Single | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL10 | 10 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1868.7 | 1855.9 | 115.93 | 115.13 | COMED_P1-2_345-L0626__B-R_SRT-A | Single | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL81 | 81 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1868.7 | 1855.9 | 115.93 | 115.13 | COMED_P4_175-45-BT2126__SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-LL82 | 82 | 270908 | PRAIRIE ; B | 270883 | SILVER LK; R | 1 | 345 | 222 | 1612 | 1868.7 | 1855.9 | 115.93 | 115.13 | COMED_P4_175-45-BT2526__SRT-A | Breaker | Yes |  |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational Only | N/A | 12 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 557.5 | 556.4 | 114.01 | 113.79 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational Only | N/A | 85 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 551.8 | 550.8 | 112.84 | 112.63 | COMED_P4_111-45-L30003__SRT-A | Breaker | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational Only | N/A | 145 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 551.8 | 550.8 | 112.84 | 112.63 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational Only | N/A | 84 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 551.8 | 550.8 | 112.84 | 112.63 | COMED_P4_111-45-TR81____SRT-A | Breaker | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational Only | N/A | 86 | 272445 | SANDWICH ; R | 272444 | SANDWICH ; B | Z1 | 138 | 222 | 489 | 551.8 | 550.8 | 112.84 | 112.63 | COMED_P4_111-45-L11124__SRT-A | Breaker | No | To be adressed through supplemental process. |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-LL15 | 15 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 547.3 | 547.1 | 109.46 | 109.42 | COMED_P1-2_345-L30003_B-R_SRT-A | Single | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL90 | 90 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 541.6 | 541.4 | 108.31 | 108.28 | COMED_P4_111-45-L30003__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL146 | 146 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 541.6 | 541.4 | 108.31 | 108.28 | COMED_P2-2_111_EJ-345B__1_SRT-A | Bus | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL89 | 89 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 541.6 | 541.4 | 108.31 | 108.28 | COMED_P4_111-45-L11124__SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026W1-GD-LL88 | 88 | 272444 | SANDWICH ; B | 272054 | MILLER RD; R | 1 | 138 | 222 | 500 | 541.6 | 541.4 | 108.31 | 108.28 | COMED_P4_111-45-TR81____SRT-A | Breaker | Yes |  |  | 351 | 449 | 460 | 498 | 421 | 500 | 513 | 557 | 407 | 489 | 502 | 544
Active | 2026-W1-GD-LL16 | 16 | 271241 | CRESCENT ; R | 348935 | 4CORBIN | 1 | 138 | 222/357 | 179 | 193.8 | 193.7 | 108.26 | 108.2 | COMED_P1-2_138-L7404___-S_SRT-A | Single | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 268 | 269 | 280 | 252 | 298 | 300 | 313 | 243 | 291 | 293 | 306

## Light Load IPD
2031 RTEP PJM Individual Plant Deliverability Result (Light Load) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | PJM Accepting Proposals | Reason For Exclusion | Comment | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026-W1-IPD-LL1 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 121.4 | 113.34 | 116.37 | AE2-185 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL2 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 119.3 | 111.38 | 114.31 | AE2-283 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL3 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 118.6 | 111.11 | 113.63 | AC1-145 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL4 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 116.8 | 109.09 | 111.92 | AF2-404 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL5 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 104.3 | 115.1 | 107.79 | 110.33 | AC1-042 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL6 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 135.4 | 147.4 | 108.37 | 108.93 | AC2-079 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-LL7 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 103.67 | 106.85 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL8 | 314691 | 3FARMVIL | 314726 | 3WILLIS | 1 | 115 | 345 | 242.5 | 257.4 | 109.15 | 106.14 | AF2-222 | DVP_P1-2: LN 9607_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026-W1-IPD-LL9 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 101.78 | 104.86 | AE2-283 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL10 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 83 | - | 101.96 | 104.51 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026-W1-IPD-LL11 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 101.52 | 104.29 | AC1-145 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL12 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 135.4 | 141.1 | 102.9 | 104.24 | AD1-082 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-LL13 | 314273 | 3BAKRS P | 314280 | 3NEWBOHE | 1 | 115 | 345 | 135.4 | 139.2 | 101.44 | 102.85 | AC2-079 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-LL14 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 99.56 | 102.56 | AF2-404 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL15 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 86 | - | 99.56 | 102.04 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026-W1-IPD-LL16 | 314532 | 3OAKRI23 | 314536 | 3SUFFOLK | 1 | 115 | 345 | 135.4 | 137.8 | 100.1 | 101.82 | AC2-079 | DVP_P1-2: LN 106_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-LL17 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 83 | - | 99.42 | 101.81 | AE2-283 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026-W1-IPD-LL18 | 314670 | 2ALTVSTA | 314667 | 4ALTVSTA | 1 | 69/138 | 345 | 124.1 | 126.1 | 95.05 | 101.6 | AE2-185 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 104 | 108 | 108 | 124 | 132 | 136 | 136 | 157 | 128 | 132 | 132 | 152
Active | 2026-W1-IPD-LL19 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 111 | - | 98.31 | 101.06 | AC1-042 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-LL20 | 200716 | 26PHILIPSB | 200727 | 26SHAW. 2 | 1 | 115 | 226 | 202 | 202.4 | 101.53 | 100.2 | AD2-133 | PN_P1-2_PN-115-052A_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 167 | 202 | N/A | 227 | 188 | 239 | N/A | 239 | 167 | 202 | N/A | 227