## N-0 Thermal
To be addressed through the interregional process
PJM N-0 Thermal Result (Summer 2031 Case) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG# | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | ContFlow(MVA) | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1201 | 1317.9 | 109.7752 | 109.73 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1201 | 1317.9 | 109.7752 | 109.73 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 546 | 592.2 | 108.3883 | 108.46 | Single | 'BASE CASE' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1201 | 1297.3 | 107.8601 | 108.02 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 546 | 583.5 | 106.7582 | 106.87 | Single | 'BASE CASE' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-N0-ST1 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345/345 | 222/222 | 1334 | 1352.5 | 100.2774 | 101.38 | Single | 'BASE CASE' | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## N-1 Thermal
To be addressed through the interregional process
PJM N-1 Thermal Result (Summer 2031 Case) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | KVs | Areas | Rating | ContFlow(MVA) | DC Ld(%) | AC Ld(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026-W1-N1-ST1 | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345/345 | 937 | 1091 | 118.0149 | 116.44 | Line_FB | 'DVP_P4-2: ELM_H1T574_SRT-A' | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (DOM-2023-0023) | 887 | 937 | N/A | 1053 | 1139 | 1191 | N/A | 1312 | 1056 | 1101 | N/A | 1205
Active | 2026-W1-N1-ST2 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 400.1 | 114.1261 | 114.65 | Line_FB | 'COMED_P4_120-45-L12002__SRT-A' | No | Substation Equipment Exclusion |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N1-ST3 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 254.6 | 113.722 | 114.17 | Tower | 'AEP_P7-1_#17439___SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST4 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 1725.1 | 111.1911 | 112.9 | Line_FB | 'COMED_P4_120-45-L11120__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST5 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 1724.8 | 111.178 | 112.88 | Line_FB | 'COMED_P4_120-45-L10322__SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST6 | 270812 | LOMBARD ;3B | 270724 | ELK GROVE; B | 1 | 345/345 | 222/222 | 1528 | 1724.8 | 111.178 | 112.88 | Bus | 'COMED_P2-2_120_LO-345R__2_SRT-A' | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026W1-N1-ST7 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 247.5 | 110.6726 | 111 | Tower | 'AEP_P7-1_#17440___SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345/345 | 222/222 | 1201 | 1317.9 | 109.7752 | 109.73 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345/345 | 222/222 | 1201 | 1317.9 | 109.7752 | 109.73 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026-W1-N1-ST8 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 382.8 | 109.0258 | 109.7 | Line_FB | 'COMED_P4_120-45-L11120__SRT-A' | No | Substation Equipment Exclusion |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N1-ST9 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 382.8 | 109.1404 | 109.68 | Line_FB | 'COMED_P4_120-45-L10322__SRT-A' | No | Substation Equipment Exclusion |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026-W1-N1-ST10 | 272855 | YORK ;RT | 271131 | BUTTERFIE; R | 1 | 138/138 | 222/222 | 349 | 382.8 | 109.1404 | 109.68 | Bus | 'COMED_P2-2_120_LO-345R__2_SRT-A' | No | Substation Equipment Exclusion |  | 351.1248 | 449.1242 | 459.6413 | 497.8849 | 421.3976 | 500.0361 | 513.1824 | 556.9236 | 406.8172 | 489.0411 | 501.7093 | 544.2554
Active | 2026W1-N1-ST11 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138/138 | 205/205 | 223 | 244.4 | 108.9686 | 109.58 | Tower | 'AEP_P7-1_#17439___SRT-A' | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026-W1-N1-ST12 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222/222 | 465 | 506.2 | 107.3118 | 108.86 | Bus | 'COMED_P2-2_120_LO-345B__6_SRT-A' | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 546 | 592.2 | 108.3883 | 108.46 | Single | 'BASE CASE' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345/345 | 222/222 | 1201 | 1297.3 | 107.8601 | 108.02 | Single | 'BASE CASE' | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 546 | 583.5 | 106.7582 | 106.87 | Single | 'BASE CASE' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST13 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138/138 | 205/205 | 223 | 237.6 | 106.009 | 106.53 | Tower | 'AEP_P7-1_#17440___SRT-A' | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST14 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138/138 | 205/205 | 350 | 372.5 | 104.9429 | 106.44 | Tower | 'AEP_P7-1_#18058___SRT-A' | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230/230 | 345/345 | 355 | 377.2 | 104.9859 | 106.27 | Line_FB | 'DVP_P4-2: ARL_250T258_SRT-A' | No | Dominions HVDC solution resolves this flowgate |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230/230 | 226/226 | 666 | 705.5 | 106.0661 | 105.93 | Line_FB | 'PL_02_P42_001063_SRT-A' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230/230 | 226/226 | 666 | 696.5 | 104.7297 | 104.57 | Line_FB | 'PL_02_P42_001063_SRT-A' | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST15 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 231.6 | 103.6323 | 103.85 | Line_FB | 'AEP_P4_#10715_05COLE 345_C_SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST16 | 247896 | 05BOLTON | 243519 | 05HALLRD | 1 | 138/138 | 205/205 | 223 | 229.5 | 102.2422 | 102.9 | Tower | 'AEP_P7-1_#17439___SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 999901 | 6POSSUM1 | 314029 | 6DUMFRES TAP | 1 | 230/230 | 345/345 | 671 | 688 | 99.8212 | 102.53 | Line_FB | 'DVP_P4-2: 237T2001_SRT-S' | No | Dominions HVDC solution resolves this flowgate |  | 605 | 671 | N/A | 701 | 769 | 818 | N/A | 840 | 743 | 793 | N/A | 818
Informational-Only | N/A | 314286 | 6CHESTF A | 314284 | 3CHESTFLD | 1 | 230/115 | 345/345 | 267 | 273.1 | 98.1648 | 102.28 | Tower | 'DVP_P7-1: LN 208-259_SRT-SL' | No | Dominions HVDC solution resolves this flowgate |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-N1-ST17 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345/345 | 222/222 | 1334 | 1352.5 | 100.2774 | 101.38 | Single | 'BASE CASE' | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-N1-ST18 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 226 | 101.1659 | 101.33 | Line_FB | 'AEP_P4_#5096_05HAYDEN 345_C2_SRT-A' | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST19 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138/138 | 205/205 | 223 | 224.3 | 100.1794 | 100.59 | Line_FB | 'AEP_P4_#10715_05COLE 345_C_SRT-A' | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-N1-ST20 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138/138 | 205/205 | 223 | 223.7 | 100.2242 | 100.33 | Tower | 'AEP_P7-1_#16019___SRT-A' | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A

## N-1 Volt Mag
PJM N-1 Voltage Magnitude Result (Summer 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Upper/Lower Limit | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comments

## N-1 Volt Drop
PJM N-1 Voltage Drop Result (Summer 2031 Case)
FG # Status | FG# | Bus # | Name | KV | Area | ContVolt | BaseVolt | Vdrop(%) | Cont Type | Contingency | PJM Accepting Proposals | Reasons for Exclusions | Comment

## N-1 Load Drop
PJM N-1 Load Drop Result (Summer 2031 Case)
FG # Status | FG# | Contingency Name | Cont. Type | Cont. Areas | Load Shed (MW) | Isolated Load (MW) | MW Drop (Cutoff = 75 MW) | PJM Accepting Proposals | Reasons for Exclusions | Comment
Informational-Only | N/A | DVP_P7-1: LN 2165-2170_SRT-A | Tower | 345 | 0.0 | 415.5 | 415.5 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P1-2: LN 9812_SRT-S | Single | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P1-2: LN 2375_SRT-A | Single | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: AE1157_256T9812_SRT-S | Line_FB | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: FOU_2061T9812_SRT-S | Line_FB | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: FOU_2125T9812_SRT-S | Line_FB | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P4-2: 2375T9500_SRT-A | Line_FB | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process
Informational-Only | N/A | DVP_P2-1: LN 9812_SRT-A | P2_1 | 345 | 0.0 | 305.0 | 305 | No | Will be addressed through the supplemental process