## Summer GenDeliv
To be addressed through the interregional process
2031 RTEP PJM Generator Deliverability Result (Summer) | [19 empty] | Conductor/Transformer Limit
FG # Status | FG # | FG Index | Fr Bus | Name | To Bus | Name | CKT | KVs | Areas | Cont Name | ContType | Rating | FN DC Flow | FN AC Flow | FN DC % | FN AC % | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026-W1-GD-S180 | 180 | 316479 | 3CHILTON | 314178 | 3LANCAST | 1 | 115 | 345 | DVP_P4-2: NRT_105952_SRT-S | Breaker | 248 | 303.9 | 300.7 | 122.53 | 121.24 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | N/A | 248 | 232 | 240 | N/A | 276 | 229 | 236 | N/A | 271
Active | 2026-W1-GD-S181 | 181 | 316479 | 3CHILTON | 314178 | 3LANCAST | 1 | 115 | 345 | DVP_P4-2: NRT_L4T1059_SRT-S | Breaker | 248 | 303.9 | 300.7 | 122.53 | 121.24 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | N/A | 248 | 232 | 240 | N/A | 276 | 229 | 236 | N/A | 271
Informational-Only | N/A | 187 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_02_P42_001063_SRT-A | Breaker | 666 | 786.1 | 784.7 | 118.03 | 117.82 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 1 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | Base Case | Single | 546 | 644.1 | 643.1 | 117.97 | 117.79 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S634 | 634 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P7-1_#17439___SRT-A | Tower | 223 | 260.3 | 261.3 | 116.71 | 117.16 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 188 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_02_P42_001063_SRT-A | Breaker | 666 | 777.2 | 775.6 | 116.7 | 116.46 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 2 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | Base Case | Single | 546 | 635.3 | 634.4 | 116.35 | 116.2 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S635 | 635 | 342559 | 4BOONE CO | 250054 | 08LONGBR | 1 | 138 | 212/320 | 34541 34553_SRT-A | Tower | 230 | 269.6 | 266.4 | 117.2 | 115.82 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Informational-Only | N/A | 193 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P2-3_PN-115-0272-A_SRT-A | Breaker | 666 | 762.2 | 761.5 | 114.45 | 114.34 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 195 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P2-3_PN-115-19E_SRT-A | Breaker | 666 | 759.4 | 759.3 | 114.02 | 114.02 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S637 | 637 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P7-1_#17440___SRT-A | Tower | 223 | 253.4 | 254.2 | 113.65 | 113.99 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 196 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P2-3_PN-115-0272-10_SRT-A | Breaker | 666 | 758.3 | 757.2 | 113.86 | 113.7 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P2-3_PN-115-0272-A_SRT-A | Breaker | 666 | 753.4 | 752.7 | 113.12 | 113.02 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S638 | 638 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P7-1_#17439___SRT-A | Tower | 223 | 250.6 | 252 | 112.39 | 112.99 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 209 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P2-3_PN-115-19E_SRT-A | Breaker | 666 | 750.5 | 750.6 | 112.69 | 112.7 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S210 | 210 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P4_120-45-L11120__SRT-A | Breaker | 1656 | 1838.9 | 1862.7 | 111.04 | 112.48 | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S211 | 211 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P4_120-45-L10322__SRT-A | Breaker | 1656 | 1838.9 | 1862.6 | 111.04 | 112.47 | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S532 | 532 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P2-2_120_LO-345R__2_SRT-A | Bus | 1656 | 1838.9 | 1862.6 | 111.04 | 112.47 | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 212 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P2-3_PN-115-0272-10_SRT-A | Breaker | 666 | 749.5 | 748.4 | 112.54 | 112.38 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S213 | 213 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | COMED_P4_120-45-L12002__SRT-A | Breaker | 1656 | 1834.7 | 1859.1 | 110.79 | 112.26 | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 218 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | Breaker | 180 | 202.4 | 198.4 | 112.43 | 110.2 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 219 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | Breaker | 180 | 199.3 | 198.4 | 110.72 | 110.2 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 217 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-3C_SRT-A | Breaker | 180 | 199.3 | 198.4 | 110.72 | 110.2 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S9 | 9 | 316479 | 3CHILTON | 314178 | 3LANCAST | 1 | 115 | 345 | DVP_P1-2: LN 1059_SRT-A | Single | 203 | 226.9 | 223.7 | 111.75 | 110.16 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | N/A | 248 | 232 | 240 | N/A | 276 | 229 | 236 | N/A | 271
Active | 2026W1-GD-S639 | 639 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P7-1_#17440___SRT-A | Tower | 223 | 244 | 245.2 | 109.42 | 109.95 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 220 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P2-3_PN-230-020-DRT_SRT-SL | Breaker | 180 | 200.2 | 197.6 | 111.2 | 109.78 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 11 | 270747 | ESS W407K;0T | 270753 | ESS W407M;0T | 1 | 345 | 222 | Base Case | Single | 1201 | 1320.6 | 1318 | 109.96 | 109.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 10 | 270733 | ELECT JCT;3R | 270747 | ESS W407K;0T | 1 | 345 | 222 | Base Case | Single | 1201 | 1320.6 | 1318 | 109.96 | 109.75 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Active | 2026W1-GD-S534 | 534 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P2-2_120_LO-345B__6_SRT-A | Bus | 465 | 499.3 | 507.7 | 107.37 | 109.18 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 225 | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | DVP_P4-2: ELM_H1T574_SRT-A | Breaker | 1053 | 1165.6 | 1149.5 | 110.69 | 109.17 | No | Violation resolved with Dominion's HVDC line |  | 887 | 937 | N/A | 1053 | 1139 | 1191 | N/A | 1312 | 1056 | 1101 | N/A | 1205
Informational-Only | N/A | 226 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P42_100926_SRT-A | Breaker | 666 | 727.1 | 726.5 | 109.18 | 109.08 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 227 | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | DVP_P4-2: ARL_250T258_SRT-A | Breaker | 355 | 382.1 | 386.7 | 107.65 | 108.94 | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Informational-Only | N/A | 641 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P71_102649_SRT-A | Tower | 666 | 725.7 | 725 | 108.96 | 108.86 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S535 | 535 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P2-2_120_LO-345B__6_SRT-A | Bus | 465 | 499.1 | 505.6 | 107.33 | 108.72 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 536 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | AP_P2-2_WP-230-005T_SRT-A | Bus | 666 | 722.4 | 722 | 108.47 | 108.4 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 14 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PN_P1-2_PN-115-037_SRT-A | Single | 666 | 721.8 | 720.8 | 108.37 | 108.22 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 16 | 270753 | ESS W407M;0T | 270813 | LOMBARD ;2R | 1 | 345 | 222 | Base Case | Single | 1201 | 1297.6 | 1297.5 | 108.04 | 108.03 | No | To be adressed through supplemental process. |  | 1201.6882 | 1478.9549 | 1567.991 | 1768.1727 | 1498.0767 | 1710.8072 | 1821.3554 | 2052.0125 | 1437.7234 | 1662.4051 | 1767.5752 | 1990.4641
Informational-Only | N/A | 230 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P42_100926_SRT-A | Breaker | 666 | 718.3 | 717.7 | 107.85 | 107.76 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S231 | 231 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P4_#10715_05COLE 345_C_SRT-A | Breaker | 223 | 239.6 | 240.1 | 107.45 | 107.68 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S642 | 642 | 243469 | 05BEATTY | 243586 | 05WHITER | 1 | 138 | 205 | AEP_P7-1_#18058___SRT-A | Tower | 350 | 371.4 | 376.6 | 106.11 | 107.6 | Yes |  |  | 558 | 651 | N/A | N/A | 704 | 773 | N/A | N/A | 606 | 691 | N/A | N/A
Informational-Only | N/A | 643 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P71_102649_SRT-A | Tower | 666 | 716.9 | 716.2 | 107.64 | 107.54 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S233 | 233 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P4_120-45-L12005__SRT-A | Breaker | 465 | 491 | 499.2 | 105.58 | 107.35 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S537 | 537 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P2-2_120_LO-345B__3_SRT-A | Bus | 465 | 491 | 499.2 | 105.58 | 107.35 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S232 | 232 | 270814 | LOMBARD ;4B | 275199 | LOMBARD ;4M | 1 | 345/138 | 222 | COMED_P4_120-45-L12003__SRT-A | Breaker | 465 | 491 | 499.2 | 105.58 | 107.35 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 539 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | AP_P2-2_WP-230-005T_SRT-A | Bus | 666 | 713.6 | 713.2 | 107.14 | 107.09 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 540 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_08_P22_102801_SRT-A | Bus | 666 | 713.8 | 712.8 | 107.17 | 107.03 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S541 | 541 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P2-2_120_LO-345B__3_SRT-A | Bus | 465 | 490.8 | 497.3 | 105.55 | 106.95 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S240 | 240 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P4_120-45-L12003__SRT-A | Breaker | 465 | 490.8 | 497.3 | 105.55 | 106.95 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Active | 2026W1-GD-S239 | 239 | 275199 | LOMBARD ;4M | 271922 | LOMBARD ; B | 1 | 138 | 222 | COMED_P4_120-45-L12005__SRT-A | Breaker | 465 | 490.8 | 497.3 | 105.55 | 106.95 | Yes |  |  | 420 | 480 | 520 | 536 | 450 | 491 | 528 | 544 | 440 | 488 | 526 | 542
Informational-Only | N/A | 19 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PN_P1-2_PN-115-037_SRT-A | Single | 666 | 712.9 | 712 | 107.05 | 106.91 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-GD-S246 | 246 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_105012_SRT-S | Breaker | 228 | 248 | 241.7 | 108.77 | 106.03 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026-W1-GD-S247 | 247 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_102712_SRT-S | Breaker | 228 | 248 | 241.7 | 108.76 | 106.02 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026-W1-GD-S248 | 248 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_17112_SRT-SL | Breaker | 228 | 248 | 241.7 | 108.75 | 106.02 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026-W1-GD-S249 | 249 | 314726 | 3WILLIS | 314691 | 3FARMVIL | 1 | 115 | 345 | DVP_P4-2: CHA_4012_SRT-S | Breaker | 228 | 247.9 | 241.7 | 108.74 | 106.01 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026W1-GD-S645 | 645 | 247896 | 05BOLTON | 243519 | 05HALLRD | 1 | 138 | 205 | AEP_P7-1_#17439___SRT-A | Tower | 223 | 234.6 | 236.1 | 105.22 | 105.89 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 544 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_08_P22_102801_SRT-A | Bus | 666 | 704.9 | 704.1 | 105.85 | 105.71 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 21 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_40_P11_001448_SRT-A | Single | 666 | 695.6 | 702.6 | 104.44 | 105.49 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 22 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_40_P11_001449_SRT-A | Single | 666 | 695.3 | 702.3 | 104.4 | 105.45 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 545 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_08_P22_102799_SRT-A | Bus | 666 | 700.3 | 700 | 105.16 | 105.11 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S262 | 262 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Breaker | 223 | 233.5 | 233.8 | 104.7 | 104.86 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S263 | 263 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P4_#10715_05COLE 345_C_SRT-A | Breaker | 223 | 232.9 | 233.8 | 104.45 | 104.86 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 28 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 208918 SUSQ 1 24.0 1 _SRT-A | Single | 666 | 697 | 695.1 | 104.66 | 104.37 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 29 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P12_000189_SRT-A | Single | 666 | 695.7 | 694.5 | 104.46 | 104.27 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 30 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_40_P11_001448_SRT-A | Single | 666 | 686.7 | 693.8 | 103.11 | 104.17 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S648 | 648 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P7-1_#16019___SRT-A | Tower | 223 | 232.1 | 232.3 | 104.06 | 104.15 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 31 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_40_P11_001449_SRT-A | Single | 666 | 686.5 | 693.5 | 103.08 | 104.13 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 550 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | AP_P2-2_WP-230-004_SRT-A | Bus | 666 | 693.8 | 693.3 | 104.17 | 104.1 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 551 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_11_P22_000176_SRT-A | Bus | 666 | 691.6 | 691.7 | 103.85 | 103.86 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 649 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_08_P71_101751_SRT-A | Tower | 666 | 691.1 | 691.4 | 103.78 | 103.82 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 552 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_08_P22_102799_SRT-A | Bus | 666 | 691.5 | 691.3 | 103.83 | 103.8 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 34 | 231000 | CLAY_230 | 214235 | LINWOOD84 | 1 | 230 | 230/235 | PECO_P1-2_220-85_SRT-A/* $ DELCO $ PECO_P1-2_220-85 $ L | Single | 809 | 851.9 | 838.6 | 105.31 | 103.66 | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Informational-Only | N/A | 650 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_48_P71_101752_SRT-A | Tower | 666 | 690 | 690.2 | 103.6 | 103.63 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 651 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PL_18_P71_103518_SRT-A | Tower | 666 | 690.8 | 689.9 | 103.73 | 103.59 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 652 | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | PECO_P7-1_220-0607_SRT-A/* $ CHESCO $ PECO_P7-1_220-0607 $ DCT | Tower | 666 | 687.9 | 688.1 | 103.28 | 103.32 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 37 | 231001 | EDGEMR 5 | 231000 | CLAY_230 | 1 | 230 | 235 | PECO_P1-2_220-85_SRT-A/* $ DELCO $ PECO_P1-2_220-85 $ L | Single | 800 | 841.1 | 826 | 105.13 | 103.25 | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 | 809 | N/A | 900 | 753 | 911 | N/A | 1017 | 732 | 890 | N/A | 992
Informational-Only | N/A | 38 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | 208918 SUSQ 1 24.0 1 _SRT-A | Single | 666 | 688.2 | 686.3 | 103.33 | 103.05 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 285 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | Breaker | 297 | 308.7 | 305.8 | 103.94 | 102.96 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 283 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-3C_SRT-A | Breaker | 297 | 304.3 | 305.8 | 102.45 | 102.96 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 284 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | Breaker | 297 | 304.3 | 305.8 | 102.45 | 102.96 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 39 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P12_000189_SRT-A | Single | 666 | 686.9 | 685.7 | 103.14 | 102.95 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 556 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | AP_P2-2_WP-230-004_SRT-A | Bus | 666 | 685 | 684.6 | 102.85 | 102.79 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S654 | 654 | 247896 | 05BOLTON | 243519 | 05HALLRD | 1 | 138 | 205 | AEP_P7-1_#17440___SRT-A | Tower | 223 | 227.8 | 229.1 | 102.16 | 102.75 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S287 | 287 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | AEP_P4_#5097_05HAYDEN 345_D1_SRT-A | Breaker | 223 | 228.7 | 228.9 | 102.56 | 102.63 | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 558 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_11_P22_000176_SRT-A | Bus | 666 | 682.8 | 683 | 102.52 | 102.55 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 288 | 314820 | 6BALLSTN | 314120 | 6CLRNDNC | 1 | 230 | 345 | DVP_P4-2: ARL_250T258_SRT-A | Breaker | 301 | 287.9 | 308.6 | 95.66 | 102.52 | No | Violation resolved with Dominion's HVDC line |  | 301 | 301 | N/A | 301 | 301 | 301 | N/A | 301 | 301 | 301 | N/A | 301
Informational-Only | N/A | 656 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_08_P71_101751_SRT-A | Tower | 666 | 682.3 | 682.7 | 102.45 | 102.51 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 289 | 999901 | 6POSSUM1 | 314029 | 6DUMFRES TAP | 1 | 230 | 345 | DVP_P4-2: 237T2001_SRT-S | Breaker | 701 | 698.2 | 718.5 | 99.61 | 102.5 | No | Violation resolved with Dominion's HVDC line |  | 605 | 671 | N/A | 701 | 769 | 818 | N/A | 840 | 743 | 793 | N/A | 818
Informational-Only | N/A | 659 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_48_P71_101752_SRT-A | Tower | 666 | 681.1 | 681.5 | 102.27 | 102.32 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 660 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PL_18_P71_103518_SRT-A | Tower | 666 | 682 | 681.2 | 102.4 | 102.28 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 292 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-020-DRT_SRT-SL | Breaker | 297 | 302.7 | 303.6 | 101.91 | 102.22 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 294 | 231001 | EDGEMR 5 | 214236 | LINWOOD85 | 1 | 230 | 230/235 | DPL_P4_2_DPEM231_SRT-A | Breaker | 809 | 841.3 | 826.5 | 103.99 | 102.16 | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Active | 2026W1-GD-S661 | 661 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P7-1_#16019___SRT-A | Tower | 223 | 227 | 227.6 | 101.79 | 102.07 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Informational-Only | N/A | 662 | 200924 | 26CANYON | 200706 | 26N.MESHPN | 1 | 230 | 226 | PECO_P7-1_220-0607_SRT-A/* $ CHESCO $ PECO_P7-1_220-0607 $ DCT | Tower | 666 | 679 | 679.4 | 101.96 | 102.01 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S296 | 296 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Breaker | 223 | 226.6 | 227.2 | 101.62 | 101.9 | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-GD-S302 | 302 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH045_SRT-A/* $ DELCO $ PECO_P4_CHICH045 $ STBK | Breaker | 796 | 822.1 | 810.8 | 103.28 | 101.86 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S560 | 560 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P2-2_CHI230B1_SRT-A/* $ DELCO $ PECO_P2-2_CHI230B1 $ B | Bus | 796 | 820.9 | 810.8 | 103.13 | 101.86 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S304 | 304 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH195_SRT-A/* $ DELCO $ PECO_P4_CHICH195 $ STBK | Breaker | 796 | 822.1 | 810.8 | 103.28 | 101.86 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S303 | 303 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH365_SRT-A/* $ DELCO $ PECO_P4_CHICH365 $ STBK | Breaker | 796 | 820.9 | 810.8 | 103.13 | 101.86 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Active | 2026W1-GD-S305 | 305 | 213559 | DELCOTAP | 228401 | MCKLTON | 1 | 230 | 230/234 | PECO_P4_CHICH435_SRT-A/* $ DELCO $ PECO_P4_CHICH435 $ STBK | Breaker | 796 | 821.2 | 810.6 | 103.17 | 101.83 | Yes |  |  | 678 (AEC) / 881 (PECO) | 796 (AEC) / 1010 (PECO) | N/A | 845 (AEC) / 1079 (PECO) | 715 (AEC) / 923 (PECO) | 835 (AEC) / 1052 (PECO) | N/A | 892 (AEC) / 1129 (PECO) | 708 (AEC) / 914 (PECO) | 827 (AEC) / 1043 (PECO) | N/A | 881 (AEC) / 1118 (PECO)
Informational-Only | N/A | 42 | 231001 | EDGEMR 5 | 214236 | LINWOOD85 | 1 | 230 | 230/235 | PECO_P1-2_220-84_SRT-A/* $ DELCO $ PECO_P1-2_220-84 $ L | Single | 809 | 835.7 | 820.9 | 103.3 | 101.47 | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Informational-Only | N/A | 43 | 314286 | 6CHESTF A | 314338 | 6SOUWEST | 1 | 230 | 345 | DVP_P1-2: LN 563_SRT-S | Single | 662.7 | 674.6 | 671.9 | 101.8 | 101.39 | No | Violation resolved with Dominion's HVDC line |  | 684 | 705 | N/A | 811 | 758 | 781 | N/A | 899 | 745 | 768 | N/A | 883
Active | 2026-W1-GD-S44 | 44 | 270814 | LOMBARD ;4B | 270812 | LOMBARD ;3B | Z1 | 345 | 222 | Base Case | Single | 1334 | 1338.8 | 1352.4 | 100.36 | 101.38 | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 45 | 231001 | EDGEMR 5 | 214236 | LINWOOD85 | 1 | 230 | 230/235 | DPL_P1_2_CKT 23015_SRT-A | Single | 809 | 833.7 | 818.4 | 103.05 | 101.16 | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Informational-Only | N/A | 665 | 231215 | SILVERSD | 231205 | DARLEY | 1 | 69 | 235 | DPL_P7_1_DBL_5NC_SRT-A | Tower | 239 | 246.9 | 241.5 | 103.33 | 101.06 | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 196 | 243 | N/A | 270 | 226 | 273 | N/A | 305 | 220 | 267 | N/A | 298
Active | 2026-W1-GD-S312 | 312 | 314178 | 3LANCAST | 313813 | 3OCRAN | 1 | 115 | 345 | DVP_P4-2: NRT_105952_SRT-S | Breaker | 268 | 276.2 | 270.8 | 103.05 | 101.04 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 226 | 233 | N/A | 268 | 321 | 331 | N/A | 381 | 306 | 316 | N/A | 363
Active | 2026-W1-GD-S313 | 313 | 314178 | 3LANCAST | 313813 | 3OCRAN | 1 | 115 | 345 | DVP_P4-2: NRT_L4T1059_SRT-S | Breaker | 268 | 276.2 | 270.8 | 103.05 | 101.04 | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 226 | 233 | N/A | 268 | 321 | 331 | N/A | 381 | 306 | 316 | N/A | 363
Informational-Only | N/A | 47 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P1-2_PN-230-013A_SRT-A | Single | 297 | 298.5 | 300.1 | 100.52 | 101.03 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 52 | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | PN_P1-2_PN-230-013A_SRT-A | Single | 180 | 182 | 181 | 101.09 | 100.55 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-GD-S53 | 53 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | Base Case | Single | 1201 | 1205.9 | 1203.7 | 100.41 | 100.22 | Yes |  |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 321 | 200675 | 26E.TWANDA | 200674 | 26TOWANDA | 3 | 230/115 | 226 | PN_P2-3_PN-230-17B25_SRT-A | Breaker | 297 | 300.7 | 297.4 | 101.25 | 100.14 | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Summer IPD
Will be addressed through the interregional process
2031 RTEP PJM Individual Plant Deliverability Result (Summer) | [17 empty] | Conductor/Transformer Limit
FG # Status | FG # | Fr Bus | Fr Name | To Bus | To Name | CKT | kVs | Areas | Rate Cont (MVA) | Cont Flow (MVA) | FN DC % | FN AC % | Plant | Cont Name | PJM Accepting Proposals | Reason For Exclusion | Comments | SN (MVA) | SLTE (MVA) | SSTE (MVA) | SLD (MVA) | WN (MVA) | WLTE (MVA) | WSTE (MVA) | WLD (MVA) | LLN (MVA) | LLLTE (MVA) | LLSTE (MVA) | LLLD (MVA)
Active | 2026-W1-IPD-S1 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 68 | - | 119.92 | 124.38 | AE2-283 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026-W1-IPD-S2 | 314178 | 3LANCAST | 316479 | 3CHILTON | 1 | 115 | 345 | 203 | 249.3 | 124.56 | 122.78 | AG1-536 | DVP_P1-2: LN 1059_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | 216 | 248 | 232 | 240 | 240 | 276 | 229 | 236 | 236 | 271
Active | 2026-W1-IPD-S3 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 68 | - | 117.65 | 122.05 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026-W1-IPD-S6 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 70 | - | 116.46 | 120.8 | AE2-283 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026-W1-IPD-S7 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 110 | 131.2 | 119.64 | 119.27 | AC2-079 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-S9 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 70 | - | 114.26 | 118.54 | AE2-185 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026-W1-IPD-S10 | 314178 | 3LANCAST | 316479 | 3CHILTON | 1 | 115 | 345 | 203 | 239.4 | 119.6 | 117.91 | AE1-155 | DVP_P1-2: LN 1059_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | 216 | 248 | 232 | 240 | 240 | 276 | 229 | 236 | 236 | 271
Active | 2026-W1-IPD-S12 | 314709 | 2GLADYS TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 68 | - | 112.45 | 116.61 | AF2-404 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 66 | 68 | N/A | 78 | 83 | 86 | N/A | 99 | 81 | 83 | N/A | 96
Active | 2026-W1-IPD-S14 | 313458 | 2AE2-283_TAP | 314730 | 3STONE MILL | 1 | 69 | 345 | 70 | - | 109.2 | 113.26 | AF2-404 | Base Case | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 68 | 70 | N/A | 81 | 86 | 89 | N/A | 102 | 83 | 86 | N/A | 99
Active | 2026-W1-IPD-S15 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1873 | 111.16 | 113.11 | AB2-132 | COMED_P4_120-45-L11120__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S16 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1872.9 | 111.16 | 113.1 | AB2-132 | COMED_P4_120-45-L10322__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S17 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1872.9 | 111.16 | 113.1 | AB2-132 | COMED_P2-2_120_LO-345R__2_SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S18 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1872.3 | 111.08 | 113.06 | AF2-200 | COMED_P4_120-45-L11120__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S19 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1872.1 | 111.08 | 113.05 | AF2-200 | COMED_P2-2_120_LO-345R__2_SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S20 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1872.1 | 111.08 | 113.05 | AF2-200 | COMED_P4_120-45-L10322__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S21 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1869.5 | 110.9 | 112.89 | AB2-132 | COMED_P4_120-45-L12002__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S22 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1868.7 | 110.83 | 112.85 | AF2-200 | COMED_P4_120-45-L12002__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S24 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1858.1 | 110.32 | 112.21 | AF2-027 | COMED_P4_120-45-L11120__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S25 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1858 | 110.32 | 112.2 | AF2-027 | COMED_P2-2_120_LO-345R__2_SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S26 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1858 | 110.32 | 112.2 | AF2-027 | COMED_P4_120-45-L10322__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S27 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1854.5 | 110.07 | 111.99 | AF2-027 | COMED_P4_120-45-L12002__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S28 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1850.7 | 109.93 | 111.76 | AF2-349 | COMED_P4_120-45-L11120__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S29 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1850.5 | 109.93 | 111.75 | AF2-349 | COMED_P4_120-45-L10322__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S30 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1850.5 | 109.93 | 111.75 | AF2-349 | COMED_P2-2_120_LO-345R__2_SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S31 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | 1847.1 | 109.67 | 111.54 | AF2-349 | COMED_P4_120-45-L12002__SRT-A | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S32 | 314691 | 3FARMVIL | 314726 | 3WILLIS | 1 | 115 | 345 | 204.9 | 227.2 | 114.6 | 110.87 | AF2-222 | DVP_P1-2: LN 9607_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026-W1-IPD-S33 | 314178 | 3LANCAST | 316479 | 3CHILTON | 1 | 115 | 345 | 203 | 224.3 | 111.61 | 110.47 | AF1-042 | DVP_P1-2: LN 1059_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | 216 | 248 | 232 | 240 | 240 | 276 | 229 | 236 | 236 | 271
Active | 2026-W1-IPD-S35 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 93.2 | 105.99 | 108.98 | AC1-145 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-S38 | 314273 | 3BAKRS P | 314280 | 3NEWBOHE | 1 | 115 | 345 | 110 | 116.4 | 104.51 | 105.85 | AC2-079 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-S40 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 110 | 114.5 | 103.22 | 104.13 | AD1-082 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-S44 | 314178 | 3LANCAST | 316479 | 3CHILTON | 1 | 115 | 345 | 203 | 210 | 104.54 | 103.41 | AD2-074 | DVP_P1-2: LN 1059_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | 216 | 248 | 232 | 240 | 240 | 276 | 229 | 236 | 236 | 271
Active | 2026-W1-IPD-S46 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 88.3 | 99.92 | 103.21 | AC1-042 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-S49 | 314532 | 3OAKRI23 | 314536 | 3SUFFOLK | 1 | 115 | 345 | 110 | 112.7 | 101.14 | 102.47 | AC2-079 | DVP_P1-2: LN 106_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-S51 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 87.2 | 97.88 | 101.99 | AE2-283 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-S52 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 100.72 | 101.95 | AF2-200 | Base Case | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S53 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 100.76 | 101.94 | AB2-132 | Base Case | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S55 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 100.6 | 101.78 | AD2-134 | Base Case | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S56 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 100.56 | 101.74 | AG1-118 | Base Case | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S57 | 250054 | 08LONGBR | 342559 | 4BOONE CO | 1 | 138 | 212/320 | 230 | 233.5 | 102.92 | 101.54 | AF2-111 | 34541 34553_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Active | 2026-W1-IPD-S58 | 314691 | 3FARMVIL | 314726 | 3WILLIS | 1 | 115 | 345 | 204.9 | 208 | 106.07 | 101.49 | AG1-285 | DVP_P1-2: LN 9607_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 198 | 218 | N/A | 228 | 250 | 266 | N/A | 273 | 242 | 258 | N/A | 265
Active | 2026-W1-IPD-S60 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | - | 101 | 101.09 | AF2-200 | Base Case | No | Substation Equipment Exclusion |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026-W1-IPD-S63 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 99.8 | 100.94 | AF2-027 | Base Case | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S64 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | - | 100.89 | 100.92 | AB2-132 | Base Case | No | Substation Equipment Exclusion |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026-W1-IPD-S65 | 314273 | 3BAKRS P | 316079 | AB2-161 TAP | 1 | 115 | 345 | 110 | 111 | 100.26 | 100.9 | AB2-161 | DVP_P1-2: LN 23_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 114 | 117 | N/A | 135 | 144 | 148 | N/A | 171 | 139 | 144 | N/A | 165
Active | 2026-W1-IPD-S66 | 270812 | LOMBARD ;3B | 270814 | LOMBARD ;4B | Z1 | 345 | 222 | 1656 | - | 99.7 | 100.79 | AF2-349 | Base Case | No | Substation Equipment Exclusion |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026-W1-IPD-S68 | 250054 | 08LONGBR | 342559 | 4BOONE CO | 1 | 138 | 212/320 | 230 | 231.3 | 101.91 | 100.56 | AF1-233 | 34541 34553_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 211 | 230 | N/A | 247 | 343 | 354 | N/A | 364 | 211 | 230 | N/A | 247
Active | 2026-W1-IPD-S69 | 314178 | 3LANCAST | 316479 | 3CHILTON | 1 | 115 | 345 | 248 | 249.3 | 101.98 | 100.52 | AG1-536 | DVP_P4-2: NRT_105952_SRT-S | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | 216 | 248 | 232 | 240 | 240 | 276 | 229 | 236 | 236 | 271
Active | 2026-W1-IPD-S70 | 314178 | 3LANCAST | 316479 | 3CHILTON | 1 | 115 | 345 | 248 | 249.3 | 101.98 | 100.52 | AG1-536 | DVP_P4-2: NRT_L4T1059_SRT-S | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 209 | 216 | 216 | 248 | 232 | 240 | 240 | 276 | 229 | 236 | 236 | 271
Active | 2026-W1-IPD-S71 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | - | 100.44 | 100.47 | AD2-134 | Base Case | No | Substation Equipment Exclusion |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026-W1-IPD-S72 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | - | 100.41 | 100.43 | AF2-182 | Base Case | No | Substation Equipment Exclusion |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Active | 2026-W1-IPD-S74 | 314670 | 2ALTVSTA | 314709 | 2GLADYS TAP | 1 | 69 | 345 | 85.5 | 85.7 | 96.14 | 100.23 | AE2-185 | DVP_P1-2: LN 173_SRT-A | No | Reliability Violations on Transmission Facilities Below 200 kV exclusion |  | 88 | 91 | N/A | 104 | 111 | 115 | N/A | 132 | 108 | 111 | N/A | 127
Active | 2026-W1-IPD-S75 | 270732 | ELECT JCT;1B | 270814 | LOMBARD ;4B | 1 | 345 | 222 | 1201 | - | 100.2 | 100.23 | AG1-118 | Base Case | No | Substation Equipment Exclusion |  | 1334.346 | 1726.3437 | 1836.8918 | 2084.2807 | 1602.6493 | 1920.5499 | 2050.8174 | 2325.0963 | 1547.0764 | 1879.3184 | 2005.4031 | 2273.1088
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 112.27 | 112.5 | V2-019 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 112.22 | 112.44 | K02 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 111.95 | 112.16 | AE2-139 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 110.65 | 110.91 | V2-019 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 110.6 | 110.85 | K02 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | - | 110.33 | 110.56 | AE2-139 | Base Case | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 727.9 | 109.24 | 109.29 | V2-019 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 727.2 | 109.19 | 109.19 | K02 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 725.9 | 108.98 | 108.99 | AE2-139 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 718.8 | 107.91 | 107.93 | V2-019 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 718.2 | 107.87 | 107.83 | K02 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 355 | 382.7 | 106.78 | 107.81 | AF1-123 | DVP_P4-2: ARL_250T258_SRT-A | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 355 | 382.7 | 106.79 | 107.81 | AF1-124 | DVP_P4-2: ARL_250T258_SRT-A | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Informational-Only | N/A | 314041 | 6GLEBE | 314185 | 6RADNOR | 1 | 230 | 345 | 355 | 382.6 | 106.75 | 107.78 | AF1-125 | DVP_P4-2: ARL_250T258_SRT-A | No | Violation resolved with Dominion's HVDC line |  | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355 | 355 | 355 | N/A | 355
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 716.8 | 107.65 | 107.63 | AE2-139 | PL_02_P42_001063_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1108.7 | 106.64 | 105.29 | AF1-124 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1108.6 | 106.63 | 105.28 | AF1-123 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1108.3 | 106.61 | 105.26 | AF1-125 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1099.9 | 105.85 | 104.45 | LTFIMP_O-066 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | 180 | 187.5 | 103.52 | 104.19 | P28 | PN_P2-3_PN-230-3C_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | 180 | 187.5 | 103.52 | 104.19 | P28 | PN_P2-3_PN-230-997-DRT-055_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | 180 | 187.5 | 105.19 | 104.19 | P28 | PN_P2-3_PN-230-997-DRT-068_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | 180 | 187.5 | 103.52 | 104.19 | P28 | PN_P1-2_PN-230-013A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1096 | 105.45 | 104.08 | AE1-173 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 200677 | 26NO MESHO | 200706 | 26N.MESHPN | 4 | 115/230 | 226 | 180 | 186.8 | 103.98 | 103.76 | P28 | PN_P2-3_PN-230-020-DRT_SRT-SL | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 690.5 | 103.5 | 103.68 | V2-019 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 688.2 | 103.05 | 103.33 | V2-019 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 688 | 103.15 | 103.31 | K02 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 686.7 | 102.9 | 103.1 | V2-019 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 686.3 | 102.9 | 103.04 | AE2-139 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 686.2 | 102.9 | 103.03 | V2-019 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1084.4 | 104.4 | 102.98 | AD1-105 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 685.8 | 102.7 | 102.97 | K02 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1083.5 | 104.29 | 102.89 | AC1-158 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 314908 | 8ELMONT | 314218 | 6ELMONT | 2 | 500/230 | 345 | 1053 | 1083.4 | 104.29 | 102.88 | AC1-191 | DVP_P4-2: ELM_H1T574_SRT-A | No | M3 project already in place to address the violation (DOM-2023-0023) |  | 887 | 937 | 937 | 1053 | 1139 | 1191 | 1191 | 1312 | 1056 | 1101 | 1101 | 1205
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 684.2 | 102.54 | 102.73 | K02 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 684 | 102.45 | 102.7 | AE2-139 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 683.7 | 102.54 | 102.65 | K02 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 682.5 | 102.29 | 102.47 | AE2-139 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 681.9 | 102.29 | 102.39 | AE2-139 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 681.7 | 102.18 | 102.36 | V2-019 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 679.5 | 101.73 | 102.02 | V2-019 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 679.3 | 101.82 | 101.99 | K02 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 677.9 | 101.57 | 101.79 | V2-019 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 677.5 | 101.57 | 101.73 | AE2-139 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 677.3 | 101.57 | 101.7 | V2-019 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 677.3 | 101.58 | 101.69 | AB1-160 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 677.1 | 101.56 | 101.67 | LTFIMP_O-066 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 677 | 101.37 | 101.66 | K02 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 675.6 | 101.34 | 101.44 | AG1-090 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 675.5 | 101.22 | 101.42 | K02 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 675.3 | 101.12 | 101.4 | AE2-139 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 675 | 101.14 | 101.35 | AB1-160 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 674.9 | 101.22 | 101.33 | K02 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 674.9 | 101.11 | 101.33 | LTFIMP_O-066 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 673.7 | 100.97 | 101.16 | AE2-139 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 673.4 | 100.98 | 101.12 | AB1-160 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 673.3 | 100.96 | 101.1 | LTFIMP_O-066 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 673.3 | 100.89 | 101.09 | AG1-090 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 673.1 | 100.97 | 101.07 | AE2-139 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 672.9 | 100.98 | 101.04 | AB1-160 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 672.8 | 100.94 | 101.03 | AD2-133 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 672.8 | 100.96 | 101.02 | LTFIMP_O-066 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 672.7 | 100.93 | 101.01 | AG1-090/AG1-377/AG1-378 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 671.8 | 100.79 | 100.87 | AG1-548 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 671.7 | 100.74 | 100.86 | AG1-090 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 671.2 | 100.74 | 100.78 | AG1-090 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 670.6 | 100.5 | 100.68 | AD2-133 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 670.4 | 100.48 | 100.67 | AG1-090/AG1-377/AG1-378 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 669.5 | 100.35 | 100.53 | AG1-548 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 669 | 100.34 | 100.45 | AD2-133 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 231000 | CLAY_230 | 231001 | EDGEMR 5 | 1 | 230 | 235 | 800 | 803.6 | 102.25 | 100.44 | LTFIMP_O-066 | PECO_P1-2_220-85_SRT-A/* $ DELCO $ PECO_P1-2_220-85 $ L | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 | 809 | N/A | 900 | 753 | 911 | N/A | 1017 | 732 | 890 | N/A | 992
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668.9 | 100.33 | 100.43 | AG1-090/AG1-377/AG1-378 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 214235 | LINWOOD84 | 231000 | CLAY_230 | 1 | 230 | 230/235 | 809 | 812.1 | 101.94 | 100.39 | LTFIMP_O-066 | PECO_P1-2_220-85_SRT-A/* $ DELCO $ PECO_P1-2_220-85 $ L | No | To be adressed through supplemental process. | M-3 project already in place to address the violation (PE-2025-008) | 654 (DPL) / 731 (PECO) | 809 (DPL) / 885 (PECO) | N/A | 900 (DPL) / 985 (PECO) | 753 (DPL) / 822 (PECO) | 911 (DPL) / 978 (PECO) | N/A | 1017 (DPL) / 1092 (PECO) | 732 (DPL) / 802 (PECO) | 890 (DPL) / 958 (PECO) | N/A | 992 (DPL) / 1069 (PECO)
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668.5 | 100.26 | 100.38 | AB1-160 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668.5 | 100.34 | 100.37 | AD2-133 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668.4 | 100.23 | 100.36 | LTFIMP_O-066 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668.4 | 100.33 | 100.35 | AG1-090/AG1-377/AG1-378 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668.1 | 100.17 | 100.32 | V2-019 | PL_48_P42_100926_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 668 | 100.19 | 100.3 | AG1-548 | PN_P1-2_PN-115-037_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 667.7 | 100.12 | 100.25 | K02 | PL_48_P42_100926_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 667.5 | 100.19 | 100.22 | AG1-548 | PN_P2-3_PN-115-0272-10_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.8 | 100.01 | 100.12 | AG1-090 | PN_P2-3_PN-115-0272-A_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.7 | 99.96 | 100.1 | V2-019 | PL_48_P41_102622_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.7 | 99.96 | 100.1 | V2-019 | PL_48_P12_000189_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.7 | 99.97 | 100.1 | V2-019 | PL_48_P11_000840_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.7 | 99.95 | 100.1 | V2-019 | PL_48_P71_102649_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.3 | 99.81 | 100.04 | AB1-160 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.2 | 99.91 | 100.03 | AE2-139 | PL_48_P42_100926_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.2 | 99.91 | 100.03 | K02 | PL_48_P41_102622_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.2 | 99.91 | 100.03 | K02 | PL_48_P12_000189_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.2 | 99.93 | 100.03 | K02 | PL_48_P11_000840_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200675 | 26E.TWANDA | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.2 | 99.91 | 100.03 | K02 | PL_48_P71_102649_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Informational-Only | N/A | 200706 | 26N.MESHPN | 200924 | 26CANYON | 1 | 230 | 226 | 666 | 666.1 | 99.78 | 100.02 | LTFIMP_O-066 | PN_P2-3_PN-115-19E_SRT-A | No | To be addressed through the interregional process |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Active | 2026W1-IPD-S4 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 480 | 580.3 | 119.24 | 120.89 | AF2-349 | COMED_P4_184-45-BT22-23_SRT-A | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-IPD-S5 | 270724 | ELK GROVE; B | 271442 | ELK GRV E; B | 1 | 345/138 | 222 | 480 | 580.3 | 119.24 | 120.89 | AF2-349 | COMED_P4_184-45-BT16-17_SRT-A | Yes |  |  | 420 | 480 | 520 | 536 | 449 | 491 | 528 | 544 | 439 | 488 | 526 | 542
Active | 2026W1-IPD-S8 | 270999 | ANTIOCH ;RT | 272393 | ROUND LK ;5R | 1 | 138 | 222 | 230 | 273.2 | 116.5 | 118.79 | AF2-349 | COMED_P7-1_345-L13821_R-R_+_345-L18502AB-N_SRT-A | Yes |  |  | 172.5746 | 222.7695 | 223.2475 | 229.7011 | 213.4476 | 252.6473 | 253 | 261.4912 | 205.0817 | 246.4327 | 247.1498 | 254.5595
Active | 2026W1-IPD-S11 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 260.1 | 116.15 | 116.64 | AD1-081 | AEP_P7-1_#17439___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S13 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 253 | 113.09 | 113.47 | AD1-081 | AEP_P7-1_#17440___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S23 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 250.6 | 111.72 | 112.37 | AD1-081 | AEP_P7-1_#17439___SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S34 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 243.8 | 108.76 | 109.33 | AD1-081 | AEP_P7-1_#17440___SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S36 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 237.9 | 106.4 | 106.68 | AD1-081 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S37 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 237.3 | 106.23 | 106.43 | AE2-148 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S39 | 243519 | 05HALLRD | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 235 | 104.64 | 105.37 | AD1-081 | AEP_P7-1_#17439___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S41 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 232.1 | 103.88 | 104.07 | AD1-081 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S42 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 231.4 | 103.29 | 103.75 | AD1-081 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S43 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 231 | 103.45 | 103.58 | AE2-148 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S45 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 230.6 | 103.01 | 103.39 | AE2-148 | AEP_P4_#10715_05COLE 345_C_SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S47 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 230.1 | 103.06 | 103.19 | AD1-081 | AEP_P7-1_#16019___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S48 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 229.4 | 102.83 | 102.88 | AE2-148 | AEP_P7-1_#16019___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S50 | 243519 | 05HALLRD | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 228 | 101.58 | 102.23 | AD1-081 | AEP_P7-1_#17440___SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S54 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 227.1 | 101.74 | 101.85 | AD1-081 | AEP_P4_#5097_05HAYDEN 345_D1_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S59 | 243469 | 05BEATTY | 247896 | 05BOLTON | 1 | 138 | 205 | 223 | 226 | 101.31 | 101.35 | AE2-148 | AEP_P4_#5097_05HAYDEN 345_D1_SRT-A | Yes |  | Overlap AEP EOL candidate | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S61 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 225.2 | 100.65 | 101 | AD1-081 | AEP_P7-1_#16019___SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S62 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 225.2 | 100.66 | 100.99 | AD1-081 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S67 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 224.3 | 100.33 | 100.6 | AE2-148 | AEP_P7-1_#16019___SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A
Active | 2026W1-IPD-S73 | 243469 | 05BEATTY | 246716 | 05PHILLIPI | 1 | 138 | 205 | 223 | 223.9 | 100.14 | 100.4 | AE2-148 | AEP_P4_#5096_05HAYDEN 345_C2_SRT-A | Yes |  |  | 223 | 223 | N/A | N/A | 281 | 281 | N/A | N/A | 242 | 242 | N/A | N/A